## 2021
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2021-01-01 | 514 | 746 | 721 | 756 | 37.83 | 2774.83 | 2605.5 | 169.33 | 2775 | 3.299 | 0.81985 | Module Cleaning has been done in Row-M,N,O,P and Row-J,K,L Inverter No-3 and 2 total module cleaning-1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2021-01-02 | 498 | 721 | 681 | 730 | 36.27 | 2666.27 | 2504.25 | 162.02 | 2667 | 3.06 | 0.84948 | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 |  | 1458 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2021-01-03 | 590 | 882 | 831 | 918 | 51.27 | 3272.27 | 3099 | 173.27 | 3273 | 3.936 | 0.81048 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2021-01-04 | 504 | 716 | 685 | 725 | 36.5 | 2666.5 | 2506.5 | 160 | 2667 | 3.228 | 0.80527 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning-1566 |  | 1566 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2021-01-05 | 544 | 786 | 751 | 787 | 41.5 | 2909.5 | 2730 | 179.5 | 2910 | 3.487 | 0.81338 | Today we are cleaning all inverter Door filters. & Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 & Today we are chang the new 1 MC4 conecter in the inverter no-1 - AJB-No-1. |  | 1440 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2021-01-06 | 661 | 1023 | 967 | 1068 | 62.39 | 3781.39 | 3597 | 184.39 | 3782 | 4.555 | 0.80926 | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2021-01-07 | 221 | 312 | 298 | 313 | 16.25 | 1160.25 | 1046.25 | 114 | 1161 | 3.304 | 0.34249 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C Inverter No-4 total module cleaning - 960 |  | 960 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2021-01-08 | 384 | 520 | 494 | 524 | 21.7 | 1943.7 | 1787.25 | 156.45 | 1944 | 2.216 | 0.85503 | Module Cleaning has been done in Row-D,E,F,G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1626 & Today we are found 1 MC4 connector Burn in Invertor No-4 AJB No-6 string No-4 --tive site. we replaced 1 MC4 connector and started the strings. |  | 1626 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2021-01-09 | 493 | 710 | 690 | 746 | 33.29 | 2672.29 | 2510.25 | 162.04 | 2673 | 3.106 | 0.83878 | Module Cleaning has been done in Row-L Inverter No-2 & Row-M,N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 1344 & Today we are found 1 MC4 connector Burn in Invertor No-3 AJB No- string No-2 ++tive site we replaced all 1 MC4 connector and started the strings. |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2021-01-10 | 509 | 752 | 711 | 817 | 39.38 | 2828.38 | 2667 | 161.38 | 2829 | 3.089 | 0.89262 | Grid failure from -10:15 to 10:22 & 11:32 to 11:47 & 01:51 to 01:59. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2021-01-11 | 656 | 1002 | 953 | 1088 | 58.74 | 3757.74 | 3567.75 | 189.99 | 3758 | 4.046 | 0.90528 | Module Cleaning has been done in Row-I,J,K Inverter No-2 & Row-F,G,H Inverter No-1 total module cleaning - 1470 & Today we are found 1 MC4 connector Burn in Invertor No-2 AJB No-5 string No-1 ++tive site we replaced all 1 MC4 connector and started the strings. |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2021-01-12 | 695 | 1059 | 987 | 1134 | 63.22 | 3938.22 | 3739.5 | 198.72 | 3939 | 4.697 | 0.81737 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 & Row-A,B,C,D,E,F,G, Inverter No-4 total module cleaning - 1473 & Today we are Recaind ABB -Wavlaty door fan -nos-3 and change the new fan in inverter no-3,4 |  | 1473 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2021-01-13 | 736 | 1144 | 1069 | 1230 | 72.15 | 4251.15 | 4053 | 198.15 | 4252 | 5.111 | 0.81085 | Module Cleaning has been done in Row-H,I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-P,Q,R,S,T inverter No-3 total module cleaning -1365 |  | 1365 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2021-01-14 | 696 | 1109 | 1038 | 1205 | 71.41 | 4119.41 | 3927 | 192.41 | 4120 | 5.3 | 0.75766 | Grid failure from -03:54 to 04:32 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2021-01-15 | 650 | 1013 | 958 | 1088 | 62.64 | 3771.64 | 3573 | 198.64 | 3772 | 4.552 | 0.80765 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2021-01-16 | 635 | 983 | 935 | 1029 | 61.95 | 3643.95 | 3465.75 | 178.2 | 3644 | 4.464 | 0.79562 | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Row-K,L, Inverter No-2 total module cleaning - 1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2021-01-17 | 590 | 902 | 884 | 917 | 53.06 | 3346.06 | 3161.25 | 184.81 | 3347 | 3.891 | 0.83839 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2021-01-18 | 599 | 918 | 867 | 912 | 53.99 | 3349.99 | 3166.5 | 183.49 | 3350 | 4.303 | 0.7588 | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-C,D,E,F,G,H Inverter No-1 total module cleaning - 1575 & Grid failure from -02:37 to 2:54 |  | 1575 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2021-01-19 | 611 | 922 | 862 | 907 | 52.15 | 3354.15 | 3174 | 180.15 | 3355 | 4.128 | 0.79215 | Module Cleaning has been done in Row-A,B & Row-A,B,C,D,E,F,G,H,I,Inverter No-1&4 total module cleaning-1491 |  | 1491 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2021-01-20 | 619 | 922 | 882 | 963 | 52.93 | 3438.93 | 3258 | 180.93 | 3439 | 4.168 | 0.80419 | Module Cleaning has been done in Row-J,K,L Inverter No-4 & Trecker 1,2,3 & Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1620 |  | 1620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2021-01-21 | 711 | 1134 | 1074 | 1210 | 73.15 | 4202.15 | 3999 | 203.15 | 4203 | 5.056 | 0.81022 | Module Cleaning has been done in Row-I,J,K,L Inverter No-2 & Row-G,H inverter No-1 total module cleaning -1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2021-01-22 | 670 | 1049 | 1003 | 1099 | 66.17 | 3887.17 | 3684.75 | 202.42 | 3888 | 4.835 | 0.78376 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E,F inverter No-4 total module cleaning -1464 & Grid failure from 8:29 to 8:42 |  | 1464 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2021-01-23 | 635 | 977 | 917 | 1053 | 56.63 | 3638.63 | 3450 | 188.63 | 3639 | 4.399 | 0.80627 | Module Cleaning has been done in Row-G,H,I,J,K,L & Inverter No-4 & Trecker 1,2,3 & Row-Q,R,S,T inverter No-3 total module cleaning -1416 & Grid failure from 6:30 to 8:21 & Grid failure from 10:37 to 10:42 |  | 1416 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2021-01-24 | 671 | 1003 | 968 | 1074 | 60.38 | 3776.38 | 3598.5 | 177.88 | 3777 | 4.524 | 0.81372 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2021-01-25 | 675 | 1024 | 1003 | 1088 | 65.66 | 3855.66 | 3659.25 | 196.41 | 3856 | 4.87 | 0.77172 | Module Cleaning has been done in Row-M,N,O,PInverter No-3 & Row-J,K,L, Inverter No-2 total module cleaning - 1617 & Today we are change the new (2) mc4 conecter in the inverter no-1 AJB No-6 & Grid failure from 11:24 to 11:54 & Today Replaced the D.C.15 Amp fuse link of the string-03 --tive line in AJB-123 of The Inverter-4 during the period of 11:30 to 11:35. |  | 1617 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
25 | 2021-01-26 | 767 | 1194 | 1144 | 1230 | 73.16 | 4408.16 | 4194 | 214.16 | 4409 | 5.026 | 0.85501 | Module Cleaning has been done in Row-I,Inverter No-2 & Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning - 1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2021-01-27 | 775 | 1215 | 1149 | 1265 | 77.09 | 4481.09 | 4263 | 218.09 | 4482 | 5.295 | 0.82501 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning - 1386 Today Replaced the D.C.12 Amp fuse link of the string-08 --tive line in AJB-110 of The Inverter-2during the period of 10:30 to 10:35. |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
27 | 2021-01-28 | 757 | 1174 | 1109 | 1235 | 73.07 | 4348.07 | 4136.25 | 211.82 | 4349 | 5.118 | 0.82821 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2021-01-29 | 766 | 1210 | 1134 | 1260 | 76.39 | 4446.39 | 4231.5 | 214.89 | 4447 | 5.276 | 0.82151 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2021-01-30 | 771 | 1210 | 1154 | 1295 | 80.31 | 4510.31 | 4295.25 | 215.06 | 4511 | 5.319 | 0.8266 | Module Cleaning has been done in Row- J,K,L Inverter No-4 & Tracker 1,2,3, & Row-N,O,P,Q,R,S,T, Inverter No- 3 total module cleaning-1368 & Grid failure from 01:57 to 02:01. |  | 1368 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2021-01-31 | 751 | 1189 | 1140 | 1270 | 78.92 | 4428.92 | 4232.25 | 196.67 | 4429 | 5.418 | 0.79674 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2021-02-01 | 716 | 1139 | 942 | 1215 | 74.09 | 4086.09 | 3884.25 | 201.84 | 4087 | 5.253 | 0.75832 | Module Cleaning has been done in Row-M,N, Inverter No-3 & Row-J,K,L, Inverter No-2 total module cleaning - 1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2021-02-02 | 690 | 1089 | 1028 | 1104 | 66.74 | 3977.74 | 3786.75 | 190.99 | 3978 | 4.934 | 0.78581 | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 & Today we are found 7 MC4 conecter burn in inverter no-4 AJB NO-19 string no-2 ++ive site & AJB NO-19 string no-4 ++ive site & AJB NO-20 string no-2 --ive site we replaced all-7 MC4 connector and started the string. |  | 1458 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2021-02-03 | 620 | 927 | 887 | 938 | 50.84 | 3422.84 | 3242.25 | 180.59 | 3423 | 4.118 | 0.81016 | Module cleaning has been done in Row-B,C,D,E,F,G,H,I Inverter no-4 total module cleaning -1314 |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2021-02-04 | 650 | 988 | 943 | 1023 | 57.54 | 3661.54 | 3474.75 | 186.79 | 3662 | 4.391 | 0.81284 | Module Cleaning has been done in Row-J,K,L Inverter No-4 & Trecker 1,2,3 & Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1620 |  | 1620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2021-02-05 | 731 | 1139 | 1088 | 1171 | 68.95 | 4197.95 | 4002 | 195.95 | 4221 | 4.977 | 0.82661 | Module Cleaning has been done in Row-I,J,K,L Inverter No-2 & Row-G,H inverter No-1 total module cleaning -1533 & Today we are found 3 MC4 connecter burn in inverter no-2 AJB NO-108 string no-8 ++ive site & inverter NO-1 AJB NO-103 string no-5,6 ++ive site we replaced all-3 MC4 connector and started the string. |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2021-02-06 | 766 | 1205 | 1140 | 1253 | 75.37 | 4439.37 | 4230 | 209.37 | 4440 | 5.172 | 0.83671 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E,F inverter No-4 total module cleaning -1464 |  | 1464 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2021-02-07 | 796 | 1255 | 1184 | 1321 | 80.9 | 4636.9 | 4425 | 211.9 | 4637 | 5.277 | 0.85645 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2021-02-08 | 782 | 1244 | 1174 | 1335 | 81.18 | 4616.18 | 4401.75 | 214.43 | 4617 | 5.465 | 0.82342 | Module Cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-Q,R,S,T inverter No-3 total module cleaning -1416 & Today we are found 1MC4 connecter burn in inverter no-1 AJB NO-102 string no-8 ++ive site we replaced 1MC4 connector and started the string. |  | 1416 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2021-02-09 | 700 | 1079 | 1039 | 1144 | 67.25 | 4029.25 | 3841.5 | 187.75 | 4030 | 4.851 | 0.8097 | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 & Row-J,K,L, inverter No-2 total module cleaning -1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2021-02-10 | 741 | 1144 | 1088 | 1190 | 69.6 | 4232.6 | 4026.75 | 205.85 | 4233 | 4.708 | 0.87632 | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 |  | 1458 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2021-02-11 | 650 | 984 | 943 | 1023 | 55.01 | 3655.01 | 3480 | 175.01 | 3656 | 4.336 | 0.82181 | Module cleaning has been done in Row-B,C,D,E,F,G,H,I Inverter no-4 total module cleaning -1314 |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2021-02-12 | 681 | 1048 | 993 | 1084 | 62.93 | 3868.93 | 3687.75 | 181.18 | 3869 | 4.64 | 0.81271 | Module Cleaning has been done in Row-j,k,l Inverter No-4 & Trecker 1,2,3 & total module cleaning -528 |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2021-02-13 | 655 | 997 | 963 | 1033 | 58.96 | 3706.96 | 3518.25 | 188.71 | 3707 | 4.528 | 0.79794 | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2021-02-14 | 671 | 1054 | 1013 | 1073 | 62.59 | 3873.59 | 3691.5 | 182.09 | 3874 | 4.726 | 0.79895 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2021-02-15 | 685 | 1033 | 978 | 1064 | 59.18 | 3819.18 | 3636 | 183.18 | 3820 | 4.429 | 0.84064 | Module Cleaning has been done in Row-I,j inverter-2 & Row-D,E,F,G,H inverter no-1 total module cleaning-1470 |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2021-02-16 | 746 | 1165 | 1098 | 1225 | 71.35 | 4305.35 | 4105.5 | 199.85 | 4306 | 4.849 | 0.86551 | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F,G inverter No-4 total module cleaning -1200 |  | 1200 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2021-02-17 | 731 | 1103 | 1039 | 1174 | 66.71 | 4113.71 | 3917.25 | 196.46 | 4114 | 4.846 | 0.82743 | Module Cleaning has been done in Row-I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-R,S,T inverter no-3 total module cleaning -1092 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2021-02-18 | 726 | 1089 | 1048 | 1169 | 66.48 | 4098.48 | 3892.5 | 205.98 | 4099 | 4.693 | 0.85129 | Module Cleaning has been done in Row-M,N,O,P,Q Inverter No-3 & Row-K,L Inverter No-2 total module cleaning - 1449 |  | 1449 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2021-02-19 | 761 | 1179 | 1104 | 1246 | 72.23 | 4362.23 | 4156.5 | 205.73 | 4363 | 4.92 | 0.86432 | Today we are change the new (5) mc4 conecter in the inverter no-3 AJB No-116. & today we are found (2)MC4 connector burn in inverter no-3 AJB NO-116 string NO-2 ++ive site &--ive site we replaced all-2 MC4 connector & started the string.& module cleaning has been done in Row-I,J inverter no-2 & Row-D,E,F,G,H, inverter no-1 total module cleaning -1470 |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2021-02-20 | 796 | 1241 | 1164 | 1325 | 78.01 | 4604.01 | 4378.5 | 225.51 | 4605 | 5.467 | 0.82098 | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F Inverter No-4 total module cleaning - 1002 |  | 1002 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2021-02-21 | 761 | 1204 | 1144 | 1270 | 74.83 | 4453.83 | 4269 | 184.83 | 4454 | 5.333 | 0.81401 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2021-02-22 | 716 | 1109 | 1049 | 1180 | 66.63 | 4120.63 | 3909 | 211.63 | 4121 | 5.083 | 0.7902 | Module Cleaning has been done in Row-G,H,I,J Inverter No-4 total module cleaning - 774 |  | 774 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2021-02-23 | 725 | 1129 | 1083 | 1209 | 68.16 | 4214.16 | 4005 | 209.16 | 4215 | 5.057 | 0.81238 | Module Cleaning has been done in Row-k,l Inverter No-4 & Trecker 1,2,3 & ROW-P,Q,R,S,T inverter no-3 total module cleaning -789 |  | 789 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2021-02-24 | 716 | 1104 | 1084 | 1195 | 67.93 | 4166.93 | 3969.75 | 197.18 | 4167 | 4.791 | 0.84772 | Module Cleaning has been done in Row-M,N,O Inverter No-3 & Row-L inverter no-2 total module cleaning - 903 & Grid failure from -15:19 to 15:23 |  | 903 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2021-02-25 | 766 | 1229 | 1184 | 1325 | 75.6 | 4579.6 | 4359 | 220.6 | 4580 | 5.299 | 0.84241 | Module Cleaning has been done in Row-I,J,K inverter no-2 total module cleaning - 840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2021-02-26 | 752 | 1190 | 1129 | 1271 | 71.17 | 4413.17 | 4199.25 | 213.92 | 4414 | 5.11 | 0.84191 | Module Cleaning has been done in Row-D,E,F,G,H inverter no-1 total module cleaning - 903 |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2021-02-27 | 755 | 1154 | 1099 | 1244 | 67.79 | 4319.79 | 4131 | 188.79 | 4320 | 5.038 | 0.83575 | Module Cleaning has been done in Row-A,B,C inverter no-1 & A,B,C,D,E,F total module cleaning - 1002 |  | 1002 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2021-02-28 | 736 | 1129 | 1064 | 1220 | 65.81 | 4214.81 | 4019.25 | 195.56 | 4215 | 5.142 | 0.79895 | Today we are faund one module damej in Inverter no-4,AJB No-4,String no-2,module no-3,B-site module serial no-NPC10BY1130277 & Grid failure from -10:04 to 10:15 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2021-03-01 | 787 | 1215 | 1144 | 1336 | 73.01 | 4555.01 | 4332.75 | 222.26 | 4556 | 5.541 | 0.8014 | Module Cleaning has been done in Row-I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1122 |  | 1122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2021-03-02 | 791 | 1235 | 1189 | 1376 | 82.04 | 4673.04 | 4451.25 | 221.79 | 4674 | 5.567 | 0.81831 | Today replced the 12-Amp D.C Fuse link of the string-7 in AJB-117 of the inverter no-3 during the poried-09:50 to 10:10 Module Cleaning has been done in Row-N,O,P,Q,R,S,T Inverter no-3 total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
61 | 2021-03-03 | 741 | 1189 | 1175 | 1285 | 78.93 | 4468.93 | 4256.25 | 212.68 | 4469 | 5.046 | 0.86321 | Module Cleaning has been done in Row-M, inverter no-3 & Row- J,K,L inverter no-2 total module cleaning total module cleaning - 1071 & Grid failure from-11:05 to 10:09 & Grid failure from-11:34 to 11:37 & Grid failure from-03:04 to 03:33 & Today we are found 1MC4 connecter burn in inverter no-1 AJB NO-105 string no-8 --ive site we replaced 1MC4 connector and started the string. |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2021-03-04 | 771 | 1225 | 1164 | 1296 | 76.37 | 4532.37 | 4322.25 | 210.12 | 4533 | 5.264 | 0.83931 | Module Cleaning has been done in Row-,I inverter no-3 & Row-D,E,F,G,H inverter no-1 total module cleaning - 1176 & Grid failure from-16:43 to 16:49 & Grid failure from-17:32 to 17:54 |  | 1176 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2021-03-05 | 776 | 1200 | 1144 | 1295 | 74.29 | 4489.29 | 4276.5 | 212.79 | 4490 | 4.792 | 0.91323 | Module Cleaning has been done in Row-A,B,C inverter no-1 & Row-A,B,C,D,E,F inverter no-4 total module cleaning - 1002 |  | 1002 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2021-03-06 | 751 | 1159 | 1104 | 1280 | 71.01 | 4365.01 | 4158.75 | 206.26 | 4366 | 5.126 | 0.83015 | Module Cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1122 |  | 1122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2021-03-07 | 777 | 1204 | 1149 | 1346 | 79.26 | 4555.26 | 4346.25 | 209.01 | 4556 | 5.395 | 0.82309 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2021-03-08 | 756 | 1167 | 1149 | 1295 | 74.98 | 4441.98 | 4236 | 205.98 | 4442 | 4.951 | 0.87446 | Grid failure from-07:19 to 07:25 & Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, inverter no-3 & Row-L,inverter no-2 total module cleaning - 1344. |  | 1344 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2021-03-09 | 771 | 1233 | 1185 | 1331 | 77.65 | 4597.65 | 4365.75 | 231.9 | 4598 | 5.437 | 0.82426 | Module Cleaning has been done in Row-I,J,K inverter no-2 & Row-G,H inverter no-1 total module cleaning - 1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2021-03-10 | 766 | 1199 | 1139 | 1280 | 73.83 | 4457.83 | 4249.5 | 208.33 | 4458 | 5.104 | 0.8513 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2021-03-11 | 711 | 1064 | 1013 | 1089 | 61.21 | 3938.21 | 3750 | 188.21 | 3939 | 4.312 | 0.89035 | Module Cleaning has been done in Row-A,B,C,D,E,F inverter no-1 & Row-A,B,C,D,E inverter no-4 total module cleaning - 1266 |  | 1266 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2021-03-12 | 725 | 1103 | 1048 | 1225 | 63.12 | 4164.12 | 3954 | 210.12 | 4165 | 4.884 | 0.83117 | Module Cleaning has been done in Row-F,G,H,I,J,L,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1320 |  | 1320 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2021-03-13 | 782 | 1205 | 1175 | 1350 | 78.42 | 4590.42 | 4374 | 216.42 | 4591 | 5.522 | 0.81033 | module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, inverter no-3 & Row-L,inverter no-2 total module cleaning - 1344. |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2021-03-14 | 770 | 1190 | 1174 | 1321 | 75.39 | 4530.39 | 4326.75 | 203.64 | 4531 | 5.186 | 0.85156 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2021-03-15 | 766 | 1194 | 1149 | 1290 | 73.62 | 4472.62 | 4266.75 | 205.87 | 4473 | 5.294 | 0.82351 | Module cleaning has been done in Row-I,J,k inverter no-2 & Row-F,G,H, inverter no-1 total module cleaning -1470 & Grid failure from-09:42 to 09:46 & Grid failure from-11:01 to 11:17 |  | 1470 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2021-03-16 | 727 | 1114 | 1064 | 1184 | 65.33 | 4154.33 | 3944.25 | 210.08 | 4155 | 5.038 | 0.80383 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2021-03-17 | 746 | 1139 | 1083 | 1215 | 68 | 4251 | 4042.5 | 208.5 | 4252 | 5.015 | 0.82637 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2021-03-18 | 695 | 998 | 958 | 1059 | 56.25 | 3766.25 | 3567.75 | 198.5 | 3767 | 4.488 | 0.81808 | Module cleaning has been done in Row- A,B,C,D,E Inverter no-1 & Row-A,B,C,D Inverter No-4 total module cleaning -915 |  | 915 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2021-03-19 | 696 | 1024 | 973 | 1119 | 56.94 | 3868.94 | 3681.75 | 187.19 | 3979 | 4.591 | 0.84473 | Module cleaning has been done in Row- E,F,G,H,I,J,K Inverter No-4 total module cleaning -1296 |  | 1296 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2021-03-20 | 685 | 1007 | 983 | 1124 | 59.78 | 3858.78 | 3657.75 | 201.03 | 3859 | 4.607 | 0.81641 | Module Cleaning has been done in Row-L, Inverter No-4 & Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Trecker 1,2,3 total module cleaning -1278 |  | 1278 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2021-03-21 | 701 | 1038 | 1053 | 1174 | 64.95 | 4030.95 | 3837 | 193.95 | 4031 | 4.883 | 0.8046 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2021-03-22 | 705 | 1089 | 1053 | 1190 | 66.33 | 4103.33 | 3893.25 | 210.08 | 4104 | 4.894 | 0.81733 | Module cleaning has been done in Row- I,J,K,L, Inverter No-2 & Row-H, Inverter No-1 total module cleaning -1323 |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2021-03-23 | 711 | 1114 | 1039 | 1169 | 66.06 | 4099.06 | 3894 | 205.06 | 4100 | 4.895 | 0.81636 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2021-03-24 | 756 | 1149 | 1083 | 1230 | 67.48 | 4285.48 | 4066.5 | 218.98 | 4286 | 5.117 | 0.81637 | Module cleaning has been done in Row- A,B,C,D,E,F,G Inverter No-1 & Row-A,B,C,D Inverter No-4 total module cleaning -1314 |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2021-03-25 | 837 | 1250 | 1185 | 1386 | 77.36 | 4735.36 | 4504.5 | 230.86 | 4736 | 5.53 | 0.83472 | Module cleaning has been done in Row- E,F,G,H,I Inverter No-4 total module cleaning -954 |  | 954 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2021-03-26 | 816 | 1225 | 1169 | 1396 | 79.35 | 4685.35 | 4464.75 | 220.6 | 4686 | 4.95 | 0.92268 | Module Cleaning has been done in Row-J,K,L, Inverter No-4 & Trecker 1,2,3 Row-M,N,O,P,Q,R,S,T, Inverter No-3 & total module cleaning -1620 |  | 1620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2021-03-27 | 726 | 1124 | 1084 | 1225 | 72.38 | 4231.38 | 4026.75 | 204.63 | 4232 | 5.036 | 0.81905 | Module cleaning has been done in Row- I,J,K,L Inverter No-2 total module cleaning -1092 & Grid failure from-08:22 to 08:25 & Grid failure from-12:09 to 12:36 |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2021-03-28 | 781 | 1230 | 1169 | 1325 | 77.45 | 4582.45 | 4362.75 | 219.7 | 4583 | 5.611 | 0.79609 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2021-03-29 | 796 | 1250 | 1185 | 1356 | 79.23 | 4666.23 | 4448.25 | 217.98 | 4667 | 5.579 | 0.81533 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2021-03-30 | 802 | 1245 | 1184 | 1376 | 79.93 | 4686.93 | 4464.75 | 222.18 | 4687 | 5.481 | 0.83347 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2021-03-31 | 766 | 1129 | 1074 | 1245 | 65.2 | 4279.2 | 4060.5 | 218.7 | 4280 | 4.879 | 0.855 | Module cleaning has been done in Row- A,B,C,D,E,F,G,H Inverter No-1 & Row-A,B,C, Inverter No-4 total module cleaning -1401 |  | 1401 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2021-04-01 | 827 | 1240 | 1179 | 1351 | 79.37 | 4676.37 | 4457.25 | 219.12 | 4677 | 5.505 | 0.82806 | Today we are cleaning all inverter Door filters. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2021-04-02 | 811 | 1219 | 1159 | 1350 | 78.46 | 4617.46 | 4403.25 | 214.21 | 4618 | 5.392 | 0.83475 | Module cleaning has been done in Row- D,E,F,G,H,I,JInverter No-4 total module cleaning -1278 |  | 1278 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2021-04-03 | 787 | 1175 | 1124 | 1366 | 75.36 | 4527.36 | 4306.5 | 220.86 | 4528 | 5.42 | 0.81425 | Module Cleaning has been done in Row-K,L, Inverter No-4 & Trecker 1,2,3 Row-P,Q,R,S,T, Inverter No-3 & total module cleaning -789 |  | 789 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2021-04-04 | 710 | 1053 | 1028 | 1225 | 65.59 | 4081.59 | 3900 | 181.59 | 4082 | 5.165 | 0.77029 | Grid failure from-16:35 to 17:27 & Grid failure from-17:30 to 17:33 & Grid failure from-17:42 to 17:47 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2021-04-05 | 772 | 1149 | 1145 | 1341 | 76.2 | 4483.2 | 4257.75 | 225.45 | 4484 | 5.535 | 0.78959 | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2021-04-06 | 781 | 1210 | 1179 | 1351 | 78.56 | 4599.56 | 4374 | 225.56 | 4600 | 5.588 | 0.80233 | Module cleaning has been done in Row-I,J,K, Inverter No-2 total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2021-04-07 | 811 | 1265 | 1205 | 1391 | 79.58 | 4751.58 | 4535.25 | 216.33 | 4752 | 5.65 | 0.81975 | Module cleaning has been done in Row- L, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -693 |  | 693 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2021-04-08 | 786 | 1190 | 1134 | 1295 | 74.43 | 4479.43 | 4257 | 222.43 | 4480 | 5.557 | 0.78576 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-1 & Row-A,B,C,D, Inverter No-4 & total module cleaning -1104 |  | 1104 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2021-04-09 | 772 | 1144 | 1088 | 1280 | 69.87 | 4353.87 | 4158 | 195.87 | 4354 | 5.369 | 0.7904 | Module cleaning has been done in Row-E,F,G,H,I,J,K Inverter No-4 total module cleaning -1134 |  | 1134 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2021-04-10 | 766 | 1134 | 1089 | 1296 | 72.02 | 4357.02 | 4141.5 | 215.52 | 4358 | 5.451 | 0.77923 | Module Cleaning has been done in Row-K,L, Inverter No-4 & Trecker 1,2,3 Row-O,P,Q,R,S,T, Inverter No-3 & total module cleaning -978 |  | 978 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2021-04-11 | 766 | 1149 | 1129 | 1305 | 75.55 | 4424.55 | 4229.25 | 195.3 | 4425 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2021-04-12 | 740 | 1114 | 1094 | 1245 | 69.58 | 4262.58 | 4052.25 | 210.33 | 4263 |  | % | Today we are chang the new (10) mc4 conecter in the inverter no-1,2,3 AJB no-105,106,107,113 &114 &Module Cleaning has been done in Row-M,N, Inverter No-1 & Row-J,K,L, Inverter No-4 & total module cleaning -1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2021-04-13 | 762 | 1154 | 1098 | 1255 | 67.09 | 4336.09 | 4109.25 | 226.84 | 4337 |  |  | Module Cleaning has been done in Row-I, Inverter No-2 & Row-D,E,F,G,H, Inverter No-1 & total module cleaning -1176 |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2021-04-14 | 750 | 1124 | 1084 | 1255 | 66.69 | 4279.69 | 4089 | 190.69 | 4280 |  |  | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F,G Inverter No-4 & total module cleaning -1200 |  | 1200 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2021-04-15 | 767 | 1134 | 1084 | 1275 | 71.74 | 4331.74 | 4125.75 | 205.99 | 4332 |  |  | Module Cleaning has been done in Row-I, Inverter No-2 & Row-H,I,J,K,L Inverter No-4 & Tracker-1,2,3 total module cleaning -924 |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2021-04-16 | 791 | 1180 | 1144 | 1381 | 76.61 | 4572.61 | 4347.75 | 224.86 | 4573 |  |  | Module cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2021-04-17 | 776 | 1179 | 1149 | 1361 | 74.32 | 4539.32 | 4325.25 | 214.07 | 4540 |  |  | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2021-04-18 | 761 | 1164 | 1129 | 1316 | 72.39 | 4442.39 | 4226.25 | 216.14 | 4443 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2021-04-19 | 777 | 1185 | 1122 | 1351 | 75.1 | 4510.1 | 4317 | 193.1 | 4511 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2021-04-20 | 751 | 1134 | 1101 | 1259 | 65.16 | 4310.16 | 4077.75 | 232.41 | 4311 | 5.209 | 0.80663 | Module Cleaning has been done in Row-I,J,K,L nverter No-2 & Row-H Inverter No-1 total module cleaning -1323 |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2021-04-21 | 786 | 1199 | 1124 | 1306 | 72.37 | 4487.37 | 4261.5 | 225.87 | 4488 | 5.211 | 0.83943 | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 total module cleaning -1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2021-04-22 | 771 | 1160 | 1099 | 1287 | 70.8 | 4387.8 | 4172.25 | 215.55 | 4388 | 5.134 | 0.83304 | Module cleaning has been done in Row-A,B,C,D Inverter No-4 total module cleaning -432 |  | 432 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2021-04-23 | 776 | 1159 | 1093 | 1299 | 72.18 | 4399.18 | 4173.75 | 225.43 | 4400 | 5.682 | 0.75475 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2021-04-24 | 615 | 847 | 802 | 927 | 42.13 | 3233.13 | 3072 | 161.13 | 3234 | 3.9 | 0.80822 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2021-04-25 | 736 | 1109 | 1043 | 1215 | 68.35 | 4171.35 | 3944.25 | 227.1 | 4172 | 5.178 | 0.7853 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2021-04-26 | 726 | 1068 | 1008 | 1169 | 65.97 | 4036.97 | 3836.25 | 200.72 | 4037 | 5.348 | 0.73573 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2021-04-27 | 695 | 1033 | 973 | 1139 | 61.25 | 3901.25 | 3701.25 | 200 | 3902 | 5.057 | 0.75205 | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-4 total module cleaning -990 |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2021-04-28 | 651 | 968 | 922 | 1124 | 49.15 | 3714.15 | 3545.25 | 168.9 | 3715 | 4.798 | 0.75466 | Grid failure from-05:04 to 05:08 & Module Cleaning has been done in Row-H,I,J,K,L Inverter No-4 & Tracker-1,2,3 total module cleaning -924 |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2021-04-29 | 695 | 991 | 1008 | 1205 | 63.76 | 3962.76 | 3787.5 | 175.26 | 3963 | 4.902 | 0.78796 | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2121-04-30 | 670 | 1061 | 1008 | 1179 | 61.84 | 3979.84 | 3752.25 | 227.59 | 3980 | 4.885 | 0.79409 | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2021-05-01 | 585 | 886 | 847 | 993 | 43.52 | 3354.52 | 3141.75 | 212.77 | 3355 | 4.072 | 0.80304 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 total module cleaning -483 & Grid failure from-03:26 to 03:32 |  | 483 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2021-05-02 | 741 | 1135 | 1089 | 1285 | 69.82 | 4319.82 | 4114.5 | 205.32 | 4320 | 5.408 | 0.77857 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2021-05-03 | 766 | 1154 | 1109 | 1316 | 71.27 | 4416.27 | 4189.5 | 226.77 | 4417 | 5.306 | 0.81136 | Grid failure from-07:15 to 07:20 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 2021-05-04 | 731 | 1124 | 1078 | 1270 | 69.88 | 4272.88 | 4069.5 | 203.38 | 4273 | 5.238 | 0.7951 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2021-05-05 | 766 | 1190 | 1139 | 1366 | 78.24 | 4539.24 | 4311 | 228.24 | 4540 | 5.684 | 0.77849 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2021-05-06 | 751 | 1168 | 1124 | 1336 | 76.55 | 4455.55 | 4245 | 210.55 | 4456 | 5.618 | 0.77307 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2021-05-07 | 736 | 1145 | 1099 | 1315 | 73.51 | 4368.51 | 4152 | 216.51 | 4369 | 5.454 | 0.78076 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2021-05-08 | 670 | 1018 | 978 | 1139 | 57.92 | 3862.92 | 3677.25 | 185.67 | 3863 | 5.037 | 0.74749 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2021-05-09 | 655 | 988 | 947 | 1197 | 58.69 | 3845.69 | 3562.5 | 283.19 | 3846 | 4.811 | 0.77916 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2021-05-10 | 737 | 1134 | 1089 | 1320 | 77.29 | 4357.29 | 4146.75 | 210.54 | 4358 | 5.473 | 0.77609 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2021-05-11 | 745 | 1144 | 1099 | 1336 | 77.3 | 4401.3 | 4197.75 | 203.55 | 4402 | 5.593 | 0.76711 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2021-05-12 | 746 | 1134 | 1089 | 1346 | 75.28 | 4390.28 | 4164.75 | 225.53 | 4391 | 5.507 | 0.77714 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-4 total module cleaning -1188 |  | 1188 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2021-05-13 | 731 | 1104 | 1063 | 1361 | 73.36 | 4332.36 | 4128 | 204.36 | 4333 | 5.354 | 0.78879 | Module cleaning has been done in Row-I,J,K,L Inverter No-4 tracker 1,2,3 & Row- R,S,T inverter No-3 total module cleaning -893 |  | 893 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2021-05-14 | 706 | 1083 | 1094 | 1315 | 72.25 | 4270.25 | 4050 | 220.25 | 4271 | 5.337 | 0.77998 | Module cleaning has been done in Row-M,N,O,P,Q, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1449 |  | 1449 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2021-05-15 | 645 | 1009 | 978 | 1139 | 54.36 | 3825.36 | 3616.5 | 208.86 | 3826 | 4.631 | 0.80524 | Module cleaning has been done in Row-I,J, Inverter No-2 & Row-D,E,F,G,H, inverter No-1 total module cleaning -1470 |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2021-05-16 | 524 | 786 | 751 | 867 | 37.29 | 2965.29 | 2807.25 | 158.04 | 2966 | 3.852 | 0.75048 | Grid failure from-04:42 to 04:46 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2021-05-17 | 303 | 418 | 393 | 449 | 14.46 | 1577.46 | 1423.5 | 153.96 | 1578 | 1.761 | 0.87337 | Grid failure from-09:19 to 09:26 & 09:33 to 09:37 & 09:38 to 10:02 & 11:18 to 11:24 & 11:24 to 12:27 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2021-05-18 | 120 | 141 | 141 | 146 | 3.3 | 551.3 | 408.75 | 142.55 | 552 | 5.51 | 0.097643 | Grid failure from-03:48 to 07:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2021-05-19 | 373 | 524 | 504 | 595 | 23.49 | 2019.49 | 1884 | 135.49 | 2020 | 2.266 | 0.86885 | Grid failure from-09:25 to 09:38 &09:48 to 10:02 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2021-05-20 | 752 | 1155 | 1124 | 1330 | 76.67 | 4437.67 | 4233 | 204.67 | 4338 | 5.447 | 0.77622 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2021-05-21 | 740 | 1149 | 1114 | 1351 | 73.05 | 4427.05 | 4217.25 | 209.8 | 4428 | 5.485 | 0.78683 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2021-05-22 | 686 | 1038 | 1023 | 1205 | 64.44 | 4016.44 | 3819.75 | 196.69 | 4017 | 5.017 | 0.78039 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-O,P,Q,R,S,T inverter No-3 total module cleaning -1302 |  | 1302 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2021-05-23 | 675 | 1064 | 1043 | 1240 | 65.29 | 4087.29 | 3897 | 190.29 | 4088 | 5.102 | 0.78095 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2021-05-24 | 696 | 1109 | 1069 | 1290 | 69.43 | 4233.43 | 4019.25 | 214.18 | 4234 | 5.458 | 0.75608 | Module Cleaning has been done in Row-J,K,L Inverter No-2 & Row-M,N Inverter No-3 total module cleaning -1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2021-05-25 | 731 | 1164 | 1114 | 1331 | 75.86 | 4415.86 | 4201.5 | 214.36 | 4416 | 5.692 | 0.75617 | Module Cleaning has been done in Row-I, Inverter No-2 & Row-A,B,C,D,E,F,G,H, Inverter No-1 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2021-05-26 | 650 | 998 | 957 | 1149 | 55.92 | 3809.92 | 3619.5 | 190.42 | 3810 | 4.763 | 0.77965 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 & Grid failure from-11:03 to 11:06 |  | 1386 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2021-05-27 | 685 | 1008 | 973 | 1220 | 61.1 | 3947.1 | 3741 | 206.1 | 3948 | 4.957 | 0.77627 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 & Grid failure from-01:28 to 01:32 |  | 1368 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2021-05-28 | 696 | 1048 | 1023 | 1219 | 60.31 | 4046.31 | 3845.25 | 201.06 | 4047 | 5.171 | 0.7628 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 & Grid failure from-04:53 to 05:22 |  | 1344 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2021-05-29 | 721 | 1059 | 1013 | 1215 | 63.41 | 4071.41 | 3865.5 | 205.91 | 4172 | 5.086 | 0.7995 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-1 total module cleaning -1113 & Today we are found 1 MC4 connecter born Inverter No-1 AJB-103 string no-3 +tive site we replaced 1-MC4 connecter and started the string |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2021-05-30 | 750 | 1103 | 1064 | 1260 | 69.94 | 4246.94 | 4044 | 202.94 | 4247 | 5.331 | 0.77647 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2021-05-31 | 747 | 1094 | 1048 | 1265 | 68.05 | 4222.05 | 4017 | 205.05 | 4223 | 5.244 | 0.78489 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2021-06-01 | 746 | 1094 | 1064 | 1305 | 70.37 | 4279.37 | 4068.75 | 210.62 | 4280 | 5.183 | 0.80485 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1368 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2021-06-02 | 746 | 1134 | 1114 | 1311 | 75.89 | 4380.89 | 4166.25 | 214.64 | 4381 | 5.014 | 0.85161 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2021-06-03 | 725 | 1089 | 1043 | 1235 | 68.58 | 4160.58 | 3965.25 | 195.33 | 4161 | 5.106 | 0.79427 | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 total module cleaning -1113 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2021-06-04 | 691 | 998 | 958 | 1149 | 60.88 | 3856.88 | 3660.75 | 196.13 | 3857 | 4.965 | 0.75715 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 & Grid failure from-04:14 to 04:38 |  | 1386 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 2021-06-05 | 766 | 1154 | 1119 | 1351 | 47.18 | 4437.18 | 3660.75 | 776.43 | 4438 | 5.098 | 0.84848 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2021-06-06 | 726 | 1073 | 1038 | 1260 | 67.93 | 4164.93 | 3960 | 204.93 | 4165 | 4.656 | 0.87188 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2021-06-07 | 690 | 1029 | 998 | 1189 | 63.17 | 3969.17 | 3790.5 | 178.67 | 3970 | 4.836 | 0.80012 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2021-06-08 | 681 | 1003 | 968 | 1140 | 61.84 | 3853.84 | 3643.5 | 210.34 | 3854 | 4.488 | 0.83697 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning -1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2021-06-09 | 670 | 973 | 927 | 1119 | 60.28 | 3749.28 | 3550.5 | 198.78 | 3750 | 4.403 | 0.83011 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2021-06-10 | 650 | 937 | 905 | 1113 | 58.34 | 3663.34 | 3455.25 | 208.09 | 3663 | 4.435 | 0.805 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2021-06-11 | 676 | 1008 | 975 | 1210 | 64.03 | 3933.03 | 3729 | 204.03 | 3934 | 5.021 | 0.76365 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1368 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2021-06-12 | 675 | 1003 | 956 | 1164 | 61.53 | 3859.53 | 3677.25 | 182.28 | 3860 | 4.939 | 0.76173 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2021-06-13 | 650 | 952 | 944 | 1084 | 53.01 | 3683.01 | 3469.5 | 213.51 | 3684 | 4.606 | 0.77956 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning -1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2021-06-14 | 686 | 1004 | 968 | 1164 | 60.61 | 3882.61 | 3682.5 | 200.11 | 3883 | 4.79 | 0.7901 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2021-06-15 | 685 | 1003 | 973 | 1185 | 62.79 | 3908.79 | 3708.75 | 200.04 | 3909 | 4.885 | 0.77993 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2021-06-16 | 650 | 947 | 917 | 1108 | 52.48 | 3674.48 | 3474.75 | 199.73 | 3675 | 4.595 | 0.77951 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2021-06-17 | 413 | 595 | 575 | 696 | 28.34 | 2307.34 | 2142.75 | 164.59 | 2308 | 3.432 | 0.65545 | Grid failure from-07:30 to 07:59 & 01:14 to 02:28 & 02:52 to 02:55 & 03:06 to 03:10 & 04:06 to 04:10 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2021-06-18 | 509 | 701 | 680 | 791 | 27.31 | 2708.31 | 2553 | 155.31 | 2709 | 3.09 | 0.85448 | Grid failure from-03:34 to 03:36 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 2021-06-19 | 298 | 393 | 378 | 434 | 13.2 | 1516.2 | 1366.5 | 149.7 | 1517 | 1.856 | 0.79664 | Grid failure from-11:02 to 11:17 & 12:57 to 01:36 & 02:17 to 02:19 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 2021-06-20 | 398 | 529 | 514 | 585 | 18.2 | 2044.2 | 1947.75 | 96.45 | 2045 | 2.213 | 0.90067 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2021-06-21 | 378 | 585 | 560 | 660 | 28.8 | 2211.8 | 2082.75 | 129.05 | 2212 | 2.891 | 0.74574 | Grid failure from-12:16 to 02:05 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 2021-06-22 | 514 | 730 | 710 | 836 | 33.34 | 2823.34 | 2648.25 | 175.09 | 2824 | 3.443 | 0.79943 | Grid failure from-08:12 to 08:19 & 12:47 to 12:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 2021-06-23 | 701 | 993 | 963 | 1139 | 52.02 | 3848.02 | 3606 | 242.02 | 3849 | 4.658 | 0.80538 | Grid failure from-04:44 to 04:46 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 2021-06-24 | 539 | 711 | 685 | 807 | 33.97 | 2775.97 | 2616 | 159.97 | 2776 | 3.251 | 0.83225 | Grid failure from-01:18 to 01:21 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 2021-06-25 | 681 | 1003 | 963 | 1139 | 57.02 | 3843.02 | 3651 | 192.02 | 3844 | 4.722 | 0.79343 | Module Cleaning has been done in Row-I,J,K, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2021-06-26 | 645 | 938 | 897 | 1069 | 55.52 | 3604.52 | 3412.5 | 192.02 | 3605 | 4.423 | 0.7944 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E Inverter No-4 total module cleaning -1266 |  | 1266 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2021-06-27 | 710 | 1063 | 1023 | 1214 | 59.21 | 4069.21 | 3888.75 | 180.46 | 4070 | 5.144 | 0.77116 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 2021-06-28 | 379 | 489 | 469 | 539 | 16.32 | 1892.32 | 1785.75 | 106.57 | 1893 | 2.141 | 0.86176 | Module cleaning has been done in Row-F,G,H,I,J,K,L Inverter No-4 tracker 1,2,3 total module cleaning -1320 |  | 1320 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 2021-06-29 | 579 | 821 | 797 | 948 | 40.19 | 3185.19 | 2962.5 | 222.69 | 3186 | 3.755 | 0.82697 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2021-06-30 | 630 | 918 | 892 | 1053 | 53.73 | 3546.73 | 3392.25 | 154.48 | 3547 | 4.29 | 0.80585 | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2021-07-01 | 595 | 887 | 857 | 1024 | 39.361 | 3402.361 | 3198 | 204.361 | 3403 | 4.635 | 0.71559 | Module cleaning has been done in Row-I,J,K,L inverter No-2 total module cleaning -1092 & Grid failure from-03:04 to 04:02 & 05:20 to 05:25 |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2021-07-02 | 635 | 938 | 902 | 1073 | 50.24 | 3598.24 | 3410.25 | 187.99 | 3599 | 4.415 | 0.79452 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,inverter No-1 total module cleaning -1113 & Grid failure from-05:21 to 05:31 |  | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2021-07-03 | 640 | 967 | 937 | 1119 | 54.18 | 3717.18 | 3506.25 | 210.93 | 3718 | 4.62 | 0.78437 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-4 total module cleaning -1188 |  | 1188 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2021-07-04 | 645 | 998 | 968 | 1149 | 61.41 | 3821.41 | 3652.5 | 168.91 | 3822 | 4.783 | 0.77883 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 2021-07-05 | 610 | 948 | 912 | 1104 | 57.24 | 3631.24 | 3419.25 | 211.99 | 3632 | 4.904 | 0.72185 | Module cleaning has been done in Row-I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-P,Q,R,S,T, total module cleaning -1167 & Grid failure from-01:11 to 01:12 & 03:32 to 04:09 |  | 1167 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 2021-07-06 | 645 | 1028 | 1008 | 1200 | 62.57 | 3943.57 | 3761.25 | 182.32 | 3944 | 5.098 | 0.75403 | Module Cleaning has been done in Row-M,N,OInverter No-3 & Row-K,L inverter no-2 total module cleaning -1176 |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 2021-07-07 | 671 | 1073 | 1039 | 1230 | 64.96 | 4077.96 | 3858 | 219.96 | 4078 | 5.084 | 0.7818 | Module Cleaning has been done in Row-I,J Inverter No-2 & Row-E,F,G,H inverter no-1 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2021-07-08 | 685 | 1033 | 992 | 1189 | 58.36 | 3957.36 | 3731.25 | 226.11 | 3958 | 4.934 | 0.78186 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 & Row-A,B,C,D,E,F,G, inverter no-4 total module cleaning -1326 |  | 1326 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2021-07-09 | 655 | 994 | 963 | 1159 | 55.54 | 3826.54 | 3661.5 | 165.04 | 3827 | 4.806 | 0.77612 | Module cleaning has been done in Row-H,I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-Q,R,S,T, inverter No-3 total module cleaning -1218 |  | 1218 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2021-07-10 | 605 | 917 | 902 | 1074 | 43.43 | 3541.43 | 3371.25 | 170.18 | 3542 | 4.464 | 0.77335 | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 & Row-K,L, inverter no-2 total module cleaning -1323 |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2021-07-11 | 529 | 751 | 726 | 852 | 32.45 | 2890.45 | 2736 | 154.45 | 2891 | 3.426 | 0.82246 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2021-07-12 | 474 | 695 | 676 | 791 | 31.4 | 2667.4 | 2493.75 | 173.65 | 2668 | 3.196 | 0.81364 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 2021-07-13 | 640 | 983 | 947 | 1149 | 56.22 | 3775.22 | 3565.5 | 209.72 | 3776 | 4.738 | 0.77676 | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-E,F,G,H, inverter no-1 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2021-07-14 | 646 | 998 | 968 | 1149 | 53.38 | 3814.38 | 3607.5 | 206.88 | 3815 | 4.715 | 0.78862 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 2021-07-15 | 634 | 1003 | 968 | 1165 | 53.11 | 3823.11 | 3681 | 142.11 | 3824 | 4.803 | 0.77599 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 2021-07-16 | 545 | 852 | 831 | 993 | 42.64 | 3263.64 | 3075 | 188.64 | 3264 | 4.131 | 0.7701 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 2021-07-17 | 554 | 817 | 791 | 937 | 43.87 | 3142.87 | 2953.5 | 189.37 | 3143 | 2.871 | 1.067 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2021-07-18 | 373 | 509 | 494 | 575 | 21.28 | 1972.28 | 1845 | 127.28 | 1973 | 1.933 | 0.99483 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 2021-07-19 | 464 | 654 | 635 | 746 | 24.46 | 2523.46 | 2355 | 168.46 | 2524 | 2.824 | 0.87112 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-1 & Row-A,B,C,D,E,F, inverter no-4 total module cleaning -1266 |  | 1266 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 2021-07-20 | 287 | 374 | 363 | 408 | 11.07 | 1443.07 | 1329.75 | 113.32 | 1444 | 1.585 | 0.88795 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 2021-07-21 | 418 | 569 | 550 | 630 | 20.84 | 2187.84 | 2020.5 | 167.34 | 2188 | 2.526 | 0.84424 | Grid failure from-09:37 to 09:49 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 2021-07-22 | 600 | 857 | 831 | 978 | 39.71 | 3305.71 | 3129.75 | 175.96 | 3306 | 3.944 | 0.81699 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 total module cleaning - 790 |  | 790 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 2021-07-23 | 338 | 443 | 424 | 479 | 14.07 | 1698.07 | 1578 | 120.07 | 1699 | 1.855 | 0.89269 | Module cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-R,S,T, inverter No-3 total module cleaning -1230 & Grid failure from-02:31 to 02:34 |  | 1230 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 2021-07-24 | 514 | 737 | 715 | 836 | 31.01 | 2833.01 | 2656.5 | 176.51 | 2834 | 3.393 | 0.81408 | Module cleaning has been done in Row-M,N,O,P,Q, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1449 & Grid failure from-01:24 to 01:37 |  | 1449 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2021-07-25 | 141 | 171 | 161 | 187 | 4.82 | 664.82 | 559.5 | 105.32 | 665 | 0.741 | 0.87469 | Today U.P.S maintenanc from -09:28 to 10:12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 2021-07-26 | 151 | 197 | 191 | 211 | 5.58 | 755.58 | 619.5 | 136.08 | 756 | 0.902 | 0.8169 | Grid failure from -02:00 to 02:31 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 2021-07-27 | 343 | 463 | 454 | 525 | 15.71 | 1800.71 | 1656.75 | 143.96 | 1801 | 1.967 | 0.8924 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 2021-07-28 | 277 | 373 | 358 | 403 | 11.11 | 1422.11 | 1284.75 | 137.36 | 1423 | 1.556 | 0.89135 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 2021-07-29 | 172 | 222 | 217 | 237 | 6.23 | 854.23 | 714 | 140.23 | 855 | 0.945 | 0.88183 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 2021-07-30 | 302 | 403 | 388 | 438 | 12.84 | 1543.84 | 1408.5 | 135.34 | 1544 | 1.874 | 0.80303 | Grid failure from -03:49 to 04:52 & 05:38 to 05:41 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 2021-07-31 | 393 | 524 | 524 | 610 | 19.44 | 2070.44 | 1910.25 | 160.19 | 2071 | 2.376 | 0.84954 | Grid failure from -06:28 to 07:28 & 10:22 to 10:31 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 2021-08-01 | 414 | 560 | 559 | 660 | 20.94 | 2213.94 | 2067 | 146.94 | 2214 | 2.637 | 0.81831 | Grid failure from -09:22 to 09:35 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 2021-08-02 | 232 | 277 | 283 | 333 | 10.16 | 1135.16 | 1018.5 | 116.66 | 1136 | 0.787 | 1.4069 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 2021-08-03 | 317 | 419 | 418 | 504 | 15.27 | 1673.27 | 1523.25 | 150.02 | 1674 | 1.953 | 0.83542 | Today replace 3phase motor coil chang. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 2021-08-04 | 388 | 509 | 514 | 620 | 21.94 | 2052.94 | 1903.5 | 149.44 | 2053 | 2.485 | 0.80522 | Grid failure from -09:21 to 09:26 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2021-08-05 | 479 | 659 | 645 | 791 | 31.47 | 2605.47 | 2467.5 | 137.97 | 2606 | 3.225 | 0.78758 | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-F,G,H, inverter no-1 total module cleaning -1197 & Today we are found 1 MC4 connecter born Inverter No-2 AJB-112 string no-7 +tive & -tive site we replaced 2-MC4 connecter and started the string |  | 1197 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 2021-08-06 | 479 | 641 | 615 | 751 | 29.78 | 2515.78 | 2346 | 169.78 | 2516 | 3.065 | 0.80008 | Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-1 & Row-Q,R,S,T, inverter no-3 total module cleaning -777 & Today we are clening all inverter door filters. |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 2021-08-07 | 483 | 655 | 640 | 771 | 29.53 | 2578.53 | 2419.5 | 159.03 | 2579 | 3.243 | 0.7751 | Module Cleaning has been done in Row-M,N,O,P, inverter no-3 total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 2021-08-08 | 530 | 756 | 736 | 867 | 34.18 | 2923.18 | 2744.25 | 178.93 | 2859 | 3.709 | 0.75129 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 2021-08-09 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 2021-08-10 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 2021-08-11 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 2021-08-12 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 2021-08-13 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 2021-08-14 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 2021-08-15 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 2021-08-16 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 2021-08-17 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 2021-08-18 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 2021-08-19 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 2021-08-20 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 2021-08-21 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 2021-08-22 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 2021-08-23 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 2021-08-24 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 2021-08-25 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 2021-08-26 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 2021-08-27 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 2021-08-28 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 2021-08-29 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 2021-08-30 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 2021-08-31 | [5 empty] | 0 |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0