## 2012
Project Name |  | PDPU-SEIPL, Gujarat 2010
Project Number |  | IN-10-0061
Capacity |  | 1026 | KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 1104500525 | 7802195 | 2100570073/ 2100567820/ 2100567898
2012-07-06 | 679 | 825 | 837 | 869 | 8 | 3218 | 3135 | 83 |  |  |  | Grid failure from 14.10 to 14.15 hours. Communication down, problem with SEEDS Gateway
2012-07-07 | 882 | 899 | 910 | 924 | 18 | 3633 | 3540 | 93 |  |  |  | Grid failure from 13-37 to 13-42 hours. Communication down, problem with SEEDS Gateway
2012-07-08 | 1051 | 1080 | 1091 | 1129 | 26 | 4377 | 4245 | 132 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway
2012-07-09 | 1114 | 1136 | 1148 | 1172 | 55 | 4625 | 4485 | 140 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway
2012-07-10 | 153 | 159 | 170 | 162 | 4 | 648 | 600 | 48 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway
2012-07-11 | 718 | 723 | 746 | 800 | 25 | 3012 | 2925 | 87 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway
2012-07-12 | 848 | 877 | 882 | 898 | 40 | 3545 | 3450 | 95 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway
2012-07-13 | 995 | 1017 | 1029 | 19.93 | 40 | 3100.93 | 2985 | 115.93 |  |  |  | Inverter 7802195 Break Down because of its S.M.P.S. found failed due to Moisture.
2012-07-14 | 927 | 944 | 955 | 72.03 | 42 | 2940.03 | 2850 | 90.03 | 2974 | 4.723 | 61.37% | Inverter 7802195 started from 16.54, after replacing the S.M.P.S & Front panel Display unit
2012-07-15 | 814 | 826 | 842 | 849 | 26 | 3357 | 3270 | 87 | 3402 | 3.942 | 84.11% | Grid Supply Failure from- 08.42 am to 08.46 am.
2012-07-16 | 791 | 825 | 831 | 826 | 35 | 3308 | 3285 | 23 | 3203 | 3.84 | 81.3% | Inverter 1104500527 was shut down from 15.24 to 15.26 & 15.29 to 15.31 for checking the Ethernet Adaptor (RETA-01)
2012-07-17 | 1114 | 1142 | 1154 | 1158 | 57 | 4625 | 4500 | 125 | 4654 | 5.546 | 81.79%
2012-07-18 | 893 | 916 | 921 | 919 | 40 | 3689 | 3570 | 119 | 3695 | 4.337 | 83.03% | M/s.Schneider has Came for Service The Inv-4,Then He Shut Downed The Inv From-17-25 to 21-00.
2012-07-19 | 826 | 842 | 860 | 735 | 37.01 | 3300.01 | 3240 | 60.01 | 3349 | 4.054 |  | M/s.Schneider has Came for Observation,Then he Shut-downed the INV-4 ,From 13-05 TO 13-25 for Data log in,,,,,,,Grid Also Failure From- 18-20 to 18-24
2012-07-20 | 910 | 939 | 961 | 944 | 41 | 3795 | 3690 | 141 | 3831 | 4.48
2012-07-21 | 870 | 899 | 944 | 941 | 44 | 3698 | 3630 | 123 | 3753 | 4.534
2012-07-22 | 617 | 644 | 656 | 623 | 22.1 | 2562.1 | 2505 | 57.1 | 2617 | 3.009 | 84.76 | Grid Supply Failure From - 10-20 TO 10-26.
2012-07-23 | 435 | 458 | 458 | 435 | 13.21 | 1799.21 | 1755 | 44.21 | 1843 | 2.062 | 87.11 | Grid Supply Failure From - 14-28 TO 14-33.
2012-07-24 | 661 | 678 | 689 | 667 | 23.449 | 2718.44 | 2640 | 78.44 | 2745 | 3.155 | 84.79
2012-07-25 | 843 | 860 | 865 | 862 | 34.61 | 3464.61 | 3375 | 89.61 | 3503 | 3.958 | 86.26 | Grid Supply Failure From- 15-39 To 15-44.
2012-07-26 | 933 | 950 | 950 | 937 | 38.76 | 3808.76 | 3705 | 103.76 | 3828 | 4.474 | 83.39
2012-07-27 | 944 | 961 | 972 | 972 | 43.06 | 3892.06 | 3780 | 112.06 | 3917 | 4.604 | 82.92
2012-07-28 | 429 | 435 | 441 | 485 | 13.41 | 1803.41 | 1710 | 93.41 | 1789 | 2.031
2012-07-29 | 317 | 328 | 334 | 279 | 7.86 | 1265.86 | 1275 | 9.14 | 1359 | 1.519
2012-07-30 | 407 | 418 | 435 | 419 | 12.55 | 1691.55 | 1635 | 56.55 | 1724 | 1.871 | 89.8
2012-07-31 | 345 | 385 | 385 | 379 | 9.07 | 1503.07 | 1470 | 33.07 | 1542 | 1.875 | 80.15 | Inv-1 & 4 Break downed From 13-05 to 13-12 due High Grid Frquancy Fault.
2012-08-01 | 610 | 627 | 644 | 633 | 14.04 | 2528.04 | 2460 | 68.04 | 2564 | 2.302 | 108.55
2012-08-02 | 973 | 990 | 989 | 965 | 2.53 | 3919.53 | 3810 | 109.53 |  |  |  | Because of Unbalanced Frequancy of GRID, Inv-4, went in F1.Hi Grid Freequancy fault mode 4th time.Tracker`s Inverters also Went in Grid fault mode severly. And Internet Radio link Also Failure from PDPU.From 11-00,O`Clock.-2-8-12 To 18-00,O`Clock Today -3-8-12 ,SEEDS data does not Available now.
2012-08-03 | 531 | 542 | 554 | 541 | 6.04 | 2174.04 | 2130 | 44.04 | 2932 |  |  | Plant Shut Downed From -11-25 to 11-33, For Rectification of Sparking Problem in the D.O.Fuse Holder of `R`Phase,,,,,Grid Failure From-12-18 to 12-23 & 16-45 to 16-57.
2012-08-04 | 814 | 837 | 849 | 841 | 16.49 | 3357.49 | 3255 | 102.49 | 3399 | 3.945 | 83.97 | Internet Failure From- 12-30 to 13-00.
2012-08-05 | 656 | 673 | 684 | 675 | 13.47 | 2701.47 | 2640 | 61.47 | 2753 | 3.183 | 84.29
2012-08-06 | 995 | 1017 | 1023 | 1041 | 25.27 | 4101.27 | 3990 | 111.27 | 4133 | 4.625 | 87.09 | Plant Shut Downed From- 09-00 to 09-07 ,For Replaced The `R`,D.O.Fuse assembly .
2012-08-07 | 718 | 741 | 752 | 763 | 19.67 | 2993.61 | 2925 | 68.61 | 3049 | 3.473 | 85.56
2012-08-08 | 475 | 492 | 492 | 495 | 5.31 | 1959.31 | 1890 | 69.31 | 2016 | 2.226 | 82.27 | Grid Supply Failure From- 17-18 to 18-30.
2012-08-09 | 543 | 559 | 571 | 552 | 2.47 | 2227.47 | 2160 | 67.47 | 2288 | 2.514 | 88.7 | Because of High Grid Voltages (256 V to 257 V) All 03,No`s fo Trackers SMA Inverters- Went to Fault ,Grid Disturbance From 12-15 to 00-00.
2012-08-10 | 870 | 854 | 825 | 902 | 0 | 3451 | 3345 | 106 | 3515 | 4.022 | 85.17 | Because of High Grid Voltages (260 V to 262 V) All 03,No`s fo Trackers SMA Inverters- Went to Fault ,Grid Disturbance From 00-00 to 19-30. And INV-2 & 3 Went to Fault-ID-2 Mode during 11-43 to 11-55 & 13-35 to 13-38, Inv-4 Also Went to Stand by Mode From -17-18 to 17-20.
2012-08-11 | 543 | 560 | 571 | 557 | 0.39 | 2231.39 | 2160 | 71.39 | 2279 | 2.549 | 87.14 | Because of High Grid Voltages (>252V) All o3,No`s of Trackers Inverters went to Fault Grid Diturbance From 00-00 to 11-15,,,,,,,11-30 to 16-30,,,,,,,,,17-00 to 18-00,,,,,,,, & 18-15 to 19-30.
2012-08-12 | 192 | 198 | 209 | 205 | 0.99 | 804.99 | 765 | 39.99 |  |  |  | Internet Failure From- 11-00 to 00-00……….. Grid Supply Failure From -16-13 to 16-33.
2012-08-13 | 300 | 311 | 317 | 306 | 7.04 | 1241.04 | 1230 | 11.04 | 1251 |  |  | Internet Started From-10-30….Grid Supply Failure From-16-50 to 16-55.
2012-08-14 | 277 | 288 | 294 | 281 | 6.06 | 1146.06 | 1095 | 51.06 | 1197 | 1.344 | 86.8
2012-08-15 | 565 | 582 | 593 | 580 | 2.72 | 2322.72 | 2265 | 57.72 | 2382 | 2.836 | 81.86 | Plant Break Downed From -11-34 To 11-42 B`coz of Blown off The D.O.Fuse of `R` Phase.
2012-08-16 | 639 | 656 | 662 | 645 | 18.48 | 2620.48 | 2535 | 85.48 | 2664 | 3.032 | 85.63
2012-08-17 | 752 | 775 | 786 | 780 | 21.01 | 3114.01 | 3030 | 84.01 | 3167 | 3.633
2012-08-18 | 899 | 927 | 944 | 949 | 19.47 | 3738.47 | 3660 | 78.47 | 3806 | 4.299 |  | Grid Supply Failure From-15-02 To 15-22.
2012-08-19 | 1142 | 1170 | 1176 | 1167 | 0.2 | 4655.2 | 4515 | 140.2 | 4706 | 5.6356 | 81.39 | Out of Few Minutes All 03,No`s fo Trackers SMA Inverters- Went to Fault ,Grid Disturbance Because of High Grid Voltages (254 V to 260 V )
2012-08-20 | 831 | 854 | 859 | 866 | 2.26 | 3412.26 | 3330 | 82.26 | 3471 | 4.121 | 82.09
2012-08-21 | 927 | 944 | 944 | 986 | 25.3 | 3826.3 | 3735 | 91.3 | 3483 |  |  | Grid Supply Failure From- 08-25 to 08-30,,,,10-12 to 10-17,,,,,,10-27 to 10-32 & 11-07 to 11-51,,,,, Our CPU has Hanged From-13-17 then we Sent to PDPU server Room for Repaired it.
2012-08-22 | 452 | 469 | 475 | 463 | 7.55 | 1866.55 | 1815 | 51.55 | 2306
2012-08-23 | 911 | 933 | 944 | 956 | 33.29 | 3777.29 | 3690 | 87.29 | 3812
2012-08-24 | 910 | 927 | 933 | 957 | 33.41 | 3760.41 | 3660 | 100.41 | 3787 | 4.505 | 81.93 | All Inverters Went to Fault Mode From - 15-10 to 15-20 & 15-25 to 15-30 due to Law Grid Freequancy.
2012-08-25 | 650 | 673 | 684 | 666 | 15.02 | 2688.02 | 2625 | 63.02 | 2679
2012-08-26 | 808 | 825 | 837 | 833 | 14.13 | 3317.13 | 3255 | 62.13 | 3427 |  |  | Grid Suplly Failure From - 08-35 to 08-40.
2012-08-27 | 1035 | 1057 | 1057 | 1086 | 34.84 | 4269.84 | 4140 | 129.84 | 4298 | 5.116 | 81.88
2012-08-28 | 424 | 441 | 447 | 445 | 12.23 | 1769.23 | 1755 | 14.23 | 1824 | 2.076 | 85.63 | Grid Supply Failure From -13-30 13-35 & 14-06 to 14-16
2012-08-29 | 904 | 933 | 944 | 936 | 37.95 | 3754.95 | 3675 | 79.95 | 3792 | 4.36 | 84.76
2012-08-30 | 922 | 950 | 949 | 955 | 35.94 | 3811.94 | 3720 | 91.94 | 3856 | 4.543 | 82.72 | Grid Supply Failure From -11-27 to 11-42.
2012-08-31 | 622 | 644 | 656 | 644 | 24.99 | 2590.99 | 2520 | 70.99 | 2627 | 3.078 |  | Grid Supply Failure From -14-54 to 15-00 & 15-05 to 15-10
2012-09-01 | 876 | 899 | 905 | 930 | 19.28 | 3629.28 | 3555 | 74.28 | 3684 | 4.313 |  | Grid supply Failure From -10-45 to 11-15.
2012-09-02 | 803 | 826 | 831 | 819 | 18.59 | 3297.59 | 3225 | 72.59 | 3343 | 3.895
2012-09-03 | 712 | 735 | 740 | 731 | 11.84 | 2929.84 | 2865 | 64.84 | 2963 | 3.415 | 84.56
2012-09-04 | 905 | 932 | 944 | 930 | 18.09 | 3729.09 | 3645 | 84.09 | 3764 | 4.216 | 87.01
2012-09-05 | 1040 | 1069 | 1080 | 1095 | 23.74 | 4307.74 | 4200 | 107.74 | 4347 | 5.06
2012-09-06 | 283 | 294 | 300 | 291 | 5.04 | 1173.04 | 1140 | 33.04 | 1218 | 1.441 | 82.38 | Grid Supply Failure From - 10-20 to 10-25.
2012-09-07 | 226 | 237 | 243 | 237 | 4.21 | 947.21 | 915 | 32.21 | 966 | 1.195 | 78.78 | I shut downed the Plant From-12-45 to 12-55, For solved the chattering problem in Fuse Holder of-11-kv, `R` D.O.Fuse.
2012-09-08 | 757 | 780 | 786 | 772 | 15.87 | 3110.87 | 3030 | 80.87 | 3167 | 3.789 | 81.46 | Grid Supply Failure From- 11-06 to 11-22 & 11-25 to 11-28. And also Blown off The .D.O.Fuse of `R` Phase .
2012-09-09 | 283 | 289 | 288 | 295 | 4.96 | 1159.96 | 1125 | 34.96 | 1217 | 1.417 | 83.7 | Grid Supply Failure From- 14-01 to14-05.
2012-09-10 | 396 | 407 | 413 | 401 | 11.66 | 1628.66 | 1605 | 23.66 | 1676 | 1.64 | 99.6
2012-09-11 | 492 | 503 | 509 | 498 | 11.88 | 2013.88 | 1965 | 48.88 | 2060 | 2.297 |  | Grid Supply Failure From- 15-35 to 15-40.
2012-09-12 | 684 | 707 | 695 | 710 | 11.07 | 2807.07 | 2745 | 62.07 | 2834 | 3.221 | 85.75
2012-09-13 | 610 | 627 | 611 | 618 | 10.76 | 2476.76 | 2430 | 46.76 | 2536 | 2.912 | 84.88 | Grid Supply Failure From -13-07 to 13-12.
2012-09-14 | 871 | 893 | 859 | 904 | 4.55 | 3531.55 | 3435 | 96.55 | 3570 | 4.363 | 79.75 | Because of Heavy Cloud All Inverters Went to Sleep mode Severaly during the Period of ,,,,,,,,,17-00 to 17-40.
2012-09-15 | 1080 | 1108 | 1080 | 1120 | 19.66 | 4407.66 | 4305 | 102.66 | 4469
2012-09-16 | 1080 | 1114 | 1074 | 1118 | 8.2 | 4394.2 | 4290 | 104.2 | 4441 | 5.395 | 80.23 | Because Of High Grid Voltages >256V All SMA Inverters-No-5 Went to Grid Disturbance Mode for Sevral Time .
2012-09-17 | 1226 | 1261 | 1215 | 1263 | 8.95 | 4973.95 | 4845 | 128.95 | 5010 | 6.15 | 79.4%
2012-09-18 | 1148 | 1187 | 1159 | 1172 | 21.26 | 4687.26 | 4575 | 112.26 | 4732 | 5.872 | 78.54 | Grid Supply Failure From -10-34 to 10-40.
2012-09-19 | 950 | 978 | 984 | 950 | 15.31 | 3877.31 | 3780 | 97.31 | 3903 | 4.736 | 80.32
2012-09-20 | 1102 | 1137 | 1142 | 1136 | 27.05 | 4544.05 | 4440 | 104.05 | 4569 | 5.622 | 79.21 | Grid Supply Failure From - 17-38 to 17-43.
2012-09-21 | 809 | 836 | 848 | 814 | 24.23 | 3331.23 | 3240 | 91.23 | 3371 | 4.021 | 81.71
2012-09-22 | 870 | 893 | 899 | 890 | 22.59 | 3574.59 | 3495 | 79.59 | 3614 | 4.392 | 80.2
2012-09-23 | 905 | 933 | 944 | 931 | 11.41 | 3724.41 | 3630 | 94.41 | 3771 | 4.512 | 81.45
2012-09-24 | 1068 | 1103 | 1108 | 1108 | 29.79 | 4416.79 | 4305 | 111.79 | 4458 | 4.856
2012-09-25 | 1159 | 1193 | 1199 | 1227 | 20.42 | 4798.42 | 4695 | 103.42 | 4853 | 5.847 | 80.89
2012-09-26 | 1193 | 1232 | 1243 | 1235 | 32.94 | 4935.94 | 4800 | 135.94 | 4973 | 5.848 | 82.88
2012-09-27 | 1170 | 1210 | 1210 | 1220 | 30.84 | 4840.84 | 4710 | 130.84 | 4871 | 6.167 | 76.98 | Grid Supply Failure From - 17-31 to 17-41.
2012-09-28 | 1295 | 1334 | 1346 | 1351 | 25.34 | 5351.34 | 5220 | 131.34 | 5370 | 6.565 |  | Grid Supply Failure From -10-40- to 10-45.
2012-09-29 | 1328 | 1374 | 1390 | 1367 | 27.16 | 5486.16 | 5340 | 146.16 | 5366 |  |  | Grid Supply Failure From- 17-30 to 17-35 & 17-36 to 17-50, & Also Filure The Net From PDPU , Because of Shut Downed The Server for It`s Service Purpose.
2012-09-30 | 1301 | 1357 | 1363 | 1344 | ERROR | 5365 | 5235 | 130 |  |  |  | Plant Break Downed From -09-30 to 09-45, Due to Blown off The D.O.Fuse of `B` Phase.
2012-10-01 | 1266 | 1323 | 1317 | 1328 | 39 | 5273 | 5130 | 143 | 5304 | 6.646 | 77.78 | Plant Break Downed From -10-50 to 11-05,Because of Loose soldaring of ,D.,O.Fuselink it`s Blown off Again.
2012-10-02 | 1114 | 1158 | 1153 | 1155 | 14.46 | 4594.46 | 4485 | 109.46 | 4636 | 5.711 | 79.12% | Grid failure from 16.11 to 16. 49
2012-10-03 | 1147 | 1188 | 1182 | 1172 | 58.21 | 4747.21 | 4620 | 127.21 | 4777 | 6.089 | 76.46 | Plant Break Downed From -11-08 to 11-23,Because of Loose soldaring of ,D.,O.Fuselink it`s Blown off Again.
2012-10-04 | 1273 | 1283 | 1272 | 1283 | 55.47 | 5166.47 | 5025 | 141.47 | 5193 | 6.582 | 76.89
2012-10-05 | 1294 | 1306 | 1289 | 1325 | 45.16 | 5259.16 | 5115 | 144.16 | 5296 | 6.67 | 77.38
2012-10-06 | 1176 | 1181 | 1176 | 1183 | 36.77 | 4752.77 | 4635 | 117.77 | 4788 | 6.188 | 75.41 | Grid Supply Failure From - 11-45 to 11-50.
2012-10-07 | 769 | 781 | 769 | 801 | 27.65 | 3147.65 | 3060 | 87.65 | 3187 | 3.911 | 79.42 | Grid Supply Failure From - 10-57 to 11-24.
2012-10-08 | 1193 | 1204 | 1193 | 1254 | 47.31 | 4891.31 | 4770 | 121.31 | 4929 | 6.198 | 77.51 | Grid Supply Failure From -09-55 to 10-00.
2012-10-09 | 1215 | 1227 | 1221 | 1293 | 30.16 | 4986.16 | 4845 | 141.16 | 5000 | 6.364 | 76.57 | Grid Supply Failure From -11-28 to 11-33,,,,,,15-20 to 15-33,,,,,,,,,,16-53 to 16-58 & 17-14 to 17-19.
2012-10-10 | 1289 | 1328 | 1340 | 1379 | 61.56 | 5397.56 | 5250 | 147.56 | 5401 |  |  | Grid Supply Failure From- 11-18 to 11-23.
2012-10-11 | 1255 | 1295 | 1317 | 1338 | 48.21 | 5253.21 | 5115 | 138.21 | 5274 | 5.58 |  | Grid Supply Failure From- 16-52 to 17-15.
2012-10-12 | 1187 | 1227 | 1278 | 1102 | 53.12 | 4847.12 | 4710 | 137.12 | 4867 | 6.318 | 75.08
2012-10-13 | 1165 | 1249 | 1272 | 1212 | 54.79 | 4952.79 | 4800 | 152.79 | 4970 | 6.214 | 77.95 | Grid Supply Failure From- 10-03 to 10-08.
2012-10-14 | 1182 | 1283 | 1272 | 1246 | 49.54 | 5032.54 | 4905 | 127.54 | 5058 | 6.255 | 78.81
2012-10-15 | 1198 | 1312 | 1300 | 1276 | 53.15 | 5139.15 | 4980 | 159.15 | 5151 | 6.432 | 78.05
2012-10-16 | 1199 | 1317 | 1300 | 1305 | 55.21 | 5176.21 | 5025 | 151.21 | 5192 | 6.511 | 77.72
2012-10-17 | 1170 | 1272 | 1261 | 1296 | 54 | 5053 | 4905 | 148 | 5077 | 6.484 | 76.31
2012-10-18 | 1136 | 1238 | 1221 | 1262 | 51.18 | 4908.18 | 4755 | 153.18 | 4915 | 6.128 | 78.17
2012-10-19 | 1080 | 1187 | 1170 | 1213 | 51.65 | 4701.65 | 4575 | 126.65 | 4727 | 5.96 | 77.3 | Plant Break Downed From- 11-47 to 12-00, Because of Blown off The D.O.Fuse of `R` Phase
2012-10-20 | 1131 | 1239 | 1204 | 1257 | 52.48 | 4883.48 | 4740 | 143.48 | 4913 | 6.287 | 76.16 | Internet Failure From- 17-32 to 18-45.
2012-10-21 | 1091 | 1170 | 1137 | 1165 | 33.6 | 4596.6 | 4485 | 111.6 | 4631 | 5.883
2012-10-22 | 1085 | 1142 | 1102 | 1132 | 39.26 | 4500.26 | 4365 | 135.26 | 4519 | 5.901
2012-10-23 | 1108 | 1147 | 1108 | 1147 | 37.55 | 4547.55 | 4425 | 122.55 | 4583 | 5.871 | 76.08
2012-10-24 | 1199 | 1210 | 1170 | 1111 | 14 | 4704 | 4590 | 114 | 4739 | 5.997 | 77.02 | Grid Supply Failure From - 08-38 to 08-41.
2012-10-25 | 1238 | 1250 | 1199 | 1221 | 36.66 | 4944.66 | 4800 | 144.66 | 4972 | 6.348 | 76.33 | Grid Supply Failure From - 14-57 to 14-58.
2012-10-26 | 1266 | 1272 | 1227 | 1289 | 40.88 | 5094.88 | 4965 | 129.88 | 5129 | 6.527
2012-10-27 | 1278 | 1289 | 1238 | 1313 | 50.94 | 5168.94 | 5025 | 143.94 | 5193 | 6.512 | 77.72
2012-10-28 | 1249 | 1249 | 1204 | 1292 | 46.85 | 5040.85 | 4890 | 150.85 | 5066 | 6.256 | 78.92 | Grid supply Failure From -08-45 to 08-50,,,,,,16-01 to 16-05,,,,,&,,16-34 to 16-40.
2012-10-29 | 1261 | 1272 | 1216 | 1323 | 62.52 | 5134.52 | 4995 | 139.52 | 5152 | 6.435 | 78.03 | Grid Supply Failure From - 17-57 to 18-01.
2012-10-30 | 1227 | 1233 | 1192 | 1285 | 55.45 | 4992.45 | 4860 | 132.45 | 5021 | 6.249 | 78.31
2012-10-31 | 1057 | 1062 | 1103 | 1081 | 44.97 | 4347.97 | 4230 | 117.97 | 4385 | 5.372 | 79.55
2012-11-01 | 565 | 560 | 605 | 571 | 15.72 | 2316.72 | 2280 | 36.72 | 2382 |  |  | Grid Supply Failure From - 09-40 TO 09-45, And Plant Break Downed From - 09-50 TO 12-00, Because of Created The Fault in Aux-440,V,Supply.
2012-11-02 | 1142 | 1170 | 1244 | 1168 | 47.55 | 4771.55 | 4635 | 136.55 | 4796 | 5.912 | 79.06
2012-11-03 | 1148 | 1233 | 1243 | 1166 | 48.69 | 4838.69 | 4695 | 143.69 | 4864 | 5.44 |  | Grid Supply Failure From - 17-30 to 17-40.
2012-11-04 | 1080 | 1198 | 1170 | 1083 | 22.15 | 4553.15 | 4425 | 128.15 | 4590 | 5.555
2012-11-05 | 1074 | 1165 | 1142 | 1042 | 38.39 | 4461.39 | 4350 | 111.39 | 4498 | 5.568 | 78.73
2012-11-06 | 1108 | 1159 | 1126 | 1036 | 35.7 | 4464.7 | 4350 | 114.7 | 4502 | 5.399 | 81.27
2012-11-07 | 1108 | 1153 | 1136 | 1070 | 33.44 | 4500.44 | 4380 | 120.44 | 4540 | 5.419 | 81.65
2012-11-08 | 1063 | 1108 | 1080 | 1045 | 35.03 | 4331.03 | 4215 | 116.03 | 4374 | 5.452 | 78.19 | Grid Supply Failure From - 08-43 to 08-48.
2012-11-09 | 1136 | 1187 | 1159 | 1170 | 30.81 | 4682.81 | 4560 | 122.81 | 4714 | 5.801 | 79.2 | Grid Supply Failure From - 09-09 to 09-18.
2012-11-10 | 1171 | 1216 | 1181 | 1225 | 34.3 | 4827.3 | 4695 | 132.3 | 4858 | 6.047 | 78.3
2012-11-11 | 1147 | 1198 | 1170 | 1214 | 30.31 | 4759.31 | 4635 | 124.31 |  |  |  | Grid Supply Failure From - 13-09 TO 13-10,,,,,Client Connect Prod.Graf has Not Updated From -6-30 to 00-00.
2012-11-12 | 1171 | 1222 | 1188 | 1260 | 35.55 | 4876.55 | 4740 | 136.55 |  |  |  | Grid Supply Failure From- 16-49 to 16-54,,,,,Client Connect Prod.Graf has Not Updated From -00-00 to 00-00.
2012-11-13 | 1108 | 1153 | 1153 | 1168 | 9.89 | 4591.89 | 4485 | 106.89 |  |  |  | Grid Supply Failur From - 10-27 to 10-32 & 11-25 to 11-30,,,,,,,,Cliend Connect Prod,Graf is Not Updated From -24-00 to 24-00.
2012-11-14 | 1028 | 1074 | 1074 | 1069 | 1.461 | 4246.461 | 4140 | 106.461 |  |  |  | Client Connect Prod.Graf Not Updated Properly.
2012-11-15 | 1029 | 1068 | 1074 | 1065 | 12.26 | 4248.26 | 4125 | 123.26 |  |  |  | Grid Supply Failure From - 17-38 to 17-41. Client Connect Prod.Graf Not Updated Properly.
2012-11-16 | 1120 | 1165 | 1170 | 1168 | 18.84 | 4641.84 | 4515 | 126.84 | 4471 |  |  | Grid Supply Failure From -12-41 to 12-46.
2012-11-17 | 1091 | 1142 | 1159 | 1123 | 24.01 | 4539.01 | 4410 | 129.01 | 4569 | 5.78 | 77.04 | Grid Supply Failure From - 09-08 to 09-30.
2012-11-18 | 1148 | 1204 | 1255 | 1205 | 18.37 | 4830.37 | 4710 | 120.37
2012-11-19 | 1079 | 1165 | 1182 | 1128 | 33.75 | 4587.75 | 4470 | 117.75 |  |  |  | Grid Supply Failure From - 12-58 to 13-03,,,,18-10 to 20-30 & 20-35 to 00-00.
2012-11-20 | 797 | 882 | 865 | 996 | 12.8 | 3552.8 | 3390 | 162.8 |  |  |  | Grid Supply Failure From - 16-40 to 16-45
2012-11-21 | 1080 | 1170 | 1148 | 1077 | 20.98 | 4495.98 | 4380 | 115.98
2012-11-22 | 1097 | 1137 | 1130 | 1058 | 19.45 | 4441.45 | 4335 | 106.45
2012-11-23 | 1108 | 1136 | 1137 | 1081 | 15.81 | 4477.81 | 4365 | 112.81
2012-11-24 | 1148 | 1170 | 1170 | 1150 | 10.19 | 4648.19 | 4515 | 133.19
2012-11-25 | 1176 | 1221 | 1198 | 1183 | 7.1 | 4785.1 | 4665 | 120.1 |  |  |  | Grid Supply Failure From - 11-05 to 11-10.
2012-11-26 | 1164 | 1216 | 1188 | 1194 | 17.37 | 4779.37 | 4635 | 144.37 |  |  |  | Grid Supply Failure From - 10-05 to 11-11.
2012-11-27 | 1142 | 1193 | 1164 | 1193 | 17.72 | 4709.72 | 4590 | 119.72 | 4755 | 6.067 | 76.38 | Grid Supply Failure From - 11-50 to 11-55.
2012-11-28 | 1148 | 1193 | 1193 | 1206 | 15.03 | 4755.03 | 4635 | 120.03 | 4799 | 5.901 | 79.26 | Grid Supply Failure From - 12-35 to 12-40 & 15-52 to 15-53.
2012-11-29 | 1176 | 1226 | 1255 | 1247 | 10.65 | 4914.65 | 4785 | 129.65 | 4965 | 5.845 | 82.79
2012-11-30 | 1153 | 1227 | 1250 | 1198 | 17.11 | 4845.11 | 4710 | 135.11 | 4882 | 5.922 | 80.34
2012-12-01 | 1108 | 1210 | 1198 | 1134 | 24.38 | 4674.38 | 4545 | 129.38 | 4712 | 5.678 | 80.88
2012-12-02 | 1057 | 1136 | 1125 | 1060 | 1.67 | 4379.67 | 4260 | 119.67 | 4431 | 5.419 | 79.69
2012-12-03 | 888 | 961 | 944 | 872 | 7.15 | 3672.15 | 3585 | 87.15 | 3732 | 4.585 | 79.33
2012-12-04 | 1001 | 1063 | 1052 | 981 | 5.25 | 4102.25 | 3990 | 112.25 | 4156 | 5.152 | 78.62
2012-12-05 | 949 | 978 | 967 | 927 | 37.63 | 3858.63 | 3750 | 108.63 | 3886 | 4.874 | 77.7 | Grid Supply Failure From - 08-51 to 10-15.
2012-12-06 | 1074 | 1114 | 1091 | 1073 | 47.91 | 4399.91 | 4275 | 124.91 | 4428 | 5.619 | 76.8 | Grid Supply Failure From - 13-31 to 13-34.
2012-12-07 | 1029 | 1063 | 1040 | 1051 | 49.37 | 4232.37 | 4110 | 122.37 | 4260 | 5.592 | 74.24 | Grid Supply Failure From - 09-28 to 09-33,,,,,,11-48 to 11-50, & 13-56 to 13-58.
2012-12-08 | 1075 | 1108 | 1091 | 1126 | 47.82 | 4447.82 | 4335 | 112.82 | 4475 | 5.61 | 77.74 | Grid Supply Failure From -09-00 to 09-17.
2012-12-09 | 1136 | 1176 | 1153 | 1200 | 40.82 | 4705.82 | 4575 | 130.82 | 4734 | 5.981 | 77.14 | Grid Supply Failure From - 09-00 to 09-17.
2012-12-10 | 1097 | 1131 | 1137 | 1171 | 49.77 | 4585.77 | 4455 | 130.77 | 4606 | 5.869 | 76.49 | Plant Break Downed From -10-32 to 10-42, Because of Blown off The D.O.Fuse of `Y` Phase …….Grid Supply Failure From -17-14 to 17-19.
2012-12-11 | 1102 | 1136 | 1175 | 1147 | 36.77 | 4596.77 | 4470 | 126.77 | 4631 | 5.799 | 77.83
2012-12-12 | 1029 | 1040 | 1114 | 1068 | 35.52 | 4286.52 | 4155 | 131.52 | 4313 | 5.471 | 76.83 | Grid Supply Failure From -13-55 to 14-20.,,,,,,Inv -2 . Shut downed From - 10-05 to 10-20.
2012-12-13 | 950 | 1035 | 1029 | 938 | 23.84 | 3975.84 | 3870 | 105.84 | 4014 | 4.993 | 78.35
2012-12-14 | 904 | 966 | 1016 | 909 | 26.25 | 3821.25 | 3660 | 161.25 | 3812 | 4.646 | 79.96
2012-12-15 | 1097 | 1142 | 1042 | 1093 | 22.8 | 4396.8 | 4335 | 61.8 | 4500 | 5.721 | 76.66
2012-12-16 | 1125 | 1171 | 1131 | 1119 | 19.08 | 4565.08 | 4440 | 125.08 | 4606 | 5.82 | 77.13
2012-12-17 | 933 | 966 | 932 | 888 | 12.84 | 3731.84 | 3645 | 86.84 | 3788 | 4.724 | 78.15
2012-12-18 | 995 | 1029 | 1001 | 967 | 27.82 | 4019.82 | 3900 | 119.82 | 4061 | 5.127 | 77.2
2006-12-19 | 1074 | 1120 | 1080 | 1078 | 23.21 | 4375.21 | 4260 | 115.21 | 4413 | 5.52 | 77.91
2012-12-20 | 1221 | 1272 | 1221 | 1277 | 23.37 | 5014.37 | 4860 | 154.37 | 5040 | 6.391 | 76.86
2012-12-21 | 1176 | 1221 | 1199 | 1130 | 36.32 | 4762.32 | 4635 | 127.32 | 4796 | 6.183 | 75.6 | Grid Supply Failure From -16-00 to 16-02.
2012-12-22 | 1148 | 1193 | 1226 | 1199 | 31.93 | 4797.93 | 4665 | 132.93 | 4837 | 6.049 | 77.93
2012-12-23 | 995 | 1035 | 1086 | 1024 | 21.55 | 4161.55 | 4035 | 126.55 | 4198 | 5.831 | 70.17 | Plant Shut downed From -12-00 to 12-47 Because of Malted the `R`Phase Arc Rod of 11-kv Isolator.
2012-12-24 | 1176 | 1244 | 1272 | 1215 | 29.68 | 4936.68 | 4800 | 136.68 | 4960 | 6.206 | 77.89
2006-12-25 | 1170 | 1283 | 1261 | 1211 | 19.49 | 4944.49 | 4800 | 144.49 | 4971 | 6.228 | 77.79
2012-12-26 | 1170 | 1231 | 1215 | 1186 | 24.6 | 4826.6 | 4695 | 131.6 | 4875 | 6.198 | 76.66
2012-12-27 | 1199 | 1217 | 1187 | 1149 | 23.6 | 4775.6 | 4650 | 125.6 | 4803 | 6.209 | 75.39
2012-12-28 | 1147 | 1182 | 1125 | 1054 | 22.4 | 4530.4 | 4395 | 135.4 | 4569 | 5.846 | 76.17
2012-12-29 | 1074 | 1125 | 1057 | 1021 | 21.46 | 4298.46 | 4185 | 113.46 | 4337 | 5.334 | 79.24
2012-12-30 | 1029 | 1068 | 1007 | 973 | 22.09 | 4099.09 | 3990 | 109.09 | 4140 | 5.099 | 79.13
2013-12-31 | 1035 | 1080 | 1012 | 984 | 12.48 | 4123.48 | 4020 | 103.48 | 4170 | 5.165 | 78.69

## 2013
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2013
Project Number |  | IN-10-0061
Capacity |  | 1026 | KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 1104500525 | 7802195 | 2100570073/ 2100567820/ 2100567898
2013-01-01 | 955 | 1001 | 950 | 922 | 8.34 | 3836.34 | 3735 | 101.34 | 3893 | 4.867 | 77.96
2013-01-02 | 1108 | 1159 | 1096 | 1113 | 14.52 | 4490.52 | 4380 | 110.52 | 4540 | 5.69 | 77.76
2013-01-03 | 1058 | 1102 | 1091 | 1045 | 10.98 | 4306.98 | 4200 | 106.98 | 4356 | 5.351 | 79.34 | Plant Shut downed From 17-30 to 17-55 for Rectification of Oil Leakage Problem in Main X-mer (D-1168)
2013-01-04 | 1091 | 1154 | 1188 | 1092 | 10.99 | 4535.99 | 4395 | 140.99 | 4585 | 5.613 | 79.61
2013-01-05 | 1125 | 1232 | 1226 | 1132 | 16.34 | 4731.34 | 4590 | 141.34 | 4773 | 5.771 | 80.61
2013-01-06 | 746 | 814 | 809 | 740 | 13.05 | 3122.05 | 3030 | 92.05 | 3167 | 3.921 | 78.72 | Grid Supply Failure From -09-19 to 11-45.
2013-01-07 | 984 | 1091 | 1080 | 988 | 25.52 | 4168.52 | 4035 | 133.52 | 4194 | 5.098 | 80.18 | Gris Supply Failure From - 11-27 to 11-30 & 11-31 to 12-29.
2013-01-08 | 1243 | 1368 | 1351 | 1293 | 17.52 | 5272.52 | 5130 | 142.52 | 5308 | 6.413 | 80.67
2013-01-09 | 1148 | 1255 | 1243 | 1196 | 31.09 | 4873.09 | 4740 | 133.09 | 4882 | 5.976 | 76.62%
2013-01-10 | 1136 | 1250 | 1233 | 1200 | 22.28 | 4841.28 | 4710 | 131.28 | 4846 | 5.952 | 79.35% | Grid Supply Failure From - 16-15 to 16-20.
2013-01-11 | 1120 | 1215 | 1198 | 1180 | 13.09 | 4726.09 | 4590 | 136.09 | 4763 | 5.887 | 78.85%
2013-01-12 | 1142 | 1187 | 1171 | 1149 | 15 | 4664 | 4530 | 134 | 4700 | 5.966 | 76.78%
2013-01-13 | 1136 | 1159 | 1142 | 1120 | 14.53 | 4571.53 | 4455 | 116.53 | 4612 | 5.832 | 77.07%
2013-01-14 | 1074 | 1035 | 927 | 999 | 19.83 | 4054.83 | 3945 | 109.83 | 4111 | 5.491 | 72.97 | Every Inverters Intermittent went in Fault Moded during the Period of 13-00 to 16-05 Because of Kite Festivel High Grid Voltages problem Happened Severly for few second only
2013-01-15 | 1086 | 1108 | 1091 | 1074 | 14.05 | 4373.05 | 4260 | 113.05 | 4418 | 5.266 | 81.77
2013-01-16 | 995 | 1012 | 1001 | 989 | 17.67 | 4014.67 | 3900 | 114.67 | 4059 | 4.829 | 81.92
2013-01-17 | 1080 | 1097 | 1079 | 1077 | 9.09 | 4342.09 | 4245 | 97.09 | 4392 | 5.501 | 77.81 | Grid Supply Failure From -15-30 to 15-35.
2013-01-18 | 1243 | 1255 | 1233 | 1187 | 11.48 | 4929.48 | 4785 | 144.48 | 4966 | 5.84 | 82.87
2013-01-19 | 1301 | 1300 | 1283 | 1259 | 16.67 | 5159.67 | 5025 | 134.67 | 5188 | 6.417 | 78.79
2013-01-20 | 1136 | 1136 | 1114 | 1097 | 13.45 | 4496.45 | 4365 | 131.45 | 4527 | 5.608 | 78.67 | Grid Supply Failure From - 11-37 to 12-30 & 18-00 to 18-55.
2013-01-21 | 1317 | 1329 | 1300 | 1307 | 9.4 | 5262.4 | 5100 | 162.4 | 5295 | 6.514 | 79.22
2013-01-22 | 1267 | 1272 | 1255 | 1274 | 8.44 | 5076.44 | 4935 | 141.44 | 5110 | 6.165 | 80.78 | Grid Supply Failure From - 09-14 09-22 & 14-10 to 14-27.
2013-01-23 | 1328 | 1334 | 1312 | 1344 | 7.12 | 5325.12 | 5175 | 150.12 | 5365 | 6.653 | 78.59
2013-01-24 | 1221 | 1233 | 1210 | 1216 | 9.52 | 4889.52 | 4755 | 134.52 | 4930 | 6.157 | 78.04 | Grid Supply From - 12-33 to 12-36 & 16-58 to 17-03.
2013-01-25 | 1261 | 1266 | 1272 | 1261 | 15.82 | 5075.82 | 4920 | 155.82 | 5121 | 6.256 | 79.78
2013-01-26 | 1238 | 1249 | 1306 | 1234 | 33.97 | 5060.97 | 4920 | 140.97 | 5111 | 6.213 | 80.1784
2013-01-27 | 1266 | 1278 | 1356 | 1293 | 35.71 | 5228.71 | 5085 | 143.71 | 5284 | 6.485 | 79.4155
2013-01-28 | 1188 | 1227 | 1284 | 1194 | 4.57 | 4897.57 | 4755 | 142.57 | 4941 | 5.736 | 83.9573 | Grid Supply From - 09-59 to 09-03 & 17-09 to 17-14.
2013-01-29 | 1164 | 1255 | 1255 | 1172 |  | 4846 | 4710 | 136 | 4891 | 5.516 | 86.4223 | Grid Supply From - 14-31 to 15-04.
2013-01-30 | 933 | 1012 | 989 | 910 | 12.55 | 3856.55 | 3750 | 106.55 | 3898 | 4.554 | 83.426
2013-01-31 | 1086 | 1131 | 1193 | 1020 | 26.93 | 4456.93 | 4245 | 211.93 | 4376 | 4.951 | 86.1464 | Grid Supply Failure From -11-41 to 11-45. & Internet Failure From 17-00 TO 00-00
2013-02-01 | 1192 | 1209 | 1187 | 1103 | 28.05 | 4719.05 | 4590 | 129.05 | 4778 | 5.801 | 80.2779 | Grid Supply Failure From - 15-19 to 15-24 & Internet Failure From - 00-00 to 17-00.
2013-02-02 | 1057 | 1080 | 1051 | 994 | 27.11 | 4209.11 | 4095 | 114.11 | 4259 | 5.257 | 78.96 | Grid Supply Failure From - 09-02 to 09-06.
2013-02-03 | 1063 | 1080 | 1052 | 1003 | 25.3 | 4223.3 | 4110 | 113.3 | 4265 | 5.284 | 78.66
2013-02-04 | 1086 | 1108 | 1080 | 1045 | 24.39 | 4343.39 | 4215 | 128.39 | 4372 | 5.377 | 79.24
2013-02-05 | 1311 | 1340 | 1306 | 1334 | 14.8 | 5305.8 | 5175 | 130.8 | 5340 | 6.414 | 81.14
2013-02-06 | 1346 | 1374 | 1379 | 1339 | 17.54 | 5455.54 | 5295 | 160.54 | 5489 | 6.621 | 80.8
2013-02-07 | 1391 | 1404 | 1470 | 1277 | 24.61 | 5566.61 | 5475 | 91.61 | 5607 | 6.727 | 81.23
2013-02-08 | 1396 | 1476 | 1487 | 1394 | 17.71 | 5770.71 | 5610 | 160.71 | 5792 | 6.883 | 82.01
2013-02-09 | 1402 | 1487 | 1458 | 1376 | 16.27 | 5739.27 | 5585 | 154.27 | 5768 | 6.855 | 82.01 | Grid Supply Failure From - 10-39 to 10-42. There was An Error found in The UGVCL. Aggregate Metere Then I Informed to Mr.Booch (Ex.En. UGVCL )
2013-02-10 | 1295 | 1356 | 1340 | 1233 | 12.65 | 5236.65 | 5085 | 151.65 | 5293 |  |  | Grid Supply Failure From - 16-14 to 16-18 & 16-35 to 16-45
2013-02-11 | 1227 | 1267 | 1244 | 1161 | 24.46 | 4923.46 | 4800 | 123.46 | 4941 | 5.974 | 80.61
2013-02-12 | 1249 | 1278 | 1255 | 1198 | 23.54 | 5003.54 | 4860 | 143.54 | 5039 | 5.634 |  | Grid Supply Failure From 14-04 to 14-09.
2013-02-13 | 1272 | 1300 | 1283 | 1257 | 25.24 | 5137.24 | 4995 | 142.24 | 5171 | 6.405 | 78.68
2013-02-14 | 1108 | 1125 | 1108 | 1098 | 24.88 | 4463.88 | 4350 | 113.88 | 4498 | 5.556 | 78.9
2013-02-15 | 560 | 576 | 583 | 562 | 7.61 | 2288.61 | 2220 | 68.61 | 2326 | 2.722 | 83.28 | Grid Supply Failure From -07-30 to 07-35.
2013-02-16 | 1464 | 1521 | 1515 | 1467 | 8.9 | 5975.9 | 5805 | 170.9 | 6005 | 6.947 | 84.24
2013-02-17 | 1385 | 1436 | 1424 | 1358 | 11.49 | 5614.49 | 5475 | 139.49 | 5637 | 6.831 | 80.42 | There was An Error found in The UGVCL. Aggregate Metere Then I Informed to Mr.Bhavsar (JE. UGVCL )
2013-02-18 | 1368 | 1408 | 1403 | 1374 | 10.99 | 5563.99 | 5410 | 153.99 | 5596 | 6.855 | 79.56 | Grid Supply Failure From - 10-49 to 10-53.
2013-02-19 | 1153 | 1199 | 1192 | 1156 | 12.57 | 4712.57 | 4590 | 122.57 | 4746 | 5.811 | 79.6 | Grid Supply Failure From 10-47 to 11-37 & 14-12 to 14-17.
2013-02-20 | 1351 | 1401 | 1391 | 1363 | 21.66 | 5527.66 | 5430 | 97.66 | 5563 | 6.532 | 83 | Grid Supply Failure From - 07-10 to 07-20 & 10-29 to 10-33
2013-02-21 | 1318 | 1352 | 1346 | 1315 | 26.68 | 5357.68 | 5205 | 152.68 | 5392 | 6.643 | 79.11
2013-02-22 | 1232 | 1277 | 1277 | 1256 | 30.43 | 5072.43 | 5040 | 32.43 | 5104 | 6.268 |  | Grid Supply Failure From - 10-50 to 10-55 & 13-01 to 13-06
2013-02-23 | 1351 | 1402 | 1431 | 1245 | 34.21 | 5463.21 | 5295 | 168.21 | 5483 |  |  | Internet Failure From - 11-35 to 11-55.
2013-02-24 | 1459 | 1504 | 1543 | 1400 | 30.67 | 5936.67 | 5805 | 131.67 | 5952 | 7.238 | 80.14
2013-02-25 | 1379 | 1442 | 1464 | 1395 | 35.19 | 5715.19 | 5575 | 140 | 5739 | 6.951 | 80.47
2013-02-26 | 1222 | 1300 | 1289 | 1213 | 23.52 | 5047.52 | 4900 | 147.52 | 5078 | 6.262 | 79.03 | Grid Supply Failure From - 09-55 to 10-10,,11-32 to 11-35,, & 17-13 to 17-20.
2013-02-27 | 1452 | 1538 | 1515 | 1460 | 25.38 | 5990.38 | 5850 | 140.38 | 6022 | 7.249 | 80.96 | Grid Supply Failure From - 09-39 to 09-44.
2013-02-28 | 1516 | 1560 | 1532 | 1463 | 26.2 | 6097.2 | 5940 | 157.2 | 6119 | 7.541 | 79.08
2013-03-01 | 1487 | 1521 | 1499 | 1452 | 0.91 | 5959.91 | 5810 | 149.91 | 5981 | 7.519 | 77.5294 | Grid Supply Failure From - 06-45 to 07-55.
2013-03-02 | 1531 | 1566 | 1537 | 1279 | 21.85 | 5934.85 | 5795 | 149.85 | 5979 | 7.727 | 75.4172 | Grid Supply Failure From - 07-35 to 07-45.
2006-03-03 | 1487 | 1515 | 1493 | 1468 | 8.72 | 5971.72 | 5825 | 146.72 | 6019 | 7.568 | 77.51 | Grid Supply Failure From- 08-50 to 08-55.
2013-03-04 | 1363 | 1396 | 1368 | 1352 | 11.91 | 5490.91 | 5345 | 145.91 | 5526 | 7.141 | 75.42 | Grid Supply Failure From - 10-16 to 10-21.
2013-03-05 | 1402 | 1431 | 1408 | 1412 | 27.81 | 5680.81 | 5530 | 150.81 | 5698 | 6.593 | 84.23
2013-03-06 | 1362 | 1390 | 1390 | 1385 | 40.89 | 5567.89 | 5415 | 152.89 | 5556 | 6.871 | 78.81 | Grid Supply Failure From - 13-46 to 13-52.
2013-03-07 | 1357 | 1386 | 1425 | 1293 | 36.48 | 5497.48 | 5355 | 142.48 | 5479 | 7.01 | 76.17
2013-03-08 | 1301 | 1362 | 1379 | 1319 | 41.64 | 5402.64 | 5260 | 142.64 | 5400 | 6.846 | 76.87
2013-03-09 | 1339 | 1436 | 1419 | 1348 | 36.07 | 5578.07 | 5430 | 148.7 | 5593
2013-03-10 | 1329 | 1402 | 1386 | 1320 | 8.45 | 5445.45 | 5310 | 135.45 | 5461 | 6.65 | 80.0393 | Grid Supply Failure From - 11-35 to 11-41.
2013-03-11 | 1142 | 1210 | 1198 | 1104 | 37.52 | 4691.52 | 4537 | 154.52 | 4739 | 5.767 | 80.092 | Grid Supply Failure From - 09-30 to 09-36.
2013-03-12 | 1396 | 1436 | 1419 | 1369 | 35.35 | 5655.35 | 5510 | 145.35 | 5680 | 6.51 | 85.0394
2013-03-13 | 1357 | 1374 | 1357 | 1317 | 37.33 | 5442.33 | 5310 | 132.33 | 5474 | 6.912 | 77.18 | Aggregate Meter Replaced by UGVCL Between - 09 to 10-00. Grid Supply Failure From - 09-17 to 09-21.
2013-03-14 | 1351 | 1379 | 1362 | 1316 | 33.08 | 5441.08 | 5310 | 131.08 | 5453 | 6.789 | 78.28 | Grid Supply Failure From - 09-17 to 09-21.
2013-03-15 | 1251 | 1374 | 1357 | 1349 | 28.22 | 5359.22 | 5230 | 129.22 | 5470 | 6.915 | 77.0988
2013-03-16 | 1250 | 1272 | 1278 | 1199 | 23.56 | 5022.56 | 4900 | 122.56 | 5060 | 6.377 | 77.33
2013-03-17 | 1362 | 1379 | 1413 | 1387 | 15.02 | 5556.02 | 5410 | 146.02 | 5587 | 6.906 | 78.85
2013-03-18 | 1318 | 1340 | 1391 | 1320 | 24.92 | 5393.92 | 5250 | 143.92 | 5406 | 6.378 | 82.61 | Grid Supply Failure From - 10-03 to 10-08 & 13-07 to 13-12.
2013-03-19 | 1260 | 1329 | 1345 | 1310 | 37 | 5281 | 5140 | 141 | 5316 | 6.695 | 77.39 | Grid Supply Failure From - 09-55 to 09-57.
2013-03-20 | 1380 | 1481 | 1453 | 1376 | 40.84 | 5730.84 | 5590 | 140.84 | 5744 | 6.937 | 80.7
2013-03-21 | 1413 | 1464 | 1442 | 1384 | 57.02 | 5760.02 | 5635 | 125.02 | 5783 | 6.98 | 80.7515
2013-03-22 | 984 | 1001 | 989 | 951 | 21.71 | 3946.71 | 3834.25 | 112.46 | 3969 |  | #DIV/0!
2013-03-23 | 1374 | 1407 | 1380 | 1360 | 21.89 | 5542.89 | 5375.25 | 167.64 | 5544 | 6.916 | 78.1305 | Plant Shut Downed From- 10-31 to 10-41 ,For Replaced The `R`,D.O.Fuse Link . Grid Supply Failure From - 16-50 to 16-53.
2013-03-24 | 1447 | 1482 | 1458 | 1456 | 13.11 | 5856.11 | 5676.75 | 179.36 | 5886 | 7.293 | 78.6623
2013-03-25 | 1407 | 1436 | 1408 | 1410 | 17.17 | 5678.17 | 5508.75 | 169.42 | 5711 | 6.856 | 81.18
2013-03-26 | 1142 | 1164 | 1148 | 1168 | 17.36 | 4639.36 | 4507.5 | 131.86 | 4684 | 5.805 | 78.64
2013-03-27 | 1125 | 1148 | 1125 | 1138 | 0.59 | 4536.59 | 4393.5 | 143.09 | 4573 | 5.574 | 79.96
2013-03-28 | 1380 | 1413 | 1385 | 1383 | 23.89 | 5584.89 | 5420.25 | 164.64 | 5611 | 6.943 | 78.76 | Grid Supply Failure From - 14-05 to 14-15.
2013-03-29 | 1402 | 1436 | 1458 | 1434 | 27.88 | 5757.88 | 5575.5 | 182.38 | 5789 | 7.021 | 80.36 | Grid Supply Failure From - 15-15 to 15-20.
2013-03-30 | 1362 | 1402 | 1442 | 1358 | 18.28 | 5582.28 | 5402.25 | 180.03 | 5616 | 7.263 | 75.36 | Plant Break Downed From - 13-12 to 13-25 Because of Blown of The D.O.Fuse of `R` Phase.
2013-03-31 | 1284 | 1312 | 1351 | 1291 | 15.19 | 5253.19 | 5091 | 162.19 | 5296 | 6.839 | 75.47% | Plnt Break Downed From 09-50 to 10-04 Because of Blown off The D.O.Fuse of `R` Phase
2013-04-01 | 1368 | 1413 | 1459 | 1374 | 9.65 | 5623.65 | 5446.5 | 177.15 |  |  |  | Internet Failure From -12-30 to 00-00
2013-04-02 | 1374 | 1464 | 1475 | 1409 | 13.6 | 5735.6 | 5556.75 | 178.85 | 5897 |  |  | Grid Supply Failure From - 07-57 to 08-01. Internet Failure From - 00-00 to 16-00 and after also Failure for Intermittent Period Till to 19- 00.
2013-04-03 | 1317 | 1425 | 1408 | 1360 | 12.11 | 5522.11 | 5345.25 | 176.86 | 5564 | 6.869 | 78.94
2013-04-04 | 1345 | 1442 | 1413 | 1379 | 17.82 | 5596.82 | 5421.75 | 175.07 | 5634 |  |  | Grid Supply Failure From - 14-42 to 14-46.
2013-04-05 | 1391 | 1447 | 1419 | 1362 | 18.59 | 5637.59 | 5465.25 | 172.34 | 5679 | 7.204 | 76.83 | Grid Supply Failure From - 18-11 to 18-16.
2013-04-06 | 1397 | 1413 | 1385 | 1338 | 19.64 | 5552.64 | 5373.75 | 178.89 | 5596 | 7.109 | 76.22
2013-04-07 | 1407 | 1431 | 1402 | 1397 | 10.04 | 5647.04 | 5476.5 | 170.54 | 5687 | 7.2 |  | Grid Supply Failure From - 8-10 to 8-20.
2013-04-08 | 1216 | 1232 | 1210 | 1213 | 30.22 | 4901.22 | 4743.75 | 157.47 | 4940 | 5.799 | 83.02 | Grid SUPPLY Failure From - 07-35 to 07-40,,,09-38 to 09-40 & 10-38 to 10-42.
2013-04-09 | 1198 | 1215 | 1199 | 1228 | 16.77 | 4856.77 | 4683.75 | 173.02 | 4899 | 6.029 | 79.19
2013-04-10 | 1278 | 1301 | 1289 | 1332 | 44.99 | 5244.99 | 5076.75 | 168.24 | 5272 | 6.464 | 79.49 | Grid Supply Failure From - 09-33 to 09-38.
2013-04-11 | 1306 | 1328 | 1357 | 1361 | 30.48 | 5382.48 | 5217.75 | 164.73 | 5417
2013-04-12 | 1317 | 1357 | 1385 | 1302 | 39.72 | 5400.72 | 5234.25 | 166.47 | 5441
2013-04-13 | 1340 | 1430 | 1419 | 1381 | 31.63 | 5601.63 | 5425.5 | 176.13
2013-04-14 | 1323 | 1425 | 1396 | 1392 | 9.84 | 5545.84 | 5368.5 | 177.34
2013-04-15 | 1311 | 1413 | 1374 | 1366 | 23.77 | 5487.77 | 5338.5 | 149.27
2013-04-16 | 1380 | 1453 | 1408 | 1418 | 23.07 | 5682.07 | 5496 | 186.07
2013-04-17 | 1294 | 1318 | 1283 | 1286 | 34.96 | 5215.96 | 5051.25 | 164.71 | 5241 | 6.563
2013-04-18 | 1092 | 1102 | 1068 | 1078 | 28.61 | 4368.61 | 4248 | 120.61 | 4384 | 5.309
2013-04-19 | 1266 | 1283 | 1250 | 1265 | 24.86 | 5088.86 | 4945.5 | 143.36 | 5130 | 6.512
2006-04-20 | 1286 | 1312 | 1283 | 1322 | 13.86 | 5216.86 | 5049 | 167.86
2013-04-21 | 1137 | 1165 | 1153 | 1186 | 2.83 | 4643.83 | 4496.25 | 147.58 | 5176 |  |  | Grid Supply From 11-15 to 11-56 & 16-55 to 17-00
2013-04-22 | 932 | 966 | 950 | 956 | 16.81 | 3820.81 | 3680.25 | 140.56 | 3858 | 4.774 | 78.76 | Internet Failure From -10-45 to 13-30.
2013-04-23 | 1312 | 1346 | 1340 | 1362 | 22.92 | 5382.92 | 5198.25 | 184.67 | 5418
2013-04-24 | 1261 | 1311 | 1300 | 1304 | 12.1 | 5188.1 | 5024.25 | 163.85 |  |  |  | Internet Failure From - 13-00 to 00-00.
2013-04-25 | 1368 | 1436 | 1419 | 1416 | 12.08 | 5651.08 | 5448.75 | 202.33 |  |  |  | Internet Failure From -00-00 to 10-30.
2013-04-26 | 1385 | 1470 | 1436 | 1422 | 5.6 | 5718.6 | 5517 | 201.6
2013-04-27 | 1362 | 1448 | 1408 | 1431 | 7.03 | 5656.03 | 5466.75 | 189.28 | 5702 |  |  | Grid Supply Failure From - 10-32 to 10-35,,,,Internet Disconnectivity Problem From - 08-15 to 17-15.
2013-04-28 | 1312 | 1385 | 1357 | 1368 | 2.99 | 5424.99 | 5230.5 | 194.49 | 5463 | 6.802 | 78.27 | Grid Supply Failure From - 08-35 to 08-38.
2013-04-29 | 1345 | 1419 | 1379 | 1403 | 17.34 | 5563.34 | 5377.5 | 185.84 | 5610 | 6.954 | 78.62
2013-04-30 | 1386 | 1424 | 1385 | 1406 | 30 | 5631 | 5439 | 192 | 5664 | 7.11 | 77.64
2013-05-01 | 1396 | 1414 | 1368 | 1353 | 16.63 | 5547.63 | 5363.25 | 184.38 | 5586
2013-05-02 | 1425 | 1441 | 1402 | 1453 | 27.95 | 5748.95 | 5550 | 198.95 | 5781 |  |  | Grid Supply Failure From - 17-08 to 17-12.
2013-05-03 | 1390 | 1408 | 1374 | 1467 | 13.53 | 5652.53 | 5453.25 | 199.28 | 5690 | 7.119 | 77.9
2013-05-04 | 1369 | 1391 | 1351 | 1469 | 24.2 | 5604.2 | 5407.5 | 196.7 | 5642 | 7.077 | 77.7
2013-05-05 | 1385 | 1402 | 1374 | 1485 | 11.48 | 5657.48 | 5460 | 197.48 | 4158 |  |  | Grid Supply Failure From - 17-49 to 17-54,,,,Internet Failure From - 09-30 to 00-00.
2013-05-06 | 1317 | 1345 | 1306 | 1427 |  | 5395 | 5241 | 154 | 5832 |  |  | Internet Failure From -00-00 to 09-45.
2013-05-07 | 1266 | 1284 | 1249 | 1362 |  | 5161 | 5004.75 | 156.25 | 5226 |  |  | Internet Failure From -05-00 to 11-45.
2013-05-08 | 1346 | 1373 | 1369 | 1442 | 27.01 | 5557.01 | 5357.2 | 199.76 | 5597 | 7.028 | 77.6205
2013-05-09 | 1334 | 1357 | 1396 | 1422 | 21 | 5530 | 5352.75 | 177.25 | 5562 |  |  | Grid Supply Failure From - 10-18 to 10-23,,,, Internet Failure From -06-00 to 09-15.
2013-05-10 | 1232 | 1289 | 1306 | 1303 | 17.07 | 5147.07 | 4974 | 173.07 | 5186 | 6.628 | 76.26
2013-05-11 | 1255 | 1346 | 1340 | 1333 | 8.5 | 5282.5 | 5085.75 | 196.75 | 5325 | 6.703 | 77.42
2013-05-12 | 1261 | 1356 | 1334 | 1336 | 2.98 | 5289.98 | 5095.5 | 194.48 | 5336 |  |  | Internet Failure From - 12-30 to 13-30.
2013-05-13 | 1249 | 1352 | 1317 | 1328 | 20.41 | 5266.41 | 5076 | 190.41 | 5299 | 6.766 | 76.33
2013-05-14 | 1244 | 1323 | 1289 | 1298 | 27.74 | 5181.74 | 4993.5 | 188.24 | 5227 |  |  | Internet Failure From 11-30 to 11-45.
2013-05-15 | 1306 | 1339 | 1295 | 1310 | 15.83 | 5265.83 | 5081.25 | 184.58 | 5308 |  |  | Internet Failure From - 10-30 to 11-00.
2013-05-16 | 1351 | 1352 | 1317 | 1343 | 13.52 | 5376.52 | 5189.25 | 187.27
2013-05-17 | 1306 | 1322 | 1283 | 1349 | 15.64 | 5275.64 | 5090.25 | 185.39 | 5285 | 6.86 | 75.0885
2013-05-18 | 1329 | 1340 | 1306 | 1413 | 8.59 | 5396.59 | 5198.25 | 198.34 |  |  |  | Internet Failure From 00-00 to 21-15
2013-05-19 | 1294 | 1312 | 1272 | 1389 | 6.45 | 5273.45 | 5081.25 | 192.2 | 5317
2013-05-20 | 1244 | 1266 | 1244 | 1353 | 22.93 | 5129.93 | 4932 | 197.93 |  |  |  | Grid Supply Failure From - 07-21 to 07-26,,,,, 09-59 to 10-02,,,10-05 to 10-07 & 10-38 to 10-40.
2013-05-21 | 1278 | 1295 | 1289 | 1380 | 16.82 | 5258.82 | 5071.5 | 187.32 | 5300 | 6.622 | 78 | Grid Supply Failure From - 11-25 to 11-30.
2013-05-22 | 1289 | 1300 | 1278 | 1399 | 20.92 | 5286.92 | 5130 | 156.92 | 5370 | 6.946 | 75.35 | Grid Supply Failure From - 08-11 to 08-15,,,13-00 to 13-04 & 18-36 to 18-40.
2013-05-23 | 1295 | 1317 | 1368 | 1408 | 24.38 | 5412.38 | 5223.75 | 188.63 | 5460 | 6.902 | 77.1 | Grid Supply Failure From - 18-33 to 18-37.
2013-05-24 | 1277 | 1323 | 1363 | 1390 | 20.92 | 5373.92 | 5181.75 | 192.17
2013-05-25 | 1170 | 1255 | 1243 | 1266 | 23.79 | 4957.79 | 4771.5 | 186.29 | 5080
2013-05-26 | 1052 | 1142 | 1137 | 1142 | 14.17 | 4487.17 | 4319.25 | 167.92 |  |  |  | Internet Failure From - 7-30 to 00-00.
2013-05-27 | 1097 | 1182 | 1147 | 1168 | 13.21 | 4607.21 | 4432.5 | 174.71 | 4937 |  |  | Internet Failure From 00-00 to 11-15.
2013-05-28 | 1193 | 1244 | 1205 | 1221 | 19.42 | 4882.42 | 4702.5 | 179.92 | 4924 | 5.917 | 81.1
2013-05-29 | 1334 | 1368 | 1334 | 1364 | 22.13 | 5422.13 | 5220 | 202.13 | 5456 | 6.573 | 80.9 | Grid Supply Failure From - 07-17 to 07-23,,,14-46 to 14-50 & 18-35 to 18-38.
2006-05-30 | 1311 | 1340 | 1000 | 1369 | 28.87 | 5048.87 | 4854.75 | 194.12 | 5086 | 6.587 | 75.25 | Grd Supply Failure From - 07-55 to 08-10,,,Inverter-3 Not Auto.started after Returned the GRID, Restarted From - 10-50.
2013-05-31 | 1295 | 1328 | 1312 | 1382 | 43.44 | 5360.44 | 5160 | 200.44 | 5391 | 6.5 | 80.83 | Grid Supply Failure From - 07-30 to 07-33.
2013-06-01 | 1261 | 1295 | 1278 | 1378 | 35.31 | 5247.31 | 5061.75 | 185.56 | 5287
2013-06-02 | 1193 | 1221 | 1209 | 1297 | 9.37 | 4929.37 | 4771.5 | 157.87 | 4976 | 6.121 | 79.23
2013-06-03 | 859 | 882 | 877 | 927 | 35.42 | 3580.42 | 3475.5 | 104.92 | 3619 | 4.353 | 80.03 | Grid Supply Failure From - 18-43 to 20-10.
2013-06-04 | 1017 | 1040 | 1051 | 1094 | 21.94 | 4223.94 | 4095.75 | 128.19 | 4261 | 5.235 | 79.33 | Grid Supply Failure From - 09-38 to 09-43 & 21-15 to 00-00.
2013-06-05 | 1063 | 1102 | 1108 | 1125 | 31.94 | 4429.94 | 4302 | 127.94 | 4455 |  |  | Grid Supply From - 00-00 to 05-15 & 15-14 to 15-22.
2013-06-06 | 1074 | 1109 | 1120 | 1139 | 28.35 | 4470.35 | 4306.5 | 163.85 | 4513 |  |  | Grid Supply From -16-10 to 16-25.
2013-06-07 | 979 | 1006 | 1006 | 1025 | 30.34 | 4046.34 | 3884.25 | 162.09 | 4081 |  |  | Grid Supply Failure From - 07-10 to 07-15.
2013-06-08 | 1096 | 1125 | 1136 | 1161 | 16.05 | 4534.05 | 4397.25 | 136.8 | 4589 |  |  | Grid Supply Failure From - 08-09 to 08-14.
2013-06-09 | 990 | 1023 | 1035 | 1049 | 7.27 | 4104.27 | 3977.25 | 127.02 | 4142
2013-06-10 | 650 | 667 | 678 | 678 | 8.25 | 2681.25 | 2550.75 | 130.5 | 2720 |  |  | Grid Supply Failure From -10-13 to 10-27,,11-11 to 12-01,,13-53 to 13-56,,17-22 to 17-28,,17-57 to 18-07 & 19-03 to 19-08 and Because of Heavy Cloud Inv-1 & Inv-4 Went to Sleep mode From - 11-02 to 11-09.
2013-06-11 | 752 | 780 | 792 | 784 | 4.68 | 3112.68 | 2972.25 | 140.43 | 3150
2013-06-12 | 966 | 996 | 1006 | 1020 | 12.08 | 4000.08 | 3868.5 | 131.58 | 3919
2013-06-13 | 916 | 944 | 956 | 941 | 7.98 | 3764.98 | 3630.75 | 134.23 | 2903 |  |  | Grid Supply Failure From - 09-11 to 09-14,,,09-19 to 09-22,,,09-26 to 09-28,,,09-34 to 09-36,,,09-56 to 09-58. Internet Failure From - 09-58 to 12-00.
2013-06-14 | 1069 | 1091 | 1096 | 1131 | 21.28 | 4408.28 | 4254.75 | 153.53 | 5479
2013-06-15 | 1113 | 1147 | 1142 | 1180 | 4.04 | 4586.04 | 4462.5 | 123.54 | 4605
2013-06-16 | 1097 | 1125 | 1131 | 1148 | 0.32 | 4501.32 | 4365.75 | 135.57 | 4541 |  |  | Because of Cyclone Grid Supply Failure From - 18-50 to 22-15.
2013-06-17 | 577 | 594 | 599 | 598 | 17.82 | 2385.82 | 2325.75 | 60.07
2013-06-18 | 605 | 628 | 639 | 623 | 19.36 | 2514.36 | 2445.75 | 68.61 |  |  |  | Grid Supply Failure From - 14-40 to 14-50. Internet Failure From 00-00 to 13-00.
2013-06-19 | 983 | 1000 | 995 | 1034 | 37.42 | 4049.42 | 3928.5 | 120.92 |  |  |  | Grid Supply Failure From - 18-35 to 18-40.
2013-06-20 | 1080 | 1097 | 1073 | 1108 | 41.17 | 4399.17 | 4239 | 160.17
2013-06-21 | 1148 | 1159 | 1177 | 1155 | 50.98 | 4689.98 | 4509 | 180.98
2013-06-22 | 1023 | 1034 | 1125 | 1071 | 26.57 | 4279.57 | 4113.75 | 165.82 |  |  |  | Grid Supply Failure From - 14-11 to 14-17.
2013-06-23 | 1035 | 1052 | 1153 | 1059 | 21.09 | 4320.09 | 4156.5 | 163.59 |  |  |  | Grid SUPPLY Failure From - 12-06 to 12-10.
2013-06-24 | 961 | 1001 | 1052 | 1006 | 38.75 | 4058.75 | 3894 | 164.75 |  |  |  | Grid Supply Failure From - 13-00 to 13-05,,,13-24 to 13-27 & 17-10 to 17-15.
2013-06-25 | 853 | 938 | 927 | 900 | 10.01 | 3628.01 | 3510 | 118.01 | 3674 |  |  | Grid Supply Failure From - 09-25 to 09-55,,,11-24 to 11-29 & 18-08 to 18-15.
2013-06-26 | 555 | 599 | 588 | 526 | 15.45 | 2283.45 | 2194.5 | 88.95 | 2330
2013-06-27 | 921 | 950 | 939 | 917 | 23.97 | 3750.97 | 3597 | 153.97 | 3787 |  |  | Grid Supply Failure From - 10-24 to 10-29.
2013-06-28 | 1057 | 1086 | 1085 | 1111 | 14.17 | 4353.17 | 4182 | 171.17 | 4390 |  |  | Grid Supply Failure From - 11-34 to 11-39.
2013-06-29 | 922 | 944 | 938 | 962 | 12.72 | 3778.72 | 3614.25 | 164.47 | 3824 |  |  | Grid Supply Failure From - 14-03 to 14-08,,,15-36 to 15-42,,,16-06 to 16-10 & 16-58 to 17-02
2013-06-30 | 825 | 848 | 843 | 834 | 18.4 | 3368.4 | 3225 | 143.4 | 3410
2013-07-01 | 944 | 966 | 961 | 916 | 41.44 | 3828.44 | 3669.75 | 158.69 | 3869
2013-07-02 | 854 | 882 | 870 | 898 | 28.73 | 3532.73 | 3382.5 | 150.23 | 3581
2013-07-03 | 452 | 470 | 475 | 476 | 10.81 | 1883.81 | 1799.25 | 84.56 |  |  |  | Grid Supply Failure From - 08-38 to 08-42.
2013-07-04 | 62 | 62 | 63 | 62 | 0.9 | 249.9 | 209.25 | 40.65 |  |  |  | Grid Supply Failure From - 07-16 to 08-30, Because of Heavy Cloud All Inverters Intermittent went to Sleep Mode.
2013-07-05 | 735 | 752 | 763 | 782 | 13.1 | 3045.1 | 2928 | 117.1 | 3161 |  |  | Grid Supply Failure From - 08-23 to 08-27 & 11-35 to 11-41.
2013-07-06 | 814 | 848 | 848 | 850 | 11.95 | 3371.95 | 3238.5 | 133.45 | 3416
2013-07-07 | 877 | 899 | 904 | 924 | 4.99 | 3608.99 | 3497.25 | 111.74 | 3655
2013-07-08 | 978 | 1017 | 1024 | 1042 | 8.82 | 4069.82 | 3936.75 | 133.07 | 4068 |  |  | Grid Supply Failure From - 09-17 to 09-22.
2013-07-09 | 786 | 809 | 814 | 836 | 8.45 | 3253.45 | 3129.75 | 123.7 | 3353 |  |  | Grid Supply Failure From - 10-52 to 10-57,,,14-47 to 14-54 & 16-38 to 16-46. Internet failure from - 00-00 to 10-45.
2013-07-10 | 978 | 1012 | 1017 | 1031 | 14.22 | 4052.22 | 3886.5 | 165.72 | 4095 |  |  | Grid Supply Failure From - 12-34 to 12-42, Internet Failure From - 15-15 to 17-10.
2013-07-11 | 582 | 605 | 611 | 598 | 11.71 | 2407.71 | 2343 | 64.71 | 2459 |  |  | Grid Supply Failure From - 07-47 to 07-51 & 15-30 to 15-35.
2013-07-12 | 724 | 751 | 757 | 758 | 13.33 | 3003.33 | 2902.5 | 100.83 | 3057
2013-07-13 | 452 | 464 | 475 | 459 | 6.17 | 1856.17 | 1789.5 | 66.67 | 1909 | 2.185 | 85.15 | Grid Supply Failure From - 10-48 to 10-52
2013-07-14 | 429 | 441 | 453 | 446 | 7.01 | 1776.01 | 1692 | 84.01 | 1830 | 3.189 | 55.93 | Grid Supply Failure From - 12-42 to 14-49.
2013-07-15 | 905 | 944 | 944 | 959 | 13.81 | 3765.81 | 3643.5 | 122.31 | 3810
2013-07-16 | 763 | 786 | 791 | 786 | 13.82 | 3139.82 | 3033.75 | 106.07 | 3181
2013-07-17 | 520 | 537 | 549 | 534 | 13.31 | 2153.31 | 2061.75 | 91.56 | 2200 |  |  | Grid Supply Failure From - 13-37 to 13-42 & 15-29 to 15-39.
2013-07-18 | 696 | 724 | 723 | 724 | 12.73 | 2879.73 | 2743.5 | 136.23 | 2925 |  |  | Grid Supply Failure From - 11-37 to 12-00.
2013-07-19 | 797 | 819 | 820 | 825 | 13.56 | 3274.56 | 3128.25 | 146.31 | 3322 | 4.039 | 80.16
2013-07-20 | 916 | 944 | 950 | 952 | 10.33 | 3772.33 | 3632.25 | 140.08 | 3807 |  |  | Seeds Box Shutdowned From -11-40 to 19-45 for it`s Mantainace.
2013-07-21 | 1113 | 1148 | 1159 | 1162 | 2.58 | 4584.58 | 4428.75 | 155.83 | 4631
2013-07-22 | 775 | 797 | 797 | 805 | 16.02 | 3190.02 | 3078 | 112.02 | 3238 |  |  | Grid Supply Failure From - 17-28 to 17-36.
2013-07-23 | 582 | 605 | 610 | 601 | 14.01 | 2412.01 | 2317.5 | 94.51 | 2465
2013-07-24 | 175 | 192 | 198 | 185 | 3.18 | 753.18 | 702.75 | 50.43 | 811 | 1.019 | 77.571
2013-07-25 | 331 | 351 | 351 | 342 | 6.42 | 1381.42 | 1335 | 46.42 | 1438 | 1.667 | 84.0768 | Grid Supply Failure From - 17-48 to 17-49.
2013-07-26 | 655 | 678 | 684 | 685 | 9.09 | 2711.09 | 2619 | 92.09 | 2759 | 3.3 | 81.48 | Grid Supply Failure From - 13-12 to 13-19 & 18-06 to 18-11.
2013-07-27 | 628 | 651 | 661 | 641 | 8.81 | 2589.81 | 2496 | 93.81 | 2610 |  |  | Internet Failure From - 11-15 to 15-15.
2013-07-28 | 396 | 412 | 413 | 405 | 7.43 | 1633.43 | 1569.75 | 63.68 |  |  |  | Grid Supply Failure From - 9-22 to 9-27.
2013-07-29 | 458 | 475 | 486 | 474 | 11.12 | 1904.12 | 1849.5 | 54.62
2013-07-30 | 576 | 599 | 605 | 592 | 13.06 | 2385.06 | 2305.5 | 79.56 |  |  |  | Grid Supply Failure From - 16-05 to 16-10.
2013-07-31 | 611 | 633 | 633 | 625 | 10.73 | 2512.73 | 2406.75 | 105.98 |  |  |  | Grid Supply Failure From - 8-25 to 8-30 & 9-11 to 9-16 & 19-21 to 19-25.
2013-08-01 | 316 | 328 | 339 | 322 | 6.06 | 1311.06 | 1248.75 | 62.31 |  |  |  | Grid Supply Failure From 16-31 to 16-36.
2013-08-02 | 526 | 549 | 549 | 544 | 7.06 | 2175.06 | 2068.5 | 106.56 |  |  |  | Grid Supply Failure From - 13-32 to 13-40 & 14-20 to 14-25, Because of Heavy Cloud and Rain all Inverters Intermittent went to Sleep mode.
2013-08-03 | 419 | 429 | 435 | 430 | 5.6 | 1718.6 | 1662 | 56.6 | 1631 | 2.099 | 75.73 | Because of Heavy Cloud and Rain All Inverters Intermittent Went to Sleep mode During Up to 09-17.
2013-08-04 | 650 | 673 | 679 | 686 | 9.34 | 2697.34 | 2601.75 | 95.59 | 2763 | 3.186 | 84.52
2013-08-05 | 1147 | 1187 | 1192 | 1142 | 14.69 | 4682.69 | 4605 | 77.69 | 4793 | 5.878 | 79.47
2013-08-06 | 775 | 798 | 792 | 801 | 6.64 | 3172.64 | 3066 | 106.64 | 3214 | 3.935 | 79.6 | Grid Supply Failure From - 14-17 to 14-24 & 19-00 to 19-03.
2013-08-07 | 893 | 921 | 927 | 929 | 21.49 | 3691.49 | 3582 | 109.49 | 3737 | 4.516 | 80.65 | Grid Supply Failure From - 10-42 to 10-47.
2013-08-08 | 826 | 842 | 842 | 859 | 16.16 | 3385.16 | 3259.5 | 125.66 | 3429 | 4.143 | 80.66
2013-08-09 | 661 | 679 | 684 | 686 | 3.83 | 2713.83 | 2636.25 | 77.58 | 2755 | 3.277 | 81.84 | Grid Supply Failure From - 06-20 to 06-25,,,Inv 1,2,3 Started From - 07-35 After Reset it Manually.
2013-08-10 | 339 | 356 | 362 | 349 | 7.53 | 1413.53 | 1359.75 | 53.78 | 1449 | 1.698 | 83.17 | Grid Supply Failure From - 08-25 to 08-30.
2013-08-11 | 990 | 1023 | 1023 | 1044 | 5.54 | 4085.54 | 3947.25 | 138.29 | 4125 | 5.006 | 80.31 | Grid Supply Failure From - 13-44 to 13-49.
2013-08-12 | 785 | 814 | 826 | 816 | 12.29 | 3253.29 | 3139.5 | 113.79 | 3292 | 3.97 | 80.82
2013-08-13 | 390 | 407 | 413 | 402 | 6.25 | 1618.25 | 1565.25 | 53 | 1660 | 1.935 | 83.61 | Because of Cloud Inv- 2 & 3 Started From - 7-43 and Inv -1 & 4 Started From - 8-37.
2013-08-14 | 809 | 826 | 831 | 847 | 13.74 | 3326.74 | 3242.25 | 84.49 | 3372 | 3.902 | 84.22 | Internet Failure From -08-30 to 13-00,,,,Grid Supply Failure From - 17-16 to 17-21.
2013-08-15 | 786 | 819 | 819 | 825 | 0.13 | 3249.13 | 3103.5 | 145.63 | 3289 | 3.943 | 81.29 | Internet Failure From -11-00 to 11-15,,,, Grid Supply Failure From - 09-19 to 09-23.
2013-08-16 | 509 | 532 | 526 | 523 | 7.75 | 2097.75 | 2040.75 | 57 | 2141 | 2.571 | 81.16 | Grid Supply Failure From - 16-57 to 17-03.
2013-08-17 | 797 | 820 | 814 | 830 | 21.38 | 3282.38 | 3170 | 112.38 | 3321 | 3.976 | 81.4 | Grid Supply Failure From - 12-37 to 12-42.
2013-08-18 | 769 | 802 | 792 | 792 | 11.67 | 3166.67 | 3069.75 | 96.92 | 3204 | 3.833 | 81.47
2013-08-19 | 915 | 944 | 927 | 945 | 25.63 | 3756.63 | 3603.75 | 152.88 | 3797 | 4.432 | 83.5
2013-08-20 | 1074 | 1109 | 1091 | 1119 | 1.24 | 4394.24 | 4230.75 | 163.49 | 4434 |  |  | Grid Supply Failure From - 08-39 to 08-44 & 11 - 28 to 11-33.
2013-08-21 | 741 | 768 | 758 | 754 | 19.4 | 3040.4 | 2932.5 | 107.9 | 3083 | 3.649 | 82.34 | Plnt Break Downed From 10-50 to 10-02 Because of Blown off The D.O.Fuse of 'B' Phase
2013-08-22 | 1069 | 1103 | 1074 | 1119 | 25.96 | 4390.96 | 4245 | 145.96 | 4424 | 5.466 | 78.88
2013-08-23 | 978 | 1006 | 989 | 1025 | 28.56 | 4026.56 | 3895 | 131.56
2013-08-24 | 548 | 577 | 565 | 567 | 9.4 | 2266.4 | 2202.75 | 63.65 |  |  |  | Grid Supply Failure From - 13-25 to 13-41.
2013-08-25 | 452 | 469 | 475 | 457 | 9.38 | 1862.38 | 1787.25 | 75.13
2013-08-26 | 611 | 633 | 566 | 630 | 9.25 | 2449.25 | 2348.25 | 101 |  |  |  | Grid Supply Failure From - 13-32 to 14-30 & 14 - 33 to 15-25.
2013-08-27 | 1198 | 1238 | 887 | 1258 | 14.17 | 4595.17 | 4426.5 | 168.67 |  |  |  | Inv-3 Intermittent went to Sleep mode During the Period of 11-10 to 12-00 .Because of It`s High Temp due to Cooling fan Problem. Then I Switch off it`s 1-AJB( out of 6-AJB ) From 12-00 to 16-00 For Temp solution.
2013-08-28 | 1103 | 1137 | 916 | 1156 | 9.8 | 4321.8 | 4140 | 181.8 |  |  |  | I switch off The AJB-114 of The Inv-3 From - 10-52 to 15-02 For stabilize it`s High Voltage Problem during The Period.
2013-08-29 | 1187 | 1227 | 916 | 1222 | 25.34 | 4577.34 | 4423.5 | 153.84 |  |  |  | I switch off The AJB-117 of The Inv-3 From - 10-37 to 16-00 For stabilize it`s High Voltage Problem during The Period.
2013-08-30 | 854 | 881 | 486 | 865 | 16.39 | 3102.39 | 2986 | 116.39 |  |  |  | Inv-3 Shut Downed From - 12-05 to 15-35 For Checked The Cooling Fan problem & Also it`s AJB-112 Switch Off From - 11-34 to 15-35.
2013-08-31 | 944 | 803 | 984 | 965 | 15.43 | 3711.43 | 3576.75 | 134.68 | 3643 | 4.896 | 72.52 | Inv-2 has Went to Sleep mode From -13-58 to 13-59 Due to Colling fan Problem Then I switch off It`s AJB-112 From - 13-58 to 14-12.
2013-09-01 | 1113 | 1154 | 1147 | 1133 | 5.33 | 4552.33 | 4398.75 | 153.58 | 4699 | 5.883 | 77.8
2013-09-02 | 866 | 893 | 905 | 871 | 12.88 | 3547.88 | 3431.25 | 116.63 | 3576 | 4.438 | 78.53
2013-09-03 | 1079 | 1114 | 1119 | 1107 | 16.03 | 4435.03 | 4284 | 151.03 | 4479 | 5.643 | 77.36
2013-09-04 | 1023 | 1062 | 1063 | 1036 | 24.45 | 4208.45 | 4038.75 | 169.7 | 3064 |  |  | Grid Failure From - 12-15 to 12-20 with High Voltages Than D.O.Fuse of `B` Phase also Blown off , Plant Started From 12-28.
2013-09-05 | 1001 | 1029 | 1024 | 1027 | 20.88 | 4101.88 | 3930.75 | 171.13 | 4240 | 4240
2013-09-06 | 1018 | 1046 | 1051 | 1047 | 18.86 | 4180.86 | 4015.5 | 165.36 | 4229 | 5.529 | 74.54
2013-09-07 | 1057 | 1091 | 1091 | 1108 | 14.69 | 4361.69 | 4227.75 | 133.94 | 4370 | 5.813 | 73.27 | Grid Failure From - 07-38 to 07-45. & Plnt Break Downed From 11-42 to 12-00. Because of Blown off The D.O.Fuse of 'Y' Phase
2013-09-08 | 1198 | 1250 | 1250 | 1238 | 15.8 | 4951.8 | 4765.5 | 186.3
2013-09-09 | 1329 | 836 | 1345 | 1375 | 14.12 | 4899.12 | 4749.75 | 149.37 | 4942 | 6.983 | 68.97 | Inv-2 Shut Downed From - 18-22 to 19-00 For Checked The Cooling Fan problem & Grid Failure From - 18-22 to 18-29.
2013-09-10 | 1323 | 1380 | 1385 | 1387 | 33.02 | 5508.02 | 5305.5 | 202.52 | 5550 | 6.968 | 77.63
2013-09-11 | 1317 | 1362 | 1374 | 1383 | 41.69 | 5477.69 | 5271 | 206.69 | 5510 | 6.918 | 77.62
2013-09-12 | 1024 | 1074 | 1074 | 1075 | 20.85 | 4267.85 | 4128.75 | 139.1 | 4316 | 5.213 | 80.6 | Internet Failure From -12:45
2013-09-13 | 1113 | 1165 | 1170 | 1174 | 17.3 | 4639.3 | 4483.5 | 155.8
2013-09-14 | 1063 | 1114 | 1114 | 1117 | 16.03 | 4424.03 | 4278.75 | 145.28 |  |  |  | Plant Break Downed From 09-48 to 09-58 Because of Blown of The D.O.Fuse of `Y` Phase,,,,Grid Failure From - 15-35 to 15-42,,,Internet Failure From - 15-30 to 00-00
2013-09-15 | 1232 | 1289 | 1300 | 1286 | 11.48 | 5118.48 | 4929.75 | 188.73 |  |  |  | Internet Failure From - 00-00 to 00-00.
2013-09-16 | 1227 | 1272 | 1289 | 1273 | 17.64 | 5078.64 | 4876.5 | 202.14 |  |  |  | Internet Failure From - 00-00 to 00-00.
2013-09-17 | 1284 | 1306 | 1340 | 1335 | 9.88 | 5274.88 | 5097.75 | 177.13 |  |  |  | Internet Failure From - 00-00 to 18-30.
2013-09-18 | 1277 | 1345 | 1351 | 1334 | 10.79 | 5317.79 | 5113.5 | 204.29
2013-09-19 | 1306 | 1396 | 1380 | 1374 | 20.16 | 5476.16 | 5241.75 | 234.41 | 5516 | 6.963 | 77.21 | Internet Failure From - 17-30 to 18-15.
2013-09-20 | 1334 | 1425 | 1391 | 1347 | 24.29 | 5521.29 | 5324.25 | 197.04 | 5560 | 7.054 | 76.82
2013-09-21 | 1018 | 1069 | 1045 | 1042 | 7.35 | 4181.35 | 4021.5 | 159.85 | 4204 | 5.331 | 76.86
2013-09-22 | 639 | 672 | 673 | 676 | 5.15 | 2665.15 | 2589.75 | 75.4 | 2735 |  |  | Internet Failure From - 13-00 to 16-30.
2013-09-23 | 379 | 396 | 401 | 386 | 6.11 | 1568.11 | 1501.5 | 66.61 | 1633 | 1.864 | 85.38 | All Inverters Went to Sleep Mode Early From - 15-45. Because of Heavy Cloud and Rain.
2013-09-24 | 469 | 498 | 504 | 494 | 4.3 | 1969.3 | 1885.5 | 83.8 | 2024 | 2.316 | 85.17 | Grid Failure From - 12-43 to 12-51,,,Internet Failure From - 11-45 to 14-00.
2013-09-25 | 203 | 220 | 220 | 209 | 2.72 | 854.72 | 818.25 | 36.47 | 915 | 1.105 | 80.7 | Grid Failure From - 07-50 to 10-51,
26-Sep. | 323 | 339 | 351 | 326 | 7.5 | 1346.5 | 1287 | 59.5 | 1401 | 1.74 | 78.47 | Grid Failure From - 11-55 to 12-00 & 12-31 to 12-36.
2013-09-27 | 751 | 780 | 780 | 782 | 16.16 | 3109.16 | 2976 | 133.16 |  |  |  | Internet Failure From - 13-00 to 00-00
2013-09-28 | 470 | 498 | 503 | 491 | 8.51 | 1970.51 | 1906.5 | 64.01 |  |  |  | Internet Failure From - 00-00 to 00-00. Grid Failure From - 11-48 to 11-53 Because of Shorte The Jumper of `Y`Phase oF The Grid. Then our D.O.Fuse of `Y`Phase Also Blown off and Plant started From 12-02. And 2nd Time Grid Failure From - 12-36 to 13-45 For Replaced The Jumper.
2013-09-29 | 887 | 927 | 927 | 938 | 5.47 | 3684.47 | 3585 | 99.47 |  |  |  | Internet Failure From - 00-00 to 00-00.
2013-09-30 | 950 | 995 | 995 | 981 | 21.88 | 3942.88 | 3831 | 111.88 |  |  |  | Internet Failure From - 00-00 to 00-00.
2013-10-01 | 792 | 826 | 831 | 816 | 16.99 | 3281.99 | 3182.25 | 99.74 |  |  |  | Internet Failure From - 00-00 to 19-45.
2013-10-02 | 1068 | 1119 | 1120 | 1116 | 11.96 | 4434.96 | 4300.5 | 134.46 | 4487 | 5.722 | 76.42
2013-10-03 | 1176 | 1215 | 1215 | 1259 | 27.84 | 4892.84 | 4714 | 178.84 | 4944 | 6.324 | 76.19
2013-10-04 | 1125 | 1171 | 1182 | 1174 | 14.95 | 4666.95 | 4490.25 | 176.7 | 4707 | 6.358 | 72.15 | Plant Break Downed From - 10-27 to 10-47 Because of Blown off The D.O.Fuse of `Y` Phase
2013-10-05 | 797 | 836 | 831 | 829 | 14.83 | 3307.83 | 3185.25 | 122.58 | 3336 | 4.411 | 73.71 | Because of Rain and Cyclone Grid Failure From - 16-00 to 18-00 due to Single Pasing Problem in Distribution Line.
2013-10-06 | 656 | 690 | 695 | 659 | 5.7 | 2705.7 | 2625.75 | 79.95 | 2730 | 3.377 | 78.79
2013-10-07 | 978 | 1023 | 1023 | 1012 | 18.35 | 4054.35 | 3924.75 | 129.6 | 4101 | 5.239 | 76.29 | Grid Failure From - 09-20 to 09-48.
2013-10-08 | 360 | 289 | 283 | 257 | 4.79 | 1193.79 | 1030.5 | 163.29 | 1200 |  |  | Because of Cloud and Rain Every Inverters Intermittent Went to Sleep mode Durin The Period of 11-00 to 14-45.
2013-10-09 | 494 | 622 | 622 | 586 | 11.14 | 2335.14 | 2355 | -19.86 | 2498 | 2.985 | 81.59 | Grid Failure From -13-03 to 13-08.
2013-10-10 | 1096 | 1147 | 1153 | 1104 | 17.16 | 4517.16 | 4388.25 | 128.91 | 4579 | 5.885 | 75.83 | Grid Failure From - 15-14 to 15-19.
2013-10-11 | 1091 | 1148 | 1142 | 1146 | 6.71 | 4533.71 | 4395.75 | 137.96 | 4584 | 5.843 | 76.46 | Grid Failure From - 14-00 to 14-38.
2013-10-12 | 1199 | 1255 | 1250 | 1252 | 10.93 | 4966.93 | 4791.5 | 175.43 | 5015 | 6.258 | 78.1
2013-10-13 | 1063 | 1119 | 1113 | 1081 | 0.13 | 4376.13 | 4254 | 122.13 | 4447 | 5.297 | 81.82
2013-10-14 | 1193 | 1250 | 1244 | 1237 | 13.46 | 4937.46 | 4758 | 179.46 | 4986 | 6.297 | 77.17
2013-10-15 | 1176 | 1238 | 1227 | 1225 | 22.77 | 4888.77 | 4710 | 178.77 | 4932 |  |  | Internet Intermittent Failure From - 10-30 to 15-00
2013-10-16 | 1226 | 1266 | 1266 | 1282 | 23.24 | 5063.24 | 4906.5 | 156.74 | 5122 | 6.546 | 76.26 | Grid Failure From - 07-54 to 07-59.
2013-10-17 | 1261 | 1323 | 1306 | 1316 | 13.93 | 5219.93 | 5085 | 134.93 | 5268 | 6.746 | 76.11
2013-10-18 | 927 | 972 | 961 | 952 | 15.03 | 3827.03 | 3692.25 | 134.78 | 3877 | 5.016 | 75.33 | Grid Failure From - 11-35 to 13-10 & 16-02 to 16-26.
2013-10-19 | 1182 | 1244 | 1227 | 1253 | 25.93 | 4931.93 | 4754.25 | 177.68 | 4961 | 6.269 | 77.13
2013-10-20 | 1227 | 1312 | 1289 | 1321 | 13.24 | 5162.24 | 4969.5 | 192.74 | 5196 | 6.683 | 75.77
2013-10-21 | 1238 | 1300 | 1289 | 1334 | 30.95 | 5191.95 | 5010 | 181.95 | 5231 | 6.707 | 76.01
2013-10-22 | 1210 | 1272 | 1261 | 1273 | 22.13 | 5038.13 | 4871.25 | 166.88 | 5071 | 6.708 | 73.68 | Grid Failure From - 09-26 to 09-29 & 13-38 to 13-55.
2013-10-23 | 1238 | 1289 | 1323 | 1306 | 22.96 | 5178.96 | 5001.75 | 177.21 | 5222 | 5.976 |  | Internet Failure From 15-15 to 18-00.
2013-10-24 | 1159 | 1238 | 1260 | 1208 | 35.01 | 4900.01 | 4731.75 | 168.26 | 4935 | 6.186 | 77.75 | Grid Failure From - 08-57 to 09-00 , 10-02 to 10-05 & 10-37 to 10-40.
2013-10-25 | 1147 | 1255 | 1238 | 1217 | 28.55 | 4885.55 | 4706.25 | 179.3 | 4913 | 6.188 | 77.38
2013-10-26 | 1188 | 1283 | 1255 | 1309 | 23.31 | 5058.31 | 4832 | 226.31 | 5040 | 6.245 | 78.65
2013-10-27 | 1181 | 1255 | 1221 | 1187 | 17.69 | 4861.69 | 4695 | 166.69 | 4909 | 6.026 | 79.39
2013-10-28 | 1131 | 1193 | 1165 | 1119 | 32.81 | 4640.81 | 4473 | 167.81 | 4676 | 5.802 | 78.55 | Grid Supply Failure From - 15-35 to 15-39 , 15-48 to 15-51 & 16-10 to 16-14.
2013-10-29 | 1147 | 1193 | 1165 | 1129 | 24.8 | 4658.8 | 4496.25 | 162.55 | 4700 | 5.764 | 79.47 | Grid Supply Failure From - 14-46 to 14-51.
2013-10-30 | 1154 | 1193 | 1164 | 1156 | 26.02 | 4693.02 | 4545.75 | 147.27 | 4727 | 5.389 | 85.49 | Internet Failure From 04-15 to 10-45. Grid Supply Failure From - 10-24 to 10-29.
2013-10-31 | 1176 | 1221 | 1159 | 1195 | 20.91 | 4771.91 | 4609.5 | 162.41 |  |  |  | Internet Failure From - 00-00 to 00-00 For Changed IP Address From PDPU.
2013-11-01 | 1175 | 1227 | 1165 | 1224 | 12.97 | 4803.97 | 4647 | 156.97
2013-11-02 | 1143 | 1204 | 1148 | 1214 | 7.45 | 4716.45 | 4565.25 | 151.2
2013-11-03 | 1147 | 1199 | 1153 | 1199 | 4.56 | 4702.56 | 4566 | 136.56
2013-11-04 | 1097 | 1136 | 1097 | 1128 | 9.01 | 4467.01 | 4325.25 | 141.76
2013-11-05 | 1125 | 1159 | 1113 | 1157 | 21.1 | 4575.1 | 4422.75 | 152.35
2013-11-06 | 967 | 995 | 961 | 987 | 32.14 | 3942.14 | 3824.25 | 117.89 |  |  |  | Grid Failure From - 08-04 to 08-07 & 12-32 to 12-35.
2013-11-07 | 966 | 1001 | 978 | 994 | 22.65 | 3961.65 | 3834.75 | 126.9 |  |  |  | Grid Failure From - 08-35 to 08-43 & 15-56 to 16-00.
2013-11-08 | 1029 | 1051 | 1080 | 1058 | 13.7 | 4231.7 | 4089.75 | 141.95 |  |  |  | Grid Failure From - 09-40 to 09-43.
2013-11-09 | 990 | 1035 | 1057 | 1011 | 25.88 | 4118.88 | 3986.25 | 132.63 |  |  |  | Inv-4 Shut Down From 17-15 to 17-24 For Rectified The Oil Leakage Problem of Aux.X`mer-4 (Sr.no-C1169).
2013-11-10 | 1068 | 1125 | 1148 | 1084 | 16.9 | 4441.9 | 4298.25 | 143.65
2013-11-11 | 1086 | 1164 | 1170 | 1110 | 28.54 | 4558.54 | 4410 | 148.54
2013-11-12 | 1068 | 1171 | 1148 | 1084 | 21.48 | 4492.48 | 4349.25 | 143.23
2013-11-13 | 1029 | 1096 | 1074 | 1010 | 22.34 | 4231.34 | 4095.75 | 135.59
2013-11-14 | 1001 | 1046 | 1023 | 950 | 22.01 | 4042.01 | 3919.5 | 122.51
2013-11-15 | 1063 | 1108 | 1086 | 1007 | 24.26 | 4288.26 | 4155 | 133.26
2013-11-16 | 1209 | 1261 | 1227 | 1165 | 24.75 | 4886.75 | 4726.5 | 160.25 |  |  |  | Grid Failure From - 07-05 to 07-10.
2013-11-17 | 1148 | 1193 | 1164 | 1091 | 18.92 | 4614.92 | 4470.75 | 144.17 |  |  |  | Inv-4 Late Started From - 07-30 Because of Fault of Emergency Stop
2013-11-18 | 1119 | 1170 | 1125 | 1074 | 22.71 | 4510.71 | 4368 | 142.71
2013-11-19 | 1176 | 1227 | 1176 | 1155 | 24.08 | 4758.08 | 4612.5 | 145.58
2013-11-20 | 1159 | 1182 | 1182 | 1179 | 28.09 | 4730.09 | 4572 | 158.09 |  |  |  | Grid Supply Failure From - 15-24 to 15-31.
2013-11-21 | 1176 | 1232 | 1210 | 1223 | 19.11 | 4860.11 | 4713.75 | 146.36
2013-11-22 | 1170 | 1221 | 1226 | 1197 | 23.67 | 4837.67 | 4686 | 151.67 | 4877 | 6.156 | 77.21
2013-11-23 | 1125 | 1159 | 1216 | 1160 | 29.06 | 4689.06 | 4533.75 | 155.31 | 4722 | 6.018 | 76.47 | Grid Supply Failure From - 16-00 to 16-05.
2013-11-24 | 1086 | 1131 | 1176 | 1110 | 19.87 | 4522.87 | 4371.75 | 151.12 | 4570 | 5.778 | 77.08
2013-11-25 | 1000 | 1051 | 1079 | 1026 | 26.4 | 4182.4 | 4059.75 | 122.65 | 4233
2013-11-26 | 1063 | 1148 | 1142 | 1099 | 25.13 | 4477.13 | 4332.75 | 144.38 | 4516 | 5.674 | 77.57
2013-11-27 | 978 | 1085 | 1058 | 1022 | 26.71 | 4169.71 | 4029 | 140.71 | 4209 | 5.193 | 78.99 | Grid Supply Failure From - 17-23 to 17-29.
2013-11-28 | 1108 | 1205 | 1159 | 1128 | 27 | 4627 | 4487.25 | 139.75 | 4670 | 5.811 | 78.32
2013-11-29 | 1086 | 1119 | 1113 | 1046 | 33.03 | 4397.03 | 4260 | 137.03 | 4435 | 5.741 | 75.29 | Grid Supply Failure From - 11-28 to 11-36.
2013-11-30 | 1114 | 1159 | 1125 | 1054 | 30.56 | 4482.56 | 4336.5 | 146.06 | 4514 | 5.826 | 75.51
2013-12-01 | 1040 | 1085 | 1052 | 1008 | 22.52 | 4207.52 | 4083.75 | 123.77 | 4255 | 5.61 | 73.92 | Grid Supply Failure From - 16-20 to 16-57.
2013-12-02 | 1097 | 1080 | 1085 | 1089 | 32.49 | 4383.49 | 4252.5 | 130.99 | 4424 | 5.812 | 74.18
2013-12-03 | 1170 | 1216 | 1182 | 1189 | 27.95 | 4784.95 | 4627.5 | 157.45 |  |  |  | Grid Supply Failure From -10-47 to 10-50.
2013-12-04 | 1085 | 1136 | 1092 | 1113 | 20.35 | 4446.35 | 4320 | 126.35 | 4496 | 5.792 | 75.65
2013-12-05 | 1069 | 1108 | 1079 | 1103 | 28.24 | 4387.24 | 4248 | 139.24 | 4422 | 5.678 | 75.9 | Grid Supply Failure From - 09-14 to 09-18.
2013-12-06 | 1125 | 1170 | 1170 | 1179 | 32.62 | 4676.62 | 4518 | 158.62 | 4709 | 6.059 | 75.74
2013-12-07 | 1130 | 1176 | 1204 | 1178 | 30.24 | 4718.24 | 4563.75 | 154.49 | 4757 | 6.119 | 75.77
2013-12-08 | 1097 | 1142 | 1182 | 1132 | 21.75 | 4574.75 | 4431.75 | 143 | 4618 | 5.982 | 75.24
2013-12-09 | 1097 | 1125 | 1182 | 1134 | 27.72 | 4565.72 | 4395 | 170.72 | 4578 | 6.009 | 74.25 | Inv-3 Shut down From - 16-31 to 18-00 For Replaced The Control card of The Cooling Fan.
2013-12-10 | 1091 | 905 | 870 | 1128 | 36.24 | 4030.24 | 3895.5 | 134.74 | 4094 | 6.043 | 66.03 | Grid Failure From - 11-20 to 11-28 , Inv-3 Shut down From - 09-40 to 11-17 & 16-00 to 17-26 and Inv-2 Shut down From - 11-18 to 12-25 & 16-00 to 17-26 For Replaced The Control card of The Cooling Fan.
2013-12-11 | 1074 | 1170 | 1142 | 1100 | 31.14 | 4517.14 | 4375.5 | 141.64 | 4549 | 5.867 | 75.57
2013-12-12 | 1080 | 1148 | 1120 | 1071 | 31.4 | 4450.4 | 4308 | 142.4 | 4491 | 5.717 | 76.56
2013-12-13 | 1131 | 1187 | 1130 | 1102 | 26.81 | 4576.81 | 4438.5 | 138.31 | 4622 | 6.048 | 74.48 | Grid Failure From- 17-30 to 17-41.
2013-12-14 | 1159 | 1210 | 1154 | 1127 | 24.57 | 4674.57 | 4522.5 | 152.07 | 4710 | 6.241 | 73.55
2013-12-15 | 1142 | 1164 | 1131 | 1102 | 18.64 | 4557.64 | 4424.25 | 133.39
2013-12-16 | 1170 | 1216 | 1153 | 1146 | 27.06 | 4712.06 | 4570.5 | 141.56
2013-12-17 | 1165 | 1204 | 1125 | 1157 | 20.71 | 4671.71 | 4520.25 | 151.46
2013-12-18 | 1051 | 1080 | 1023 | 1073 | 27.03 | 4254.03 | 4137.75 | 116.28
2013-12-19 | 1097 | 1136 | 1080 | 1128 | 22.38 | 4463.38 | 4329.75 | 133.63
2013-12-20 | 1159 | 1199 | 1181 | 1194 | 29.67 | 4762.67 | 4608 | 154.67
2013-12-21 | 1029 | 1063 | 1092 | 1033 | 18.36 | 4235.36 | 4105.5 | 129.86
2013-12-22 | 1012 | 1045 | 1085 | 1018 | 18.2 | 4178.2 | 4045.5 | 132.7
2013-12-23 | 1034 | 1092 | 1108 | 1053 | 26.94 | 4313.94 | 4184.25 | 129.69
2013-12-24 | 741 | 808 | 797 | 708 | 22.08 | 3076.08 | 2979 | 97.08
2013-12-25 | 836 | 916 | 876 | 811 | 19.71 | 3458.71 | 3362.25 | 96.46
2013-12-26 | 820 | 865 | 831 | 769 | 21.47 | 3306.47 | 3210.75 | 95.72
2013-12-27 | 956 | 989 | 945 | 885 | 16.58 | 3791.58 | 3666.75 | 124.83 | 3680 | 5.724 | 62.6615 | Grid Supply Failure From - 14-57 to 15-01.
2013-12-28 | 1040 | 1075 | 1023 | 969 | 15.98 | 4122.98 | 3994.5 | 128.48 | 4010 | 5.312 | 73.5765
2013-12-29 | 961 | 989 | 944 | 908 | 9.85 | 3811.85 | 3700.5 | 111.35 | 3721 | 5.02 | 72.2451 | Grid Supply Failure From - 12-58 to 13-07.
2013-12-30 | 848 | 876 | 831 | 798 | 19.14 | 3372.14 | 3274.5 | 97.64 | 3290 | 4.367 | 73.4286
2014-12-31 | 1091 | 1125 | 1069 | 1079 | 13.67 | 4377.67 | 4239.75 | 137.92 | 4250 | 5.64 | 73.445

## 2014
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2014
Project Number |  | IN-10-0061
Capacity |  | 1026 | KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 1104500525 | 7802195 | 2100570073/ 2100567820/ 2100567898
2014-01-01 | 695 | 712 | 689 | 676 | 17.62 | 2789.62 | 2712 | 77.62 | 2795 | 3.53 | 77.172
2014-01-02 | 470 | 492 | 498 | 465 | 11.35 | 1936.35 | 1869.75 | 66.6 | 1950 | 2.393 | 79.4227
2014-01-03 | 893 | 927 | 944 | 896 | 21.16 | 3681.16 | 3568.5 | 112.66 | 3698 | 4.707 | 76.5729
2014-01-04 | 910 | 956 | 972 | 912 | 21.15 | 3771.15 | 3656.25 | 114.9 | 3782 | 4.681 | 78.7473 | Grid Failure From - 17-40 to 17-55.
2014-01-05 | 1119 | 1198 | 1199 | 1124 | 19.55 | 4659.55 | 4518 | 141.55 | 4675 | 5.943 | 76.6705
2014-01-06 | 1165 | 1250 | 1238 | 1164 | 25.94 | 4842.94 | 4689 | 153.94 | 4854 | 6.18 | 76.5533 | Grid Failure From - 11-31 to 11-34.
2014-01-07 | 1136 | 1260 | 1204 | 1146 | 24.09 | 4770.09 | 4625.25 | 144.84 | 4775 | 5.928 | 78.5087
2014-01-08 | 1007 | 1080 | 1035 | 952 | 30.96 | 4104.96 | 3972 | 132.96 | 4115 | 5.171 | 77.5618
2014-01-09 | 1046 | 1097 | 1045 | 979 | 24.62 | 4191.62 | 4064.25 | 127.37 | 4195 | 5.593 | 73.1038 | Grid Failure From - 14-21 to 14-51.
2014-01-10 | 1023 | 1046 | 1018 | 914 | 21.84 | 4022.84 | 3897.75 | 125.09 | 4028 | 5.291 | 74.2001
2014-01-11 | 871 | 899 | 859 | 772 | 13.58 | 3414.58 | 3312.75 | 101.83 | 3421 | 4.394 | 75.8832
2014-01-12 | 1102 | 1147 | 1097 | 1026 | 14.1 | 4386.1 | 4247.25 | 138.85 | 4390 | 5.61 | 76.2701 | Grid Failure From - 16-33 to 16-52 & 17-25 to 17-35.
2014-01-13 | 995 | 1035 | 995 | 883 | 22.08 | 3930.08 | 3806.25 | 123.83 | 3935 | 5.09 | 75.3494 | Inv-4 Shut-down From 15-45 to 17-29.
2014-01-14 | 1006 | 1046 | 1006 | 969 | 0.94 | 4027.94 | 3901.5 | 126.44 | 4032 | 5.208 | 75.4575 | Grid Supply Failure From - 17-53 to 17-58.
2014-01-15 | 1131 | 1198 | 1148 | 1108 | 3.14 | 4588.14 | 4446 | 142.14 | 4592 | 5.953 | 75.1828
2014-01-16 | 1136 | 1188 | 1137 | 1123 | 6.43 | 4590.43 | 4447.5 | 142.93 | 4594 | 5.872 | 76.2531
2014-01-17 | 933 | 966 | 955 | 911 | 16.97 | 3781.97 | 3603 | 178.97 | 3785 | 4.814 | 76.6324
2014-01-18 | 1210 | 1261 | 1283 | 1213 | 30.84 | 4997.84 | 4776 | 221.84 | 5002 | 6.303 | 77.348
2014-01-19 | 1187 | 1238 | 1267 | 1177 | 71.38 | 4940.38 | 4725 | 215.38 | 4943 | 6.053 | 79.5926
2014-01-20 | 961 | 1018 | 1029 | 943 | 50.91 | 4001.91 | 3813.75 | 188.16 | 4005 | 5.043 | 77.4045
2014-01-21 | 611 | 638 | 633 | 591 | 26.06 | 2499.06 | 2350.5 | 148.56 |  |  | #DIV/0! | Grid Failure From - 09-53 to 10-59.
2014-01-22 | 876 | 928 | 916 | 864 | 42.11 | 3626.11 | 3447.75 | 178.36 |  |  | #DIV/0! | Internet Failure From - 05-00 to 00-00.
2014-01-23 | 1114 | 1170 | 1158 | 1113 | 60.83 | 4615.83 | 4407 | 208.83 |  |  | #DIV/0! | Internet Started From-13-00 but 8 Pot Switch Failure Then My CPU is not connected With Net only Seeds Gate Way is Connected now.
2014-01-24 | 1074 | 1131 | 1109 | 1092 | 54.24 | 4460.24 | 4274.25 | 185.99 |  |  | #DIV/0! | Grid Failure From- 08-00 to 08-05 , 08-25 to 08-30 & 10-04 to 10-35 , All Inverters Started From 09-07 Because It`s Aux.MCB Tripped With Grid Failure at 08-00 Then I Manually Reset it And Stared The Plant.
2014-01-25 | 1153 | 1209 | 1192 | 1149 | 63 | 4766 | 4569.75 | 196.25 | 4770 | 6.029 | 77.1127 | Grid Failure From - 12-35 to 12-43.
2014-01-26 | 1001 | 1063 | 1041 | 995 | 52.68 | 4152.68 | 3966 | 186.68 | 4156 | 5.134 | 78.8991
2014-01-27 | 1187 | 1250 | 1232 | 1106 | 69.64 | 4844.64 | 4631.25 | 213.39 | 4850 | 6.112 | 77.3412 | Inv-4 Shut Down From 16-10 to 19-10 by M/s.Schneider for Rectify The Comm.Error Problem.
2014-01-28 | 1170 | 1232 | 1216 | 1186 | 73.8 | 4877.8 | 4671.75 | 206.05 | 4881 | 6.286 | 75.681 | Grid Failure From - 13-32 to 13-39 & 15-56 to 16-32.
2014-01-29 | 1222 | 1289 | 1266 | 1229 | 73.88 | 5079.88 | 4869 | 210.88 | 5083 | 6.555 | 75.5788 | Grid Failure From - 15-29 to 15-34.
2014-01-30 | 1255 | 1323 | 1306 | 1306 | 77.82 | 5267.82 | 5022 | 245.82 | 5271 | 6.657 | 77.1733 | Grid failure From - 14-01 to 14-04.
2014-01-31 | 1260 | 1329 | 1317 | 1292 | 82.08 | 5280.08 | 5066.25 | 213.83 | 5284 | 6.585 | 78.2095
2014-02-01 | 1210 | 1277 | 1295 | 1230 | 76.54 | 5088.54 | 4871.25 | 217.29 | 5092 | 6.324 | 78.4782
2014-02-02 | 939 | 995 | 1000 | 932 | 49.56 | 3915.56 | 3743.25 | 172.31 | 3919 | 4.814 | 79.3454
2014-02-03 | 1028 | 1091 | 1103 | 1019 | 60.27 | 4301.27 | 4124.25 | 177.02 | 4305 | 5.543 | 75.6974
2014-02-04 | 1160 | 1255 | 1232 | 1170 | 71.66 | 4888.66 | 4685.25 | 203.41 | 4892 | 6.157 | 77.4408
2014-02-05 | 1170 | 1272 | 1227 | 1189 | 71.22 | 4929.22 | 4723.5 | 205.72 | 4933 | 6.168 | 77.9506
2014-02-06 | 1204 | 1272 | 1221 | 1173 | 72.18 | 4942.18 | 4737 | 205.18 | 4948 | 6.242 | 77.2607
2014-02-07 | 1249 | 1295 | 1261 | 1236 | 74.55 | 5115.55 | 4908.75 | 206.8 | 5119 | 6.32 | 78.9443
2014-02-08 | 1363 | 1385 | 1368 | 1357 | 86.28 | 5559.28 | 5331 | 228.28 |  |  | #DIV/0!
2014-02-09 | 1374 | 1436 | 1379 | 1355 | 86.74 | 5630.74 | 5389.5 | 241.24 | 5635 | 6.878 | 79.8517
2014-02-10 | 1243 | 1306 | 1255 | 1250 | 79.06 | 5133.06 | 4926 | 207.06 | 5137 | 6.469 | 77.3972 | Grid Failure From - 13-17 to 13-31.
2014-02-11 | 1267 | 1323 | 1273 | 1276 | 79.26 | 5218.26 | 5014.5 | 203.76 |  |  | #DIV/0! | Grid Failure From - 11-40 to 11-45.
2014-02-12 | 1023 | 1068 | 1051 | 1033 | 63.17 | 4238.17 | 4055.25 | 182.92 | 4244 | 5.213 | 79.3488 | Grid Failure From - 12-28 to 13-58.
2014-02-13 | 1249 | 1306 | 1323 | 1267 | 73.71 | 5218.71 | 5001.75 | 216.96 | 5225 | 6.305 | 80.7707
2014-02-14 | 1063 | 1131 | 1136 | 1065 | 55.97 | 4450.97 | 4265.25 | 185.72 | 4455 | 4.966 | 87.4367 | Inv-5.1 Shut down from-11-10 to 12-50
2014-02-15 | 854 | 933 | 913 | 839 | 40.75 | 3579.75 | 3417 | 162.75 | 3583 | 4.329 | 80.67 | Because of Cloud Inv-4 went to Sleep mode From - 9-58 to 9-59 , 10-31 to 10-32 & 13-29 to 13-30.
2014-02-16 | 1170 | 1294 | 1253 | 1166 | 67.16 | 4950.16 | 4757.25 | 192.91 | 4955 | 6.083 | 79.3923 | Grid Failure From - 10-54 to 10-59.
2014-02-17 | 1312 | 1420 | 1368 | 1304 | 79.14 | 5483.14 | 5127 | 356.14 | 5488 | 6.572 | 81.3897
2014-02-18 | 1413 | 1475 | 1419 | 1304 | 87.52 | 5698.52 | 5472.75 | 225.77 | 5705 | 7.067 | 78.6816 | Inv-4 Shut-down From 16-15 to 17-20 by M/s.Schneider.
2014-02-19 | 1283 | 1323 | 1277 | 1237 | 78.78 | 5198.78 | 5004 | 194.78 | 5204 | 6.572 | 77.1778 | Plnt Shut-down From - 17-33 to 17-35 & 17-40 to 18-00 By M/s.Suk-kam UPS.
2014-02-20 | 1114 | 1159 | 1120 | 1091 | 61.67 | 4545.67 | 4367.25 | 178.42 | 4549 | 5.723 | 77.472
2014-02-21 | 701 | 723 | 695 | 695 | 26.93 | 2840.93 | 2704.5 | 136.43 | 2844 | 3.395 | 81.6474 | Fully Cloudy Day
2014-02-22 | 1255 | 1301 | 1249 | 1275 | 74.35 | 5154.35 | 4947.75 | 206.6 | 5161 | 6.458 | 77.8912
2014-02-23 | 1244 | 1300 | 1255 | 1258 | 72.81 | 5129.81 | 4929.75 | 200.06 | 5134 | 6.283 | 79.6419
2014-02-24 | 984 | 1029 | 1012 | 986 | 48.45 | 4059.45 | 3883.5 | 175.95 | 4064 | 4.807 | 82.4009
2014-02-25 | 1029 | 1091 | 1114 | 1059 | 56.26 | 4349.26 | 4174.5 | 174.76 | 4355 | 5.576 | 76.1234
2014-02-26 | 780 | 837 | 860 | 795 | 39.25 | 3311.25 | 3180 | 131.25 | 3316 | 4.441 | 72.7757 | Grid Failure From - 11-18 to 11-30 & 16-19 to 16-26.
2014-02-27 | 1006 | 1108 | 1108 | 986 | 57.14 | 4265.14 | 4067.25 | 197.89 | 4270 | 5.26 | 79.1215
2014-02-28 | 1227 | 1374 | 1345 | 1262 | 73.9 | 5281.9 | 5065.5 | 216.4 | 5285 | 6.375 | 80.8011
2014-03-01 | 1396 | 1385 | 1470 | 1388 | 85.81 | 5724.81 | 5492.25 | 232.56 | 5496 | 6.968 | 76.8761
2014-03-02 | 1374 | 1470 | 1419 | 1345 | 81.8 | 5689.8 | 5452.5 | 237.3 | 5693 | 6.779 | 81.8518
2014-03-03 | 1261 | 1323 | 1272 | 1197 | 70.96 | 5123.96 | 4912.5 | 211.46 | 5128 | 6.364 | 78.5363 | Grid Failure From - 16-27 to 16-32.
2014-03-04 | 1356 | 1413 | 1368 | 1325 | 82.82 | 5544.82 | 5319 | 225.82 | 5549 | 6.94 | 77.9306 | Grid Failure From - 15-37 to 15-41.
2014-03-05 | 1233 | 1277 | 1238 | 1254 | 73.58 | 5075.58 | 4863.75 | 211.83 | 5080 | 6.412 | 77.2188
2014-03-06 | 1266 | 1318 | 1272 | 1303 | 76.93 | 5235.93 | 5023.5 | 212.43 | 5240 | 6.523 | 78.2955
2014-03-07 | 1318 | 1368 | 1340 | 1381 | 80.87 | 5487.87 | 5264.25 | 223.62 | 5492 | 6.749 | 79.3129
2014-03-08 | 1288 | 1345 | 1346 | 1384 | 81.47 | 5444.47 | 5216.25 | 228.22 | 5450 | 6.825 | 77.8299 | Grid Failure From - 08-30 to 08-35 , Inv- 1 , 2 , 3 Restarted From - 08-58.
2014-03-09 | 1210 | 1272 | 1283 | 1261 | 71.48 | 5097.48 | 4924.5 | 172.98 | 5101 | 6.568 | 75.6963 | Grid Failure From - 02-02 to 02-15 ( But VCB Tripped Then Plant Started From -08-20) Also Grid Failure From - 11-22 to 11-27.
2014-03-10 | 1131 | 1188 | 1198 | 1155 | 65.37 | 4737.37 | 4536.75 | 200.62 | 4742 | 6.023 | 76.7364
2014-03-11 | 1165 | 1255 | 1233 | 1189 | 68.87 | 4910.87 | 4713.75 | 197.12 | 4916 | 6.28 | 76.2965 | Grid Failure From - 12-01 to 12-10.
2014-03-12 | 927 | 1006 | 967 | 932 | 50.73 | 3882.73 | 3724.5 | 158.23 | 3885 | 4.764 | 79.4826 | Grid Failure From - 12-07 to 13-36.
2014-03-13 | 1345 | 1430 | 1373 | 1355 | 78.49 | 5581.49 | 5361.75 | 219.74 | 5586 | 6.831 | 79.702
2014-03-14 | 1340 | 1391 | 1329 | 1321 | 82.56 | 5463.56 | 5248.5 | 215.06 | 5467 | 6.821 | 78.1185 | Grid Failure From - 12-35 to 12-39.
2014-03-15 | 1329 | 1385 | 1329 | 1358 | 84.12 | 5485.12 | 5259.75 | 225.37 | 5489 | 6.938 | 77.1102
2014-03-16 | 1238 | 1283 | 1232 | 1250 | 79.05 | 5082.05 | 4883.25 | 198.8 | 5088 | 6.463 | 76.7301 | Grid Failure From - 10-34 to 10-39.
2014-03-17 | 1385 | 1448 | 1391 | 1483 | 89.76 | 5796.76 | 5568 | 228.76 | 5803 | 7.083 | 79.8524
2014-03-18 | 1453 | 1509 | 1498 | 1529 | 94.13 | 6083.13 | 5844 | 239.13 | 5089 | 7.435 | 66.712
2014-03-19 | 1385 | 1447 | 1470 | 1458 | 88.85 | 5848.85 | 5626.5 | 222.35 | 5854 | 7.242 | 78.7856
2014-03-20 | 1357 | 1431 | 1458 | 1412 | 88.69 | 5746.69 | 5513.25 | 233.44 | 5752 | 7.132 | 78.6068
2014-03-21 | 1436 | 1549 | 1544 | 1524 | 94.74 | 6147.74 | 5902.5 | 245.24 | 6153 | 7.325 | 81.8713 | Grid Failure From - 16-53 to 16-57.
2014-03-22 | 1328 | 1447 | 1407 | 1399 | 82.69 | 5663.69 | 5442.75 | 220.94 | 5667 | 6.834 | 80.8222
2014-03-23 | 1284 | 1368 | 1335 | 1321 | 76.54 | 5384.54 | 5175.75 | 208.79 | 5390 | 6.528 | 80.4751
2014-03-24 | 1385 | 1459 | 1419 | 1411 | 84.66 | 5758.66 | 5532.75 | 225.91 | 5540 | 7.013 | 76.9943
2014-03-25 | 1368 | 1407 | 1390 | 1400 | 86.07 | 5651.07 | 5434.5 | 216.57 | 5659 | 7.073 | 77.981 | Grid Failure From - 17-55 to 18-02.
2014-03-26 | 1317 | 1386 | 1340 | 1385 | 81.65 | 5509.65 | 5301.75 | 207.9 | 5515 | 6.912 | 77.7668
2014-03-27 | 1170 | 1215 | 1182 | 1226 | 68.28 | 4861.28 | 4672.5 | 188.78 | 4869 | 6.067 | 78.2201 | Grid Failure From - 07-40 to 07-45.
2014-03-28 | 1306 | 1368 | 1357 | 1390 | 83.33 | 5504.33 | 5289 | 215.33 | 5512 | 6.872 | 78.1769 | Grid Failure From - 10-51 to 10-53.
2014-03-29 | 1351 | 1413 | 1430 | 1441 | 85.31 | 5720.31 | 5501.25 | 219.06 | 5726 | 6.981 | 79.9441
2014-03-30 | 1295 | 1363 | 1391 | 1390 | 77.87 | 5516.87 | 5299.5 | 217.37 | 5521 | 6.706 | 80.2429
2014-03-31 | 1317 | 1396 | 1424 | 1421 | 82.88 | 5640.88 | 5424.75 | 216.13 | 5647 | 6.905 | 79.7089
2014-04-01 | 1368 | 1504 | 1482 | 1470 | 88.45 | 5912.45 | 5678.25 | 234.2 | 5918 | 7.159 | 80.5703
2014-04-02 | 1351 | 1464 | 1424 | 1408 | 83.46 | 5730.46 | 5504.2 | 226.26 | 5736 | 6.941 | 80.5452
2014-04-03 | 1227 | 1284 | 1255 | 1236 | 65.42 | 5067.42 | 4893 | 174.42 | 5072 | 7.097 | 69.6558 | I observed Switch off The Main ACB at Morning 09-00 , Then I Started The Plant From - 09-05
2014-04-04 | 1346 | 1407 | 1363 | 1364 | 85.56 | 5565.56 | 5349 | 216.56 | 5571 | 7.145 | 75.9947 | Replaced D.C.12Amp.Fuse Link of The String.04 --tive in AJB-105 ( Inv-4)
2014-04-05 | 1227 | 1233 | 1243 | 1269 | 80.88 | 5052.88 | 4865.25 | 187.63 |  |  | #DIV/0! | Grid Failure From - 13-26 to 13-31 & 14-24 to 14-50,,,Inv-2 Shut-Down From 17-00 to 18-00 and Replaced The AFPS Card of Cooling Fan By M/s.ABB.
2014-04-06 | 1368 | 1419 | 1386 | 1358 | 88.87 | 5619.87 | 5403.75 | 216.12 | 5628 | 7.221 | 75.9643 | At.14-07 I Observed Tripped The Q11.MCB of MJB-4 ( INV-4 ) Then I Reset it and Retight it`s Termination.
2014-04-07 | 1210 | 1261 | 1232 | 1283 | 70.4 | 5056.4 | 4870.5 | 185.9 | 5060 | 6.416 | 76.8668
2014-04-08 | 1288 | 1339 | 1306 | 1389 | 80.47 | 5402.47 | 5190.75 | 211.72 | 5409 | 6.85 | 76.9625
2014-04-09 | 1318 | 1369 | 1362 | 1428 | 86.36 | 5563.36 | 5364 | 199.36 | 5569 | 7.083 | 76.6324
2014-04-10 | 1187 | 1226 | 1267 | 1258 | 76.82 | 5014.82 | 4828.5 | 186.32 | 5021 | 6.41 | 76.3457 | Grid Failure From - 09-48 to 09-53 & 13-43 to 13-58.
2014-04-11 | 1300 | 1368 | 1430 | 1418 | 86.61 | 5602.61 | 5388.75 | 213.86 | 5609 | 7.029 | 77.7758
2014-04-12 | 1261 | 1380 | 1391 | 1377 | 82.72 | 5491.72 | 5287.5 | 204.22 | 5501 | 6.786 | 79.0097
2014-04-13 | 1221 | 1357 | 1344 | 1323 | 80.79 | 5325.79 | 5111.25 | 214.54 | 5330 | 6.621 | 78.4614 | Grid Failure From - 09-29 to 09-37.
2014-04-14 | 1221 | 1368 | 1334 | 1323 | 79.02 | 5325.02 | 5122.5 | 202.52 | 5331 | 6.592 | 78.8214
2014-04-15 | 1199 | 1294 | 1255 | 1249 | 70.96 | 5067.96 | 4880.25 | 187.71 | 5072 | 6.323 | 78.1823
2014-04-16 | 1283 | 1340 | 1306 | 1307 | 76.72 | 5312.72 | 5116.5 | 196.22 | 5320 | 6.649 | 77.9844
2014-04-17 | 1249 | 1284 | 1244 | 1254 | 77.23 | 5108.23 | 4915.5 | 192.73 | 5115 | 6.435 | 77.4729 | Grid Failure From - 16-08 to 16-13.
2014-04-18 | 1284 | 1317 | 1283 | 1323 | 81.61 | 5288.61 | 5086.5 | 202.11 | 5292 | 6.596 | 78.1973
2014-04-19 | 1232 | 1272 | 1227 | 1307 | 74.31 | 5112.31 | 4920.75 | 191.56 | 5118 | 6.4 | 77.9423
2014-04-20 | 1137 | 1164 | 1131 | 1203 | 65.52 | 4700.52 | 4520.25 | 180.27 |  |  | #DIV/0! | Because Cloud Inv-4 Went to Sleep mode From - 17-25 & Inv-1,2,3 Went to Sleep mode From -17-44 and Due to Cyclone and Rain Grid Failure From 18-15 to Late Night.
2014-04-21 | 1266 | 1329 | 1328 | 1377 | 70.57 | 5370.57 | 5228.25 | 142.32 |  |  | #DIV/0! | Because of GRID Failure From Yesterday Evening to Late Night .VCB Also Switch off Due to Failure The Battery Back-Up, Then I started The Plant From - 08-48, Grid Failure From - 09-23 TO 09-28. Internet Failure From Yesterday 18-15 to 00-00
2014-04-22 | 1295 | 1362 | 1357 | 1391 | 83.49 | 5488.49 | 5284.5 | 203.99 |  |  | #DIV/0! | Grid Failure From - 09-17 to 09-36 & 16-04 to 16-06. Internet Failure From 00-00 to 00-00.
2014-04-23 | 1283 | 1357 | 1351 | 1376 | 85.04 | 5452.04 | 5253.75 | 198.29 |  |  | #DIV/0! | Grid Failure From - 09-34 to 09-37 , 10-24 to 10-29 & 11-09 to 11-12 , Internet Failure From 00-00 to 00-00 .
2014-04-24 | 1334 | 1402 | 1402 | 1431 | 79.69 | 5648.69 | 5445 | 203.69 |  |  | #DIV/0! | Internet Failure From 00-00 to 00-00.
2014-04-25 | 1261 | 1329 | 1323 | 1365 | 82.33 | 5360.33 | 5156.25 | 204.08 |  |  | #DIV/0! | Grid Failure From - 08-55 to 09-35. Internet Failure From 00-00 to 14-45.
2014-04-26 | 1243 | 1312 | 1306 | 1361 | 76.22 | 5298.22 | 5100.75 | 197.47 | 5305 | 6.726 | 76.8743
2014-04-27 | 1018 | 1068 | 1063 | 1090 | 65.39 | 4304.39 | 4134 | 170.39 | 4310 | 5.75 | 73.057 | Grid Failure From - 8:30 to 8:35 & 10:40 to 11:55.
2014-04-28 | 1233 | 1295 | 1289 | 1332 | 79.74 | 5228.74 | 5031 | 197.74 | 5235 | 6.726 | 75.8599
2014-04-29 | 1226 | 1289 | 1283 | 1345 | 79.6 | 5222.6 | 5037.75 | 184.85 |  |  | #DIV/0! | Grid Failure From -17:48 to 17:50 , Rahul Mohan Shut-down The SEEDS During The Period of 13:45 to 16-15.
2014-04-30 | 1261 | 1328 | 1312 | 1382 | 83.91 | 5366.91 | 5166 | 200.91 | 5370 | 6.866 | 76.2295
5341
2014-05-01 | 1227 | 1295 | 1323 | 1403 | 86.34 | 5334.34 | 5126.25 | 208.09 | 5440 | 6.948 | 76.3118
2014-05-02 | 1272 | 1328 | 1334 | 1414 | 84.38 | 5432.38 | 5232 | 200.38 | 5439 | 6.952 | 76.2539 | Grid Failure From - 17:44 to 17:49.
2014-05-03 | 1148 | 1204 | 1210 | 1269 | 65.56 | 4896.56 | 4702.5 | 194.06 | 4903 | 6.232 | 76.6809 | Grid Failure From - 16-27 to 19-29.
2014-05-04 | 1175 | 1227 | 1243 | 1317 | 69.07 | 5031.07 | 4852.5 | 178.57 | 5038 | 6.326 | 77.6214
2014-05-05 | 1120 | 1154 | 1216 | 1238 | 67.15 | 4795.15 | 4602 | 193.15 | 4800 | 6.079 | 76.9594
2006-05-06 | 1085 | 1147 | 1193 | 1225 | 66.05 | 4716.05 | 4542 | 174.05 | 4720 | 5.983 | 76.891
2006-05-07 | 1205 | 1301 | 1340 | 1248 | 78.39 | 5172.39 | 5063.25 | 109.14 | 5179 | 6.43 | 78.5032 | Grid Failure From - 08:16 to 08:20
2006-05-08 | 1215 | 1334 | 1345 | 1353 | 77.77 | 5324.77 | 5136.75 | 188.02 | 5330 | 6.594 | 78.7827
2014-05-09 | 1300 | 1390 | 1391 | 1391 | 85.97 | 5557.97 | 5348.25 | 209.72 | 5600 | 6.957 | 78.4546
2014-05-10 | 1187 | 1205 | 1216 | 1232 | 69.93 | 4909.93 | 4721.25 | 188.68 | 4938 | 6.338 | 75.93 | Grid Failure From - 11:27 to 11:48 & 17:49 to 17:55.
2014-05-11 | 1267 | 1306 | 1294 | 1349 | 80.29 | 5296.29 | 5084.25 | 212.04 | 5316 | 6.681 | 77.55
2014-05-12 | 1244 | 1322 | 1312 | 1372 | 82.38 | 5332.38 | 5129.25 | 203.13 | 5357 | 6.663 | 78.36 | Grid Failure from 16:10 to 16:14 & 18:47 to 18:51
2014-05-13 | 1119 | 1193 | 1170 | 1244 | 68.94 | 4794.94 | 4602 | 192.94 | 4817 | 6.13 | 76.58
2014-05-14 | 1142 | 1217 | 1215 | 1272 | 69.19 | 4915.19 | 4722.75 | 192.44 | 4940 | 6.102 | 78.9
2014-05-15 | 1227 | 1288 | 1295 | 1362 | 79.36 | 5251.36 | 5050.5 | 200.86 | 5275 | 6.469 | 79.47
2014-05-16 | 1102 | 1147 | 1159 | 1212 | 67.36 | 4687.36 | 4504.5 | 182.86 | 4715 | 5.745 | 79.99
2014-05-17 | 1216 | 1273 | 1306 | 1347 | 77.42 | 5219.42 | 5025 | 194.42 | 5249 | 6.43 | 79.56
2014-05-18 | 1158 | 1215 | 1244 | 1345 | 79.43 | 5041.43 | 4844.25 | 197.18 | 5066 | 6.587 | 74.96 | Grid Failure From -08:00 to 08:05 But Inverter - 1 , 2 & 3 Reset at 08:50.
2014-05-19 | 1058 | 1119 | 1125 | 1164 | 69.38 | 4535.38 | 4360.5 | 174.88 | 4569 | 5.729 | 77.73 | Grid Failure From - 09:05 to 09:10 & 12:05 to 12:18.
2014-05-20 | 1227 | 1329 | 1294 | 1343 | 59.57 | 5252.57 | 5073 | 179.57 | 5300 | 6.477 | 79.75
2014-05-21 | 1288 | 1396 | 1346 | 1414 | 91.07 | 5535.07 | 5328 | 207.07 | 5561 | 6.81 | 79.58
2014-05-22 | 1306 | 1368 | 1323 | 1396 | 90.68 | 5483.68 | 5281.5 | 202.18 | 5513 | 7.001 | 76.75
2014-05-23 | 1306 | 1357 | 1311 | 1390 | 90.99 | 5454.99 | 5252.25 | 202.74 | 5476 | 6.979 | 76.47
2014-05-24 | 1267 | 1317 | 1280 | 1354 | 87.16 | 5305.16 | 5108.25 | 196.91 | 5330 | 6.797 | 76.42
2014-05-25 | 1176 | 1216 | 1182 | 1279 | 75.87 | 4928.87 | 4752.9 | 175.97 | 4967 | 6.391 | 75.67
2014-05-26 | 1113 | 1153 | 1125 | 1197 | 69.83 | 4657.83 | 4482.75 | 175.08 | 4674 | 6.007 | 75.83
2014-05-27 | 577 | 605 | 593 | 617 | 34.55 | 2426.55 | 2309.25 | 117.3 | 2458 | 3.272 | 73.21 | Grid failure from 9:14 am to 13:04 pm.
2014-05-28 | 1153 | 1216 | 1187 | 1284 | 68.6 | 4908.6 | 4735.5 | 173.1 | 4938 | 6.326 | 76.08
2014-05-29 | 1193 | 1243 | 1221 | 1335 | 79.56 | 5071.56 | 4881 | 190.56 | 5092 | 6.361 | 78.0217 | Internet Failure From - 02:15 to 09:50.
2014-05-30 | 1210 | 1267 | 1267 | 1361 | 83.09 | 5188.09 | 5000.25 | 187.84 | 5215 | 6.639 | 76.56
2014-05-31 | 1193 | 1244 | 1278 | 1337 | 76.57 | 5128.57 | 4931.25 | 197.32 | 5144 | 6.554 | 76.49
2014-06-01 | 1136 | 1187 | 1232 | 1268 | 70.32 | 4893.32 | 4713.75 | 179.57 | 4927 | 6.295 | 76.28 | Grid Failure From - 09:06 to 09:09
2014-06-02 | 1120 | 1198 | 1210 | 1259 | 70.38 | 4857.38 | 4668.75 | 188.63 | 4881 | 6.18 | 76.9791 | Internet Failure From - 11:00 to 16:45 & Grid Failure From - 17:15 to 17:27.
2014-06-03 | 1147 | 1233 | 1227 | 1271 | 76.74 | 4954.74 | 4767.75 | 186.99 | 4981 | 6.361 | 76.32 | Grid Failure From - 12:03 to 12:11
2014-06-04 | 990 | 1057 | 1057 | 1102 | 69.75 | 4275.75 | 4118.25 | 157.5 | 4339 | 5.955 | 71.01
2014-06-05 | 1192 | 1238 | 1238 | 1251 | 74.72 | 4993.72 | 4813.5 | 180.22 | 5054 | 6.4 | 76.96
2014-06-06 | 1227 | 1283 | 1272 | 1278 | 82.96 | 5142.96 | 4949.95 | 193.01 | 5173 | 6.596 | 76.43
2014-06-07 | 1171 | 1210 | 1210 | 1231 | 77.45 | 4899.45 | 4703.2 | 196.25 | 4953 | 6.478 | 74.52 | Grid Failure From - 09:43 to 09:46 & D.O.Fuse of `Y` Phase also Blown of With Grid Failure ,Then Plant Started From - 10:02 After Returned The GRID.
2014-06-08 | 1221 | 1272 | 1266 | 1308 | 85.47 | 5152.47 | 4953.75 | 198.72 | 5182 | 6.601 | 76.51
2014-06-09 | 1221 | 1267 | 1272 | 1309 | 84.03 | 5153.03 | 4955.25 | 197.78 | 5197 | 6.559 | 77.22
2014-06-10 | 1142 | 1192 | 1204 | 1248 | 76.18 | 4862.18 | 4671.8 | 190.38 | 4885 | 6.215 | 76.6
2014-06-11 | 1102 | 1142 | 1159 | 1198 | 65.85 | 4666.85 | 4482.7 | 184.15 | 4693 | 5.841 | 78.3 | Grid Failure From - 17:55 to 18:00.
2014-06-12 | 1001 | 1046 | 1063 | 1067 | 57.25 | 4234.25 | 4063.5 | 170.75 | 4264 | 5.263 | 78.96 | Grid Failure From - 14:33 to 14:38
2014-06-13 | 1051 | 1091 | 1119 | 1131 | 68.73 | 4460.73 | 4275.75 | 184.98 | 4474 | 5.589 | 78.02
2014-06-14 | 1097 | 1148 | 1123 | 1160 | 69.11 | 4597.11 | 4439.25 | 157.86 | 4649 | 5.848 | 77.48
2014-06-15 | 1074 | 1125 | 1178 | 1139 | 72.03 | 4588.03 | 4370.25 | 217.78 | 4587 | 5.702 | 78.4
2014-06-16 | 848 | 893 | 888 | 900 | 41.96 | 3570.96 | 3408.75 | 162.21 | 3601 | 4.529 | 77.49 | Grid Failure From -17:42 to 17:45.
2014-06-17 | 916 | 967 | 972 | 993 | 49.8 | 3897.8 | 3725.25 | 172.55 | 3938 | 4.843 | 79.25 | Grid Failure From - 13:42 to 14:03 & 18:25 to 18:27.
2014-06-18 | 1063 | 1114 | 1120 | 1128 | 66.67 | 4491.67 | 4317 | 174.67 | 4525 | 5.611 | 78.6 | Inverter-1-Shut-Down From 18:05 & Grid Failure From - 18:19 to 18:21.
2014-06-19 | 1102 | 1153 | 1164 | 1162 | 64.11 | 4645.11 | 4482.7 | 162.41 | 4709 | 5.786 | 79.3237
2014-06-20 | 1069 | 1125 | 1125 | 1128 | 60.01 | 4507.01 | 4332.8 | 174.21 | 4527 | 5.698 | 77.43
2014-06-21 | 1023 | 1074 | 1080 | 1087 | 52.33 | 4316.33 | 4132.5 | 183.83 | 4333 | 5.522 | 76.44
2014-06-22 | 944 | 995 | 1007 | 1018 | 46.16 | 4010.16 | 3843 | 167.16 | 4034 | 5.017 | 78.36 | Grid Failure From - 17:34 to 17:42
2014-06-23 | 1007 | 1063 | 1068 | 1073 | 54.25 | 4265.25 | 4101 | 164.25 | 4293 | 5.476 | 76.4 | Grid Failure From -11:11 to 11:14
2014-06-24 | 1077 | 1136 | 1148 | 1153 | 61.33 | 4575.33 | 4395 | 180.33 | 4595 | 5.866 | 76.34
2014-06-25 | 995 | 1052 | 1074 | 1068 | 54.58 | 4243.58 | 4078.5 | 165.08 | 4284 | 5.49 | 76.05
2014-06-26 | 1040 | 1102 | 1136 | 1117 | 61.77 | 4456.77 | 4281.75 | 175.02 | 4502 | 5.709 | 76.85
2014-06-27 | 1080 | 1176 | 1187 | 1179 | 67.82 | 4689.82 | 4511.25 | 178.57 | 4743 | 6.003 | 77 | Grid Failure From - 17:40 to 17:48 & 18:13 to 18:28. & Inveter No -1 D C vollage low so not start
2014-06-28 | 1085 | 1193 | 1182 | 1172 | 66.25 | 4698.25 | 4510.5 | 187.75 | 4747 | 5.964 | 77.57
2014-06-29 | 1080 | 1165 | 1136 | 1133 | 60.29 | 4574.29 | 4393.5 | 180.79 | 4601 | 5.89 | 76.13
2014-06-30 | 1023 | 1079 | 1052 | 1058 | 53.8 | 4265.8 | 4125 | 140.8 | 4276 | 5.56 | 74.95
2014-07-01 | 1040 | 1080 | 1057 | 1060 | 60.66 | 4297.66 | 4119 | 178.66 | 4342 | 5.44 | 77.79
2014-07-02 | 1001 | 1046 | 1023 | 1037 | 58.28 | 4165.28 | 3991.5 | 173.78 | 4188 | 5.34 | 76.43 | Grid Failure From - 15:19 to 15:21
2014-07-03 | 984 | 1024 | 1001 | 1038 | 53.63 | 4100.63 | 3933.75 | 166.88 | 4135 | 5.153 | 78.21
2014-07-04 | 984 | 1028 | 1006 | 1055 | 54.59 | 4127.59 | 3952.5 | 175.09 | 4177 | 5.25 | 77.54 | Grid Failure From - 16:26 to 16:47
2014-07-05 | 1006 | 1046 | 1035 | 1092 | 60.58 | 4239.58 | 4058.25 | 181.33 | 4266 | 5.693 | 73.03 | Grid Failure From - 16:26 to 11:11 to 11:34
2014-07-06 | 1017 | 1074 | 1063 | 1110 | 62.32 | 4326.32 | 4167 | 159.32 | 4352 | 5.621 | 75.46 | Grid Failure From - 16:26 to 15:39 to 15:57
2014-07-07 | 961 | 1001 | 1017 | 1038 | 52.73 | 4069.73 | 3896.25 | 173.48 | 4092 | 5.18 | 76.99
2014-07-08 | 1069 | 1148 | 1142 | 1146 | 65.36 | 4570.36 | 4390.5 | 179.86 | 4602 | 5.58 | 80.38
2014-07-09 | 1046 | 1136 | 1102 | 1124 | 61.52 | 4469.52 | 4277.25 | 192.27 | 4489 | 6.128 | 71.39 | Grid Failure From - 9:06 to 9:16
2014-07-10 | 1057 | 1279 | 1063 | 1115 | 62.19 | 4576.19 | 4219.5 | 356.69 | 4433 | 5.783 | 74.71
2014-07-11 | 1114 | 950 | 1126 | 1176 | 70.3 | 4436.3 | 4258.5 | 177.8 | 4478 | 6.103 | 71.51 | ABB Inverter no-2 did not wake up in the morning reset it @ 10:00 o clock & Grid failure from - 13:58 to 14:00
2014-07-12 | 944 | 989 | 961 | 998 | 46.86 | 3938.86 | 3777.75 | 161.11 | 3968 | 5.016 | 77.1 | Cloudy Day
2014-07-13 | 938 | 978 | 949 | 993 | 49.36 | 3907.36 | 3745.5 | 161.86 |  | 5.139
2014-07-14 | 605 | 633 | 628 | 634 | 23.35 | 2523.35 | 2392.5 | 130.85 | 2563 | 2.958 | 84.45 | Fully Cloudy Day
2014-07-15 | 730 | 758 | 752 | 770 | 29.73 | 3039.73 | 2895 | 144.73 |  | 3.719
2014-07-16 | 441 | 458 | 463 | 476 | 15.26 | 1853.26 | 1739.25 | 114.01 | 1892 | 2.231 | 82.65
2014-07-17 | 650 | 684 | 679 | 718 | 26.64 | 2757.64 | 2631 | 126.64 | 2791 | 3.232 | 84.16 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 ++tive in AJB-100 of The Inverter-4 during The Period of 10:15 To 10:20. Battery water Fileed in 03 no`s of Compund Light ( 02 Back side Light & 01 Front side Light )
2014-07-18 | 401 | 407 | 413 | 428 | 12.57 | 1661.57 | 1549.5 | 112.07 | 1695 | 1.973 | 83.73 | Grid Failure From - 10:32 to 10:42
2014-07-19 | 729 | 752 | 751 | 794 | 28.09 | 3054.09 | 2916 | 138.09 | 3081 | 3.589 | 83.67 | Fully Cloudy Day
2014-07-20 | 990 | 1023 | 1029 | 1078 | 47.71 | 4167.71 | 4002 | 165.71 | 4189 | 5.016 | 81.39
2014-07-21 | 1017 | 1052 | 1057 | 1106 | 55.94 | 4287.94 | 4110 | 177.94 | 4301 | 5.32 | 78.79 | Grid Failure From - 14:05 to 14:43 & D.O.Fuse of `R` Phase also Blown of With Grid Failure ,Then Plant Started From - 14:43 After Returned The GRID.WO # 791503
2014-07-22 | 945 | 975 | 978 | 1020 | 44.89 | 3962.89 | 3810 | 152.89 | 3986 | 4.757 | 81.66
2014-07-23 | 344 | 356 | 357 | 363 | 10.39 | 1430.39 | 1312.5 | 117.89 | 1442 | 1.665 | 84.41 | Fully Cloudy Day
2014-07-24 | 113 | 119 | 124 | 124 | 2.41 | 482.41 | 388 | 94.41 | 509 | 685 | 72.42 | Heavy Cloud and Rain
2014-07-25 | 571 | 594 | 594 | 616 | 17.92 | 2392.92 | 2259 | 133.92 | 2412 | 2.754 | 85.36 | Cloud and Rain
2014-07-26 | 911 | 932 | 938 | 999 | 41.76 | 3821.76 | 3658.5 | 163.26 | 3866 | 4.7 | 80.17
2014-07-27 | 898 | 928 | 933 | 980 | 41.65 | 3780.65 | 3626.25 | 154.4 | 3806 | 4.513 | 82.19
2014-07-28 | 730 | 752 | 757 | 788 | 30.07 | 3057.07 | 2922.75 | 134.32 | 3077 | 3.615 | 82.96 | Cloud and Rain
2014-07-29 | 559 | 582 | 583 | 598 | 18.98 | 2340.98 | 2218.5 | 122.48 | 2367 | 2.72 | 84.81 | Cloud and Rain
2014-07-30 | 684 | 706 | 712 | 748 | 26.98 | 2876.98 | 2731.5 | 145.48 | 2907 | 3.412 | 83.04 | Cloud and Rain
2014-07-31 | 945 | 973 | 978 | 1051 | 48.81 | 3995.81 | 3836.25 | 159.56 | 4026 | 4.998 | 78.51 | Cloudy Day
2014-08-01 | 966 | 989 | 989 | 1070 | 47.28 | 4061.28 | 3899.25 | 162.03 | 4086 | 5.046 | 78.92
2014-08-02 | 662 | 690 | 690 | 718 | 26.83 | 2786.83 | 2646 | 140.83 | 2808 | 3.321 | 82.41 | Cloud and Rain
2014-08-03 | 650 | 667 | 673 | 711 | 27.14 | 2728.14 | 2584.5 | 143.64 | 2745 | 3.359 | 79.64 | Cloud and Rain
2014-08-04 | 752 | 775 | 780 | 812 | 27.61 | 3146.61 | 3000 | 146.61 | 3176 | 3.845 | 80.5 | Grid Failure From - 10:15 to 10:24 WO#980264 & Cloudy Day
2014-08-05 | 599 | 616 | 622 | 637 | 21.31 | 2495.31 | 2388.75 | 106.56 | 2530 | 2.966 | 83.13 | Cloud and Rain
2014-08-06 | 328 | 339 | 339 | 341 | 9.06 | 1356.06 | 1243.5 | 112.56 | 1375 | 1.566 | 85.57 | Cloud and Rain
2014-08-07 | 701 | 724 | 729 | 754 | 25.43 | 2933.43 | 2805 | 128.43 | 2967 | 3.463 | 83.5 | Cloudy Day
2014-08-08 | 967 | 989 | 979 | 1054 | 53.53 | 4042.53 | 3879 | 163.53 | 4067 | 5.112 | 77.54 | Grid Failure From - 17:58 to 18:25 WO#1058270 & Cloudy Day
2014-08-09 | 1091 | 1125 | 1130 | 1173 | 59.04 | 4578.04 | 4404.75 | 173.29 | 4626 | 5.698 | 79.12
2014-08-10 | 927 | 961 | 967 | 1002 | 52.42 | 3909.42 | 3748.5 | 160.92 | 3937 | 4.799 | 79.95 | Cloudy Day
2014-08-11 | 905 | 922 | 921 | 973 | 48.35 | 3769.35 | 3615 | 154.35 | 3798 | 4.647 | 79.65 | Cloudy Day
2014-08-12 | 1079 | 1119 | 1097 | 1178 | 58.65 | 4531.65 | 4353.75 | 177.9 | 4555 | 5.82 | 76.28 | Cloud and Rain
2014-08-13 | 826 | 848 | 842 | 907 | 43.38 | 3466.38 | 3318.75 | 147.63 | 3474 | 4.3 | 78.74 | Grid Failure From - 9:13 to 9:25(WO#1113328) & second time Grid Failure From - 11:12 to 11:15 & D.O.Fuse of `Y` Phase also Blown of With Grid Failure ,Then Plant Started From - 11:27 After Returned The GRID.(WO#1114096)
2014-08-14 | 752 | 774 | 758 | 803 | 32.61 | 3119.61 | 2981.25 | 138.36 | 3148 | 3.769 | 81.4 | Cloud and Rain
2014-08-15 | 881 | 911 | 905 | 951 | 38.63 | 3686.63 | 3522 | 164.63 | 3710 | 4.476 | 80.78 | Cloud and Rain
2014-08-16 | 809 | 836 | 814 | 877 | 36.72 | 3372.72 | 3216.75 | 155.97 | 3401 | 4.304 | 77.01 | Grid Failure From - 14:30 to 15:40 WO#1153598 & Rain & Cloudy
2014-08-17 | 995 | 1029 | 1017 | 1050 | 39.65 | 4130.65 | 3965.25 | 165.4 | 4161 | 5.119 | 79.22 | Cloudy Day
2014-08-18 | 1102 | 1137 | 1131 | 1192 | 47.81 | 4609.81 | 4434 | 175.81 | 4645 | 5.83 | 77.65 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07 --tive in AJB-116 of The Inverter-3 during The Period of 10:20 To 10:25.WO#(1174948) & Rain & Cloudy
2014-08-19 | 1080 | 1119 | 1114 | 1180 | 49.15 | 4542.15 | 4363.5 | 178.65 | 4562 | 5.763 | 77.15 | Cloudy Day
2014-08-20 | 1165 | 1221 | 1204 | 1245 | 54.27 | 4889.27 | 4703.25 | 186.02 | 4909 | 6.228 | 76.82 | Today I Replaced The 1 D.C.12Amp Fuse Link of The String- 07 ++tive in AJB-109 of The Inverter-2 during The Period of 10:50 To 10:55.WO#(1220529) & 2, D.C.12Amp Fuse Link of The String- 08 --tive in AJB-112 of The Inverter-2 during The Period of 16:35 To 16:40.WO#(1223722)
2014-08-21 | 1193 | 1255 | 1244 | 1310 | 53.96 | 5055.96 | 4864.5 | 191.46 | 5084 | 6.439 | 76.95
2014-08-22 | 1057 | 1114 | 1108 | 1142 | 56.82 | 4477.82 | 4307.25 | 170.57 | 4501 | 6.085 | 72.09 | Grid Failure From 12:33 to12:47 for D.O Fuse of "Y" Phase blown after replace fuse and plant start
2014-08-23 | 554 | 582 | 576 | 601 | 28.05 | 2341.05 | 2217 | 124.05 | 2367 | 2.848 | 81 | Cloudy Day
2014-08-24 | 707 | 752 | 747 | 778 | 32.1 | 3016.1 | 2858.25 | 157.85 | 3069 | 4.731 | 63.22 | D.O Fuse of "Y" phase blown at 10:30 Am, Fuse was replaced and plant started at 11:35 Am. & Rain & Cloudy
2014-08-25 | 780 | 820 | 820 | 851 | 36.31 | 3307.31 | 3152.25 | 155.06 | 3347 | 4.045 | 80.64 | Cloudy Day
2014-08-26 | 1170 | 1238 | 1238 | 1307 | 74.22 | 5027.22 | 4830 | 197.22 | 5055 |  |  | D.O Fuse of "Y" phase blown at 10:10 Am, Fuse was replaced and plant started at 11:24 (WO#1306835)
2014-08-27 | 978 | 1040 | 1040 | 1084 | 59.11 | 4201.11 | 4027.5 | 173.61 | 4224 |  |  | D.O Fuse of "R"Y"B" phase blown at 12:10 Am, Fuse was replaced and plant started at 13:08 Pm.
2014-08-28 | 1102 | 1165 | 1175 | 1187 | 58.56 | 4687.56 | 4502.25 | 185.31 | 4714 |  |  | Cloudy Day
2014-08-29 | 1024 | 1091 | 1092 | 1125 | 55.25 | 4387.25 | 4224 | 163.25 | 4421 |  |  | Cloudy Day
2014-08-30 | 384 | 407 | 412 | 403 | 12.41 | 1618.41 | 1499.25 | 119.16 | 1640 |  |  | Rain & Cloudy Day
2014-08-31 | 939 | 995 | 995 | 1063 | 48.44 | 4040.44 | 3877.5 | 162.94 | 4083 |  |  | D.O Fuse of "Y" phase blown at 12:50 Am, Fuse was replaced and plant started at 13:08 (WO#1383416) Rain & Cloudy Day
2014-09-01 | 548 | 588 | 588 | 603 | 18.43 | 2345.43 | 2223 | 122.43 | 2378 |  |  | D.O Fuse of "R" phase blown at 13:30 Am, Fuse was replaced and plant started at 13:48 (WO#) Rain & Cloudy Day & 2 time Grid Failure from-8:10 to 10:46 wo#(1395963) & 11:30 to 12:25wo#(1397012)
2014-09-02 | 837 | 882 | 894 | 900 | 28.6 | 3541.6 | 3407.25 | 134.35 | 3580 |  |  | Rain & Cloudy Day
2014-09-03 | 672 | 712 | 712 | 733 | 21.16 | 2850.16 | 2709.75 | 140.41 | 2883 |  |  | Cloudy Day
2014-09-04 | 221 | 237 | 243 | 230 | 6.3 | 937.3 | 841 | 96.3 | 999 |  |  | Grid Failure From - 14:08 to 14:54 WO#1437911 & Rain & Cloudy & Inv-No:-4 Filter & inveter cleaning
2014-09-05 | 910 | 962 | 967 | 970 | 24.83 | 3833.83 | 3668.25 | 165.58 | 3862 |  |  | Cloudy Day
2014-09-06 | 1074 | 1136 | 1142 | 1176 | 29.96 | 4557.96 | 4385.25 | 172.71 | 4591
2014-09-07 | 961 | 1023 | 1029 | 1034 | 28.51 | 4075.51 | 3901 | 174.51 | 4097 |  |  | D.O Fuse of "R'&'Y" phase blown at 10:47 Am, Fuse was replaced and plant started at 11:20 (WO#1486006) Cloudy Day
2014-09-08 | 204 | 221 | 220 | 212 | 5.99 | 862.99 | 759 | 103.99 | 921 |  |  | Grid Failure From - 15:34 to 15:44 WO#1501674 & Grid Failure From - 17:02 to 17:37 & Grid Failure From - 17:54 to 18:16 & Fully Rain
2014-09-09 | 170 | 186 | 187 | 178 | 4.62 | 725.62 | 619.5 | 106.12 | 767 |  |  | Rain & Cloudy Day
2014-09-10 | 152 | 159 | 164 | 153 | 3.82 | 631.82 | 525 | 106.82 | 668 | 816 | 79.79 | Rain & Cloudy Day
2014-09-11 | 452 | 480 | 486 | 463 | 13.27 | 1894.27 | 1791 | 103.27 | 1941 | 2.15 | 87.99 | Rain & Cloudy Day
2014-09-12 | 685 | 729 | 729 | 738 | 25.74 | 2906.74 | 2772.75 | 133.99 | 2947 | 3.507 | 81.9 | Cloudy Day
2014-09-13 | 678 | 724 | 729 | 724 | 27.22 | 2882.22 | 2750.25 | 131.97 | 2924 | 3.427 | 83.16 | Grid Failure From - 16:50 to 16:54 & Cloudy Day
2014-09-14 | 786 | 831 | 831 | 841 | 34.18 | 3323.18 | 3180 | 143.18 | 3357 | 4.019 | 81.41 | Cloudy Day
2014-09-15 | 740 | 774 | 781 | 787 | 34.26 | 3116.26 | 2978.25 | 138.01 | 3148 | 3.837 | 79.96 | Rain & Cloudy Day
2014-09-16 | 1074 | 1142 | 1142 | 1172 | 52.04 | 4582.04 | 4416.75 | 165.29 | 4619 |  |  | Cloudy Day
2006-09-17 | 962 | 1024 | 1017 | 1038 | 49.41 | 4090.41 | 3917.25 | 173.16 | 4105 | 5.617 | 71.22 | Grid Failure From - 13:02 to 14:20 WO#1631677 & Cloudy Day
2006-09-18 | 1170 | 1226 | 1233 | 1246 | 69.4 | 4944.4 | 4755 | 189.4 | 4971 | 6.588 | 73.54 | D.O Fuse of "R" phase blown at 12:12 pm, Fuse was replaced and plant started at 12:34 (WO#1644643) & Cloudy Day
2006-09-19 | 1260 | 1312 | 1322 | 1353 | 73.65 | 5320.65 | 5111.25 | 209.4 | 5334 | 6.765 | 76.92
2006-09-20 | 1272 | 1329 | 1335 | 1393 | 74 | 5403 | 5191.5 | 211.5 | 5424 | 6.819 | 77.52 | Today I Replaced The 1 D.C.12Amp Fuse Link of The String-NO- 02 ++tive in AJB-101 of The Inverter-4 during The Period of 10:40 To 10:45.WO#(1671005)
2006-09-21 | 1222 | 1266 | 1266 | 1316 | 70.68 | 5140.68 | 4939.5 | 201.18 | 5167 | 6.58 | 76.53
2006-09-22 | 938 | 973 | 967 | 1011 | 51.04 | 3940.04 | 3774.75 | 165.29 | 3963 | 5.131 | 75.27 | Grid Failure From - 10:12 to 10:35 WO#1697916 & Cloudy Day
2006-09-23 | 1176 | 1215 | 1215 | 1299 | 67.97 | 4972.97 | 4784.25 | 188.72 | 4998 | 6.43 | 75.75 | Cloudy Day
2006-09-24 | 1125 | 1165 | 1188 | 1265 | 64.04 | 4807.04 | 4620.75 | 186.29 | 4832 | 6.224 | 75.66 | Grid Failure From - 8:28 to 8:37 WO#1724239
2006-09-25 | 882 | 927 | 955 | 969 | 29.07 | 3762.07 | 3607.5 | 154.57 | 3796 | 5.404 | 68.46 | Today I Replaced The D.C.12Amp Fuse Link of The String- 08 --tive in AJB-110 of The Inverter-2 during The Period of 12:10 To 12:15.WO#(1737960) & Grid Failure From - 07:29 to 07:55 & our vcb trip After reset vcb plant started 9:32 WO#1736380 & Cloudy
2006-09-26 | 1140 | 1198 | 1238 | 1245 | 39.44 | 4860.44 | 4656 | 204.44 | 4870 | 6.282 | 75.55
2006-09-27 | 1192 | 1261 | 1306 | 1321 | 39.78 | 5119.78 | 4924.5 | 195.28 | 5148 | 6.678 | 75.15
2014-09-28 | 1126 | 1182 | 1216 | 1257 | 38.25 | 4819.25 | 4625.25 | 194 | 4840 | 6.369 | 74.06
2014-09-29 | 994 | 1051 | 1079 | 1111 | 34.33 | 4269.33 | 4090.5 | 178.83 | 4292 | 5.623 | 74.39 | Cloudy Day
2014-09-30 | 996 | 1046 | 1075 | 1114 | 34.08 | 4265.08 | 4095 | 170.08 | 4294 | 5.629 | 74.35 | Grid Failure From - 10:12 to 10:35 WO#1822946 & Cloudy Day
2014-10-01 | 1096 | 1165 | 1187 | 1230 | 35.6 | 4713.6 | 4522.5 | 191.1 | 4739 | 6.174 | 74.81
2014-10-02 | 1131 | 1198 | 1221 | 1279 | 36.23 | 4865.23 | 4683 | 182.23 | 4894 | 6.364 | 74.95
2014-10-03 | 1153 | 1221 | 1272 | 1294 | 36.51 | 4976.51 | 4785.75 | 190.76 | 5024 | 6.493 | 75.41
2014-10-04 | 1148 | 1210 | 1277 | 1278 | 37.31 | 4950.31 | 4756.5 | 193.81 | 4973 | 6.414 | 75.56
2014-10-05 | 918 | 972 | 1012 | 1035 | 30.02 | 3967.02 | 3792.75 | 174.27 | 3981 | 5.159 | 75.21 | Grid Failure From - 14:17 to 16:53 WO#1888096
2014-10-06 | 882 | 924 | 984 | 974 | 37.77 | 3801.77 | 3647.25 | 154.52 | 3856 | 4.855 | 77.41 | Grid Failure From - 16:32 to 16:34 WO#1697916
2014-10-07 | 1159 | 1227 | 1295 | 1323 | 52.03 | 5056.03 | 4857 | 199.03 | 5076 | 6.497 | 76.14 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 --tive in AJB-105 of The Inverter-4 during The Period of 10:45 To 10:50.WO#1914138
2014-10-08 | 40 | 1152 | 1176 | 1222 | 44.4 | 3634.4 | 3439.5 | 194.9 | 3627 |  |  | Grid Failure From - 8:10 to 8:25 WO#1926295 & 8:50 Inverter 1 is down, informed ABB. They will be working to resolve this issue WO#1926581
[6 empty] | 0 |  | 0
2014-10-09 |  | 1199 | 1193 | 1212 | 44.14 | 3648.14 | 3490.5 | 157.64 | 3685 | 6.057 | 5929 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-10 |  | 1232 | 1198 | 1210 | 44.52 | 3684.52 | 3535.5 | 149.02 | 3715 | 6.172 | 58.66 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-11 |  | 1091 | 1057 | 1066 | 30.15 | 3244.15 | 3108 | 136.15 | 3260 | 6.284 | 50.56 | Grid Failure From - 8:47 to 9:25 & D.O.Fuse of `B` Phase also Blown of With High Frequncy & Fuse link sport also Blown ,Then Plant Started From - 9:42 .WO # 1972636
2014-10-12 |  | 1148 | 1227 | 1239 | 34.77 | 3648.77 | 3514.5 | 134.27 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-13 |  | 1266 | 1221 | 1207 | 34.84 | 3728.84 | 3570.75 | 158.09 | 3764 | 6.439 | 56.97 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-14 |  | 1222 | 1165 | 1166 | 34 | 3587 | 3429.75 | 157.25 | 3621 | 6.362 | 55.47 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-15 |  | 1125 | 1080 | 1094 | 32.36 | 3331.36 | 3183 | 148.36 | 3371 | 5.931 | 55.39 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & cleaning & tietnece L.T panel
2014-10-16 |  | 1063 | 1017 | 1072 | 26.56 | 3178.56 | 3029.25 | 149.31 | 3222 | 6.268 | 50.1 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & cleaning & tietnece L.T panel & Grid Failure From - 8:27 to 9:43 WO#2043269
2014-10-17 |  | 1209 | 1148 | 1277 | 30.23 | 3664.23 | 3507.75 | 156.48 | 3708 | 6.361 | 56.81 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581, & Today I Replaced The D.C.12Amp Fuse Link of The String- 04 --tive in AJB-105 of The Inverter-4 during The Period of 10:50 To 10:55.WO#2057851
2014-10-18 |  | 1204 | 1181 | 1271 | 29.99 | 3685.99 | 3530.25 | 155.74 | 3719 | 6.385 | 56.76 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-19 |  | 1160 | 1171 | 1197 | 30.33 | 3558.33 | 3405 | 153.33 | 3599 | 6.129 | 57.23 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581
2014-10-20 |  | 1124 | 1158 | 1197 | 29.62 | 3508.62 | 3354.75 | 153.87 | 3547 | 5.976 | 57.84 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 17:15 to 17:42 WO#2101384
2014-10-21 |  | 1171 | 1205 | 1221 | 29.69 | 3626.69 | 3489 | 137.69 | 3691 | 5.094 | 70.62 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 11:03 to 11:11 WO#2110541
2014-10-22 |  | 1187 | 1181 | 1136 | 29.47 | 3533.47 | 3384.75 | 148.72 | 3585 | 6.017 | 58.07 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 8:44 to 8:54 WO#2122704
2014-10-23 |  | 1159 | 1131 | 316 | 27.9 | 2633.9 | 2490.75 | 143.15 | 2694 | 5.928 | 44.29 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 11:05 to 11:10 WO#2138394 & inverter 4 producing low due to cybro controler faulty WO#2138162
2014-10-24 |  | 1051 | 1029 | 1002 | 33.39 | 3115.39 | 2977.5 | 137.89 | 3186 | 5.155 | 60.23 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581.
2014-10-25 |  | 1171 | 1142 | 1128 | 38.03 | 3479.03 | 3328.5 | 150.53 | 3547 | 5.73 | 60.33 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 16:39 to 16:44 WO#2175271
2014-10-26 |  | 933 | 910 | 880 | 30.35 | 2753.35 | 2611.5 | 141.85 | 2793 | 4.498 | 60.52 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581.
2014-10-27 |  | 1023 | 995 | 985 | 33.97 | 3036.97 | 2895 | 141.97 | 3082 | 5.008 | 59.98 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 15:06 to 16:13 WO#
2014-10-28 |  | 96 | 91 | 85 | 3.84 | 275.84 | 209.25 | 66.59 | 317 |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure & Government side 11kv H Poll "R" Phase L.A Failure From - 8:17 to 15:55 WO#2212818
2014-10-29 |  | 204 | 197 |  | 6.18 | 407.18 | 396 | 11.18 |  |  |  | inverter 1 & 4 is down iformed ABB & Schneider & Grid Failure with High voltage than our plant sort circuit than plant(inverter 1&2) started 11:55 & U.P.S & Battery charger Blown
2014-10-30 |  | 480 | 470 |  | 15.99 | 965.99 | 899.25 | 66.74 |  |  |  | inverter 1 & 4 is down iformed ABB & Schneider & Grid Failure with High voltage than our plant sort circuit than plant(inverter 1&2) started 11:55 & U.P.S & Battery charger Blown & our side visit schneider engineer & resolve issue inverter no-4 started
2014-10-31 |  | 758 | 740 | 734 | 24.58 | 2256.58 | 2142 | 114.58 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & U.P.S & Battery charger Blown
0
2014-11-01 |  | 1000 | 978 | 964 | 33.64 | 2975.64 | 2849.25 | 126.39 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & U.P.S & Battery charger Blown
2014-11-02 |  | 1035 | 1008 | 980 | 36 | 3059 | 2928.75 | 130.25 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & U.P.S & Battery charger Blown
2014-11-03 |  | 972 | 927 | 1034 | 36.96 | 2969.96 | 2853.75 | 116.21 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown & U.P.S rectified
2014-11-04 |  | 1052 | 1006 | 1033 | 36.32 | 3127.32 | 2996.25 | 131.07 | 3147 | 5.381 | 57 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown
2014-11-05 |  | 1198 | 1131 | 1244 | 39.8 | 3612.8 | 3468.75 | 144.05 | 3623 | 5.793 | 60.95 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown
2014-11-06 |  | 1216 | 1159 | 1300 | 40.56 | 3715.56 | 3567 | 148.56 | 3739 | 6.237 | 58.42 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown & Grid failure from 16:21 to 16:25
2014-11-07 | 6 | 1170 | 1108 | 1247 | 56.77 | 3587.77 | 3450 | 137.77 | 3624 | 6.146 | 57.47 | Grid Failure From - 9:50 to 9:55 WO#2369551 & ABB Service engineer Mr. Salim has come to site. He has rectified the problem by replacing faulty ACB. Inverter starte at 16:20
2014-11-08 | 1046 | 1097 | 1040 | 1087 | 65.07 | 4335.07 | 4150.5 | 184.57 | 4355 | 5.763 | 73.65 | Grid Failure From 9:18 to 9:30 & inverter no 4 down due to auxiliary supply MCB tripped and it was not able to reset for 30 minutes after that reset @ 10:00 AM. WO #2387806
2014-11-09 | 1040 | 1102 | 1052 | 1169 | 66.25 | 4429.25 | 4255.5 | 173.75 | 4458 | 5.723 | 75.92 | Battery charger Blown
2014-11-10 | 950 | 1001 | 989 | 1035 | 57.55 | 4032.55 | 3867 | 165.55 | 4058 | 5.201 | 76.04 | Battery charger Blown
2014-11-11 | 899 | 950 | 1006 | 967 | 52.43 | 3874.43 | 3708 | 166.43 | 3894 | 4.926 | 77.04 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07 ++tive in AJB-116 of The Inverter-3 during The Period of 10:35 To 10:40.WO#(2435089) & Battery charger Blown
2014-11-12 | 910 | 1017 | 1035 | 1015 | 54.88 | 4031.88 | 3864 | 167.88 | 4057 | 5.1 | 77.53 | Battery charger Blown
2014-11-13 | 905 | 1023 | 1000 | 990 | 51.65 | 3969.65 | 3801 | 168.65 | 3991 | 4.986 | 78.01 | Battery charger Blown
2014-11-14 | 842 | 905 | 882 | 861 | 42.65 | 3532.65 | 3389.25 | 143.4 | 3579 | 4.646 | 75.08 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 ++tive in AJB-102 of The Inverter-1 during The Period of 11:55 To 12:00.WO#(2480488) & Battery charger Blown & Grid Failure From - 15:54 to 16:03 WO#2482657
2014-11-15 | 695 | 729 | 713 | 690 | 28.43 | 2855.43 | 2739 | 116.43 | 2851 | 3.764 | 73.82 | Battery charger Blown
2014-11-16 | 792 | 837 | 819 | 825 | 37.41 | 3310.41 | 3165.75 | 144.66 | 3366 | 4.314 | 76.04 | Battery charger Blown
2014-11-17 | 887 | 950 | 916 | 972 | 37.37 | 3762.37 | 3612.75 | 149.62 | 3802 | 5.035 | 73.59 | Battery charger Blown & Grid Failure From - 8:00 to 9:20 WO#2541824 & 9:59 to 10:05 WO#2542101 & 17:32 to 17:46 WO#2546487
2014-11-18 | 877 | 927 | 882 | 936 | 47.83 | 3669.83 | 3522 | 147.83 | 3711 | 5.049 | 71.63 | Battery charger Blown Grid & Failure From - 8:31 to 9:09 WO#2556092 & inverter no-3 morning time note wake up so reset (3 time inverter on off) to inverter so started 9:10 WO#2555238 & Array /balance of system
2014-11-19 | 1017 | 1079 | 1074 | 1105 | 61.98 | 4336.98 | 4165.5 | 171.48 | 4370 | 5.64 | 75.51 | Battery charger Blown & Tracker P.M
2014-11-20 | 1074 | 1143 | 1142 | 1172 | 68.94 | 4599.94 | 4428 | 171.94 | 4636 | 6.053 | 74.64 | Battery charger Blown &Combiner & Grid Failure From- 15:31 to 15:43 WO#2589251
2014-11-21 | 995 | 1057 | 1086 | 1078 | 60.32 | 4276.32 | 4108.5 | 167.82 | 4334 | 5.496 | 76.85 | Seeds (Das) meteorological (MET) station p.m & Battery charger blown
2014-11-22 | 1029 | 1108 | 1131 | 1111 | 62.61 | 4441.61 | 4267.5 | 174.11 | 4471 | 5.753 | 75.74 | Battery charger Blown & Grid Failure From- 16:59 to 17:09 WO# 2627748 & 17:25 to 17:30 WO# 2627992
2014-11-23 | 1006 | 1102 | 1102 | 826 | 61.33 | 4097.33 | 3942 | 155.33 | 4141 | 5.741 | 70.3 | Battery charger blown & Grid failure from- 9:48 to 9:53 WO# 2639096 & Inverter #4 due to auto tripped it was not able to reset 1:35 hour after that reset @2:35 WO# 2640754
2014-11-24 | 996 | 1114 | 1091 | 367 | 59.29 | 3627.29 | 3456 | 171.29 | 3648 | 5.608 | 63.4 | Inverter #4 is down 11:12 AM informed Schneider WO#2656601 & Transformer No-4 (P.M R,B,N,)Oil Lickege gass kitt failure
2014-11-25 | 1006 | 1102 | 1063 | 1035 | 58.03 | 4264.03 | 4095 | 169.03 | 4291 | 5.529 | 75.64 | Grid failure from- 13:18 to 13:30 WO#2671705 & Module visual Inspection P.M
2014-11-26 | 1057 | 1125 | 1085 | 1031 | 56.49 | 4354.49 | 4188.75 | 165.74 | 4386 | 5.834 | 73.27 | Inverter #4 is morning time on, off on, off, call to schneider service engineer is going to attend this problem tomorrow.
2014-11-27 | 1063 | 1131 | 1091 | 348 | 56.47 | 3689.47 | 3512.25 | 177.22 | 3720 | 5.761 | 70.9 | Inverter # 4 ,11:15 auto trip and it was not able to reset after schneider engineer come to our side and resolve issue inverter started from 17:05 WO#2700380
2014-11-28 | 1040 | 1103 | 1063 | 874 | 55.32 | 4135.32 | 3983.25 | 152.07 | 4173 | 5.764 | 68.53 | Inverter # 4 ,11:35 auto tripped & 13:05 auto start & Grid Failure From -17:05 to 17:11 & scond time 17:27 to 17:33 WO# 2719696 & WO#2720220
2014-11-29 | 984 | 1040 | 1012 |  | 51.45 | 3087.45 | 2931.75 | 155.7 | 3115 | 5.418 | 66.16 | Inverter 4 is down, informed Schneider.They will be working resolve this issue & Grid Failure From- 17:31 to 17:39 WO#2738903
2014-11-30 | 978 | 1040 | 1023 | 957 | 51.77 | 4049.77 | 3883.5 | 166.27 | 4084 | 5.426 | 63.79 | Inverter #4 replesh the D.C 12 Volts realy & solle the issue Inverter started 09:10
2014-12-01 | 904 | 955 | 967 | 976 | 46.94 | 3848.94 | 3686.25 | 162.69 | 3879 | 5.317 | 71.1 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 ++tive in AJB-101 of The Inverter-4 during The Period of 10:35 To 10:40.WO#(2766976) & Grid Failure From- 14:08 to 15:09 WO#2769479
2014-12-02 | 916 | 995 | 995 | 1008 | 51.67 | 3965.67 | 3809.25 | 156.42 | 4004 | 5.251 | 74.31 | Grid Failure From- 11:32 to 11:45 WO#2783874
2014-12-03 | 1035 | 1131 | 1108 | 1113 | 61.31 | 4448.31 | 4266 | 182.31 | 4468 | 5.768 | 75.49 | Grid Failure From- 16:50 to 16:58 WO#2803128
2014-12-04 | 1057 | 1131 | 1108 | 1095 | 62.69 | 4453.69 | 4283.25 | 170.44 | 4483 | 5.81 | 75.2
2014-12-05 | 1023 | 1097 | 1063 | 1057 | 58.87 | 4298.87 | 4126.5 | 172.37 | 4342 | 5.608 | 75.46 | Grid Failure From- 12:39 to 13:05 WO#2832390
2014-12-06 | 1024 | 1096 | 1069 | 1076 | 52.46 | 4317.46 | 4153.5 | 163.96 | 4365 | 5.532 | 76.9 | Grid Failure From 15:00 to 15:04 WO#2848950
2014-12-07 | 1068 | 1148 | 1114 | 1143 | 62.32 | 4535.32 | 4355.25 | 180.07 | 4558 | 5.919 | 75.05 | Grid Failure-Plant started 7:55 to WO#2861355
2006-12-08 | 972 | 1051 | 1023 | 1035 | 50.84 | 4131.84 | 3963 | 168.84 | 4165 | 5.425 | 74.82 | Grid Failure From 7:05 to 8:07 WO#2878909
2006-12-09 | 1052 | 1131 | 1142 | 1023 | 58.23 | 4406.23 | 4231.5 | 174.73 |  |  |  | Inverter No-4 started 9:13 WO#2895864
2006-12-10 | 972 | 1057 | 1074 | 1015 | 51.41 | 4169.41 | 3995.25 | 174.16 | 4191
2006-12-11 | 916 | 1018 | 1000 | 909 | 48.04 | 3891.04 | 3729.75 | 161.29 | 3911 | 4.893 | 77.9
2006-12-12 | 944 | 1029 | 1012 | 930 | 48.41 | 3963.41 | 3792 | 171.41 | 3994
2006-12-13 | 967 | 1023 | 1012 | 929 | 49.31 | 3980.31 | 3822 | 158.31 | 4001 | 5.146 | 75.77
2014-12-14 | 1023 | 1091 | 1069 | 986 | 53.29 | 4222.29 | 4048.5 | 173.79 | 4234 | 5.435 | 75.92
2014-12-15 | 1086 | 1159 | 1142 | 1079 | 57.41 | 4523.41 | 4338.75 | 184.66 | 4539 | 5.882 | 75.21
2014-12-16 | 1000 | 1057 | 1046 |  | 55.14 | 3158.14 | 3026.25 | 131.89 | 3199 | 5.336 | 58.43 | Grid Failure From 7:05 to 8:07 WO#2878909 & Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon)
2014-12-17 | 1074 | 1142 | 1131 |  | 65.75 | 3412.75 | 3243 | 169.75 | 3423 | 5.686 | 58.67 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon)
2014-12-18 | 967 | 1018 | 1062 |  | 60.44 | 3107.44 | 2961.75 | 145.69 | 3143 |  |  | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 15:19 to 16:35 WO# 3108567 & 2 Time 16:39 to 16:44 WO#3108613 3 Time 17:42 to 1749 WO#3109816
2014-12-19 | 860 | 978 | 1001 |  | 46.05 | 2885.05 | 2751 | 134.05 | 2900 | 5.059 | 55.87 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 14:35 to 16:05 WO#3127429 & Inverter 1 is down Informed ABB (Inverter side Mini power supply faulty)
2014-12-20 | 390 | 435 | 531 |  | 21.83 | 1377.83 | 1298.25 | 79.58 | 1415 | 2.472 | 55.79 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 12:24 to 12:47 WO#3144608 & 15:21 to 15:23 WO#3150822 & Inverter 1 is down Informed ABB (Inverter side Mini power supply faulty) inverter started 11:40 a.m & Cloudy Day
2014-12-21 | 1051 | 1142 | 1148 |  | 66.68 | 3407.68 | 3268.5 | 139.18 | 3414 | 5.867 | 56.71 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 14:20 to 14:30 WO# 3167155
2014-12-22 | 1018 | 1058 | 1063 |  | 61.05 | 3200.05 | 3055.5 | 144.55 | 3212 |  |  | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-103 of The Inverter-1 during The Period of 9:55 To 10:00.WO#(3181932) & Inverter No-1 mini power bank (D.C.15 VOLTS) Repleshed & Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon)
2014-12-23 | [5 empty] | 0 |  | 0 | 560 |  |  | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 10:25 to 19:30 WO# 3201757
2014-12-24 | [5 empty] | 0 |  | 0 | 3159 |  |  | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon)
2014-12-25 | 1012 | 1063 | 1063 |  | 62.49 | 3200.49 | 3074.25 | 126.24 | 3212 | 5.473 | 57.2 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 12:38 to 12:43 WO# 3240768
2014-12-26 | 1131 | 1176 | 1215 |  | 73.58 | 3595.58 | 3441 | 154.58 | 3589 | 6.107 | 57.27 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon)
2014-12-27 | 882 | 933 | 967 |  | 56.9 | 2838.9 | 2713.5 | 125.4 | 2841 | 5.052 | 54.81 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 14:31 to 16:38 WO# 3283954
2014-12-28 | 1085 | 1187 | 1210 |  | 67.18 | 3549.18 | 3384.75 | 164.43 | 3542 | 5.93 | 58.21 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 --tive in AJB-101 of The Inverter-1 during The Period of 15:25 To 15:30.WO#(3300992) & Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon)
2014-12-29 | 667 | 707 | 723 |  | 42.84 | 2139.84 | 2031.75 | 108.09 | 2155 | 3.683 | 57.02 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 12:48 to 12:54 WO# 3316468 & Grid Failure From 13:22 to 17:41 WO#
2014-12-30 | 1001 | 1080 | 1086 |  | 56.74 | 3223.74 | 3087 | 136.74 | 3237 | 5.335 | 59.13 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 17:09 to 17:14 WO#
2014-12-31 | 899 | 949 | 944 | 827 | 48.65 | 3667.65 | 3494.25 | 173.4 | 3623 | 4.717 | 74.86 | Inverter 4 is resolve the issue started 9:05 (Replesh Inverter side D.C,contector) & Grid Failure From 16:47 to 17:48 WO#
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0

## 2015
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2015
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 1104500525 | 7802195 | 2100570073/ 2100567820/ 2100567898
2015-01-01 | 542 | 560 | 509 | 529 | 22.5 | 2162.5 | 2035.5 | 127 | 2197 | 2.78 | 77.02 | Inverter No- 3 Auto trip 8:50 (modulre fan problem) 9:50 Auto start WO#3381467 & Today I Replaced The D.C.12Amp Fuse Link of The String- 01 --tive in AJB-105 of The Inverter-4 during The Period of 10:25 To 10:30.WO#(3381507)
2015-01-02 | 792 | 831 | 842 | 821 | 36.93 | 3322.93 | 3177 | 145.93 | 3352 | 4.15 | 78.72 | Grid Failure From 13:02 to 13:09 WO#3402756
2006-01-03 | 933 | 978 | 995 | 953 | 49.96 | 3908.96 | 3755.25 | 153.71 | 3942 | 5.303 | 72.45 | Grid Failure From 8:05 to 9:19 WO#3419549
2015-01-04 | 1046 | 1102 | 1114 | 1071 | 61.29 | 4394.29 | 4210.5 | 183.79 | 4430 |  |  | Grid Failure From 16:45 to 18:45 WO#3450753
2015-01-05 | 893 | 939 | 944 | 902 | 41.55 | 3719.55 | 3556.5 | 163.05 | 3744 | 4.8 | 76.02 | The GERMI Plant has Failure The GRID From -14:34 to 17:54 (wo#3470232) With high Frequency so our D.O Fuse of 'B' phase blown at 17:54 to 18:40 (WO#3473799)
2015-01-06 | 1040 | 1097 | 1102 | 1065 | 58.77 | 4362.77 | 4194 | 168.77 | 4388 | 5.726 | 74.69 | Today I Replaced The D.C.12Amp Fuse Link of The String- 08 --tive in AJB-105 of The Inverter-4 during The Period of 10:05 To 10:10.WO#(3486775) & Grid Failure From 15:57 to 18:28 WO#
2015-01-07 | 543 | 571 | 577 | 551 | 29.48 | 2271.48 | 2167.5 | 103.98 | 3212 | 3.165 | 71.19 | Grid Failure From 15:57 to 18:28 WO# 3518160
2015-01-08 | 1051 | 1113 | 1120 | 1077 | 60.24 | 4421.24 | 4242.75 | 178.49 | 4444 | 5.805 | 74.61 | Grid Failure From 17:42 to 18:52 WO# 3545933
2015-01-09 | 1092 | 1154 | 1159 | 1150 | 66.91 | 4621.91 | 4439.25 | 182.66 | 4647 | 6.106 | 74.17 | Battery water Fileed in 5 kw Battery Bank
2015-01-10 | 1079 | 1130 | 1130 | 1138 | 71.79 | 4548.79 | 4379.25 | 169.54 | 4580 | 6.021 | 74.13 | Grid Failure From 13:48 to 13:57 WO# 3593881
2015-01-11 | 1091 | 1137 | 1154 | 1122 | 70.17 | 4574.17 | 4389.75 | 184.42 | 4592 | 6.051 | 73.96
2015-01-12 | 1041 | 1085 | 1124 | 1066 | 66.71 | 4382.71 | 4197 | 185.71 | 4398 | 6.031 | 71.07 | Grid Failure From 14:48 to 15:08 WO#3648062 & 15:26 to 15:44 WO#3648693
2015-01-13 | 1034 | 1080 | 1126 | 1048 | 60.77 | 4348.77 | 4176.75 | 172.02 | 4401 | 5.773 | 74.3
2015-01-14 | 786 | 820 | 847 | 772 | 37.51 | 3262.51 | 3114 | 148.51 | 3290 | 4.273 | 75.04 | Cloudy day & Inverer 4 run healthy but exhaust fan faulty
2015-01-15 | 989 | 1023 | 1069 | 966 | 54.31 | 4101.31 | 3912.75 | 188.56 | 4110 | 5.362 | 74.7 | Inverter no-4 run healthy but exhaust fan not working
2015-01-16 | 1040 | 1102 | 1119 | 1039 | 59.66 | 4359.66 | 4181.25 | 178.41 | 4379 | 5.738 | 74.38 | Grid Failure From 11:05 to 11:08 WO#3758192
2015-01-17 | 1143 | 1193 | 1204 | 1113 | 66.42 | 4719.42 | 4523.25 | 196.17 | 4725 | 6.169 | 74.69 | Grid Failure From 13:39 to 13:46 WO#3798043
2015-01-18 | 1192 | 1238 | 1238 | 1153 | 69.02 | 4890.02 | 4687.5 | 202.52 | 4901 | 6.416 | 74.45 | NO any Issue
2015-01-19 | 1108 | 1142 | 1154 | 1072 | 63.1 | 4539.1 | 4354.5 | 184.6 | 4548 | 5.922 | 74.85 | Transformer -1 & 4 (P.M)
2015-01-20 | 950 | 978 | 984 | 904 | 48.11 | 3864.11 | 3708.75 | 155.36 | 3872 | 5.094 | 74.08 | NO any Issue
2015-01-21 | 509 | 515 | 520 | 506 | 19.88 | 2069.88 | 1950.75 | 119.13 | 2092 | 2.54 | 80.27 | fully cloudy Day
2015-01-22 | 1131 | 1198 | 1215 | 1171 | 59.33 | 4774.33 | 4583 | 191.33 | 4797 | 6.087 | 76.81 | NO any Issue
2015-01-23 | 1142 | 1205 | 1227 | 1171 | 69.43 | 4814.43 | 4617.75 | 196.68 | 4824 | 6.101 | 77.06 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-101 of The Inverter-4 during The Period of 10:25 To 10:30.WO#(3984715)
2015-01-24 | 1012 | 1063 | 1080 | 1020 | 57.57 | 4232.57 | 4059 | 173.57 | 4271 | 5.268 | 78.97 | Grid supply failure from 13:29 to 13:34(WO#4024145)
2015-01-25 | 622 | 650 | 661 | 618 | 26.01 | 2577.01 | 2443.5 | 133.51 | 2621 | 3.217 | 79.4 | NO any Issue
2015-01-26 | 1023 | 1074 | 1097 | 1010 | 52.93 | 4256.93 | 4077.75 | 179.18 | 4292 | 5.451 | 76.74 | Grid supply failure from 17:22 to 17:55 (WO#)
2015-01-27 | 1159 | 1221 | 1238 | 1180 | 66.97 | 4864.97 | 4671.75 | 193.22 | 4875 | 6.162 | 77.1 | NO any Issue
2015-01-28 | 1255 | 1334 | 1362 | 1293 | 77.77 | 5321.77 | 5103 | 218.77 | 5320 |  |  | Internet failure
2015-01-29 | 1211 | 1289 | 1312 | 1226 | 74.45 | 5112.45 | 4900.5 | 211.95 | 5102 | 6.498 | 76.52 | Grid supply failure from 12:20 to 12:30 (WO#4194605)
2015-01-30 | 1238 | 1329 | 1334 | 1267 | 76.26 | 5244.26 | 5031 | 213.26 | 5251 | 6.586 | 77.7 | NO any Issue
2015-01-31 | 1260 | 1334 | 1340 | 1386 | 76.27 | 5396.27 | 5086.5 | 309.77 | 5308 | 6.783 | 76.27 | Inverter no- 1,2,3,4, filter cleaning
2015-02-01 | 1148 | 1210 | 1221 | 1153 | 72.39 | 4804.39 | 4611 | 193.39 | 4805 | 6.005 | 77.9889 | NO any Issue
2015-02-02 | 1098 | 1153 | 1159 | 1115 | 65.25 | 4590.25 | 4403.25 | 187 | 4609 | 5.983 | 75.08 | NO any Issue
2015-02-03 | 735 | 775 | 775 | 766 | 30.54 | 3081.54 | 2947.5 | 134.04 | 3111 | 4.024 | 75.35 | Grid supply failure from 9:55 to 12:38 (WO#4378455)
2015-02-04 | 1227 | 1288 | 1317 | 1273 | 73.57 | 5178.57 | 4968 | 210.57 | 5207 | 6.545 | 77.54 | Module cleaning done Inverter 3 Row N,O,P,Q,R. Total module cleaning 610
2015-02-05 | 1102 | 1165 | 1204 | 1129 | 63.38 | 4663.38 | 4477.5 | 185.88 | 4683 | 5.798 | 78.72 | Module cleaning done Inverter 2 & 3 Row K,L,M. Total module cleaning 650
2015-02-06 | 1040 | 1125 | 1131 | 1049 | 60.32 | 4405.32 | 4227.75 | 177.57 | 4425 | 5.684 | 75.87 | Module cleaning done Inverter 2 Row I,J. Total module cleaning 650
2015-02-07 | 1125 | 1198 | 1198 | 1129 | 66.99 | 4716.99 | 4522.5 | 194.49 | 4730 | 6.103 | 76.49 | Module cleaning done Inverter 2 & 3 Row . Total module cleaning 650 & Grid supply failure from 9:32 to 12:35 (WO#4540622)
2015-02-08 | 1199 | 1272 | 1278 | 1196 | 72.62 | 5017.62 | 4812.75 | 204.87 | 5023 | 6.407 | 76.41 | NO any Issue
2015-02-09 | 1261 | 1323 | 1323 | 1275 | 77.67 | 5259.67 | 5049 | 210.67 | 5267 | 6.666 | 77.01 | Module cleaning done Inverter 1 & 4 Row A,B.& A,B,C,D,E Total module cleaning 650
2015-02-10 | 1147 | 1199 | 1204 | 1167 | 65.98 | 4782.98 | 4591.5 | 191.48 | 4797 | 6.018 | 77.69 | Module cleaning done Inverter 4 Row .& F,G,H,I, Total module cleaning 650
2015-02-11 | 1125 | 1187 | 1199 | 1172 | 66.17 | 4749.17 | 4563.75 | 185.42 | 4769 | 6.044 | 76.9 | Module cleaning done Inverter 4 & Trackers, Row .& ,j,k,l, Total module cleaning 640
2015-02-12 | 1244 | 1317 | 1357 | 1312 | 79.38 | 5309.38 | 5109.75 | 199.63 | 5328 | 6.699 | 77.51 | Module cleaning done Inverter 3 Row ,O,P,Q,R,S,T, Total module cleaning 640
2015-02-13 | 1219 | 1307 | 1345 | 1287 | 77.68 | 5235.68 | 5032.5 | 203.18 | 5248 | 6.674 | 76.64 | Module cleaning done Inverter 3 & 2 Row ,K,L,M,N, Total module cleaning 645 & Replaced The Demaj module as a 11`nd From Uper Last of The `L` Row,String- 3 JB-110 (OLD Module Sr.no-PB10B068470151) NEW MODULE-PB10B047480118 & 2 Module Replaced Front of the Row no-T string no-1 AJB NO-117 INverter no-3 Damege modulr sr.no-PB10B071470175 NEW Module sr.no-PB10B068470104
2015-02-14 | 1161 | 1249 | 1272 | 1208 | 72.81 | 4962.81 | 4760.25 | 202.56 | 4969 | 6.383 | 75.87 | NO any Issue
2015-02-15 | 1119 | 1198 | 1221 | 1169 | 69.15 | 4776.15 | 4593 | 183.15 | 4791 | 6.186 | 75.48 | NO any Issue
2015-02-16 | 1199 | 1312 | 1312 | 1267 | 75.22 | 5165.22 | 4971 | 194.22 | 5207 | 6.606 | 76.82 | Module cleaning done Inverter 2 Row ,I,J Total module cleaning 604
2015-02-17 | 1210 | 1323 | 1317 | 1260 | 76.37 | 5186.37 | 4988.25 | 198.12 | 5197 | 6.613 | 76.59 | NO any Issue
2015-02-18 | 1102 | 1181 | 1176 | 1111 | 64.29 | 4634.29 | 4456.5 | 177.79 | 4652 | 6 | 75.56 | Grid supply failure from 16:14 to 16:19 (WO#5113888) & Module cleaning done Inverter 2 & 1, Row ,E,F,G,H, Total module cleaning 630
2015-02-19 | 1125 | 1165 | 1159 | 1085 | 63.91 | 4597.91 | 4413.75 | 184.16 | 4634 | 5.931 | 76.15 | Module cleaning done Inverter -1 & 4 Row ,A,B,C,D,Inverter -No-4 Row- A,B,C, Total module cleaning 640
2015-02-20 | 1153 | 1199 | 1187 | 1170 | 65.8 | 4774.8 | 4594.5 | 180.3 | 4800 | 6.22 | 75.21 | Module cleaning done Inverter -4 Row -D,E,F,G, Total module cleaning 652
2015-02-21 | 1142 | 1181 | 1176 | 1205 | 67.7 | 4771.7 | 4587.75 | 183.95 | 4811 | 6.379 | 73.5 | Grid Failure From - 13:10 to 13:13 (WO#5285421) & Module cleaning done Inverter-4 Row H,I,J, Total module cleaning 630 & Plant shutdown due to replace isolator switch (G.O.D) @ 17:18 to 2:25
2015-02-22 | 864 | 933 | 921 | 937 | 43.45 | 3698.45 | 3587.25 | 111.2 | 3721 |  |  | Our side Grid Failure due to R' Y' B', D.O, fuse Blown & 'B' Phase L.A, Failure @9:21 to 11:35 WO#5340473 & seeds P.M
2015-02-23 | 1147 | 1193 | 1222 | 1209 | 66.41 | 4837.41 | 4649.25 | 188.16 | 4855 | 6.286 | 75.27 | Module cleaning done Inverter -4 Row -K,L, & Trackers & Inverter-3 ROW- R,S,T, Total module cleaning 650 & Combiner P.M,
2015-02-24 | 973 | 1017 | 1068 | 1002 | 54.34 | 4114.34 | 3954.75 | 159.59 | 4163 | 5.179 | 78.34 | Module cleaning done Inverter-3 ROW- N,O,P,Q, Total module cleaning 645
2015-02-25 | 1204 | 1306 | 1334 | 1260 | 74.06 | 5178.06 | 4966.5 | 211.56 | 5177 | 6.275 | 8041 | Module cleaning done Inverter-3 &2 ROW- J,K,L,M, Total module cleaning 650
2015-02-26 | 1312 | 1436 | 1431 | 1345 | 85.14 | 5609.14 | 5393.25 | 215.89 | 5605 | 6.926 | 78.87 | Module cleaning done Inverter- 2 & 1 ROW- G,H,I, Total module cleaning 660
2015-02-27 | 1277 | 1352 | 1334 | 1267 | 78.11 | 5308.11 | 5097.75 | 210.36 | 5340 | 6.89 | 75.53 | Module cleaning done Inverter- 1 ROW- A,B,C,D,E,F, Total module cleaning 670
2015-02-28 | 1035 | 1073 | 1074 | 1002 | 56.6 | 4240.6 | 4071.75 | 168.85 | 4267 | 5.59 | 74.39 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 --tive in AJB-102 of The Inverter-4 during The Period of 15:10 To 15:15.WO#(5732232) & Module cleaning done Inverter- 4 ROW- A,B,C,D,E, Total module cleaning 650
2015-03-01 | 639 | 673 | 673 | 667 | 31.64 | 2683.64 | 2541 | 142.64 | 2706 | 3.361 | 78.47 | Grid Failure From - 12:02 to 12:07 (WO#5787456) & Fully Cloudy Day
2015-03-02 | 1153 | 1221 | 1227 | 1206 | 63.95 | 4870.95 | 4676.25 | 194.7 | 4873 | 6.049 | 78.51 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07 --tive in AJB-108 of The Inverter-2 during The Period of 10:05 To 10:10.WO#(5847185)
2015-03-03 | 1046 | 1114 | 1108 | 1092 | 62.6 | 4422.6 | 4241.25 | 181.35 | 4430 | 5.622 | 76.8 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 --tive in AJB-102 of The Inverter-4 during The Period of 15:10 To 15:15.WO#(5914038) & Grid Failure From - 17:20 to 17:32 (WO#5982141)
2015-03-04 | 1277 | 1357 | 1345 | 1375 | 80.68 | 5434.68 | 5217.75 | 216.93 | 5441 | 6.891 | 76.95 | Grid supply failure from 15:10 to 15:15 (WO#6007340) & Module cleaning done Inverter 4 Row ,A,B,C,D,E, Total module cleaning 650
2015-03-05 | 1221 | 1300 | 1283 | 1302 | 74.51 | 5180.51 | 4977.75 | 202.76 | 5231 | 6.734 | 75.71 | Module cleaning done Inverter 4 Row ,F,G,H,I, Total module cleaning 660
2015-03-06 | 1210 | 1284 | 1278 | 1301 | 73.53 | 5146.53 | 4943.25 | 203.28 | 5193 | 6.682 | 75.74 | NO any Issue
2015-03-07 | 1086 | 1153 | 1165 | 1166 | 63.68 | 4633.68 | 4435.5 | 198.18 | 4671 | 6.051 | 75.23 | Module cleaning done Inverter 4 Row ,J,K,L, & Trackers Total module cleaning 660
2015-03-08 | 1221 | 1306 | 1323 | 1340 | 79.43 | 5269.43 | 5061 | 208.43 | 5322 | 6.96 | 74.52 | Grid supply failure from 16:58 to 17:15 (WO#6308762)
2015-03-09 | 1306 | 1396 | 1430 | 1382 | 81.91 | 5595.91 | 5379 | 216.91 | 5603 | 7.172 | 76.14 | Module cleaning done Inverter 3 Row O,P,Q,R,S,T, Total module cleaning 660
2015-03-10 | 1153 | 1250 | 1244 | 1211 | 66.54 | 4924.54 | 4725.75 | 198.79 | 4934 | 6.29 | 76.45 | Grid supply Failure From - 9:45 to 9:47 & 9:59 to 10:11 & 10:48 to 11:00 & 11:33 to 11:36 & 12:22 to 12:25. Module cleaning done Inverter 2 & 3 Row L,M,N, Total module cleaning 670
2015-03-11 | 1137 | 1232 | 1221 | 1184 | 63.96 | 4837.96 | 4653.75 | 184.21 | 4851 | 6.293 | 75.13 | Module cleaning done Inverter 2 Row H,I,J,K, Total module cleaning 665
2015-03-12 | 1017 | 1080 | 1063 | 1011 | 50.99 | 4221.99 | 4044 | 177.99 | 4236 | 5.623 | 73.42 | Module cleaning done Inverter -1 Row D,E,F,G, Total module cleaning 650
2015-03-13 | 933 | 984 | 978 | 962 | 45.58 | 3902.58 | 3732.75 | 169.83 | 3945 | 5.085 | 75.61 | Module cleaning done Inverter 1 & 4 Row A,B,C,& A,B,C, Total module cleaning 665
2015-03-14 | 984 | 1034 | 1034 | 988 | 48.18 | 4088.18 | 3912.75 | 175.43 | 4124 | 5.318 | 75.58 | Grid supply failure from 13:40 to 13:47 (WO#6689811) & Module cleaning done Inverter- 4 Row -D,E,F,G, Total module cleaning 660
2015-03-15 | 1221 | 1300 | 1295 | 1157 | 65.12 | 5038.12 | 4847.25 | 190.87 | 5084 | 6.704 | 73.91 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 --tive in AJB-105 of The Inverter-4 during The Period of 16:10 To 16:15.WO#(6754787)
2015-03-16 | 1351 | 1448 | 1441 | 1412 | 77.5 | 5729.5 | 5504.25 | 225.25 | 5727 | 7.375 | 75.68 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 --tive in AJB-105 of The Inverter-4 during The Period of 10:15 To 10:20.WO#(6812097) | 6812097
2015-03-17 | 1345 | 1436 | 1431 | 1441 | 78.4 | 5731.4 | 5505.75 | 225.65 | 5760 | 7.287 | 77.04 | NO any Issue
2015-03-18 | 1380 | 1475 | 1475 | 1474 | 80.42 | 5884.42 | 5661 | 223.42 | 5918 | 7.515 | 76.75 | Module cleaning done Inverter-3 Row P,Q,R,S,T, Total module cleaning 630 |  | 630
2015-03-19 | 1323 | 1425 | 1419 | 1408 | 77.55 | 5652.55 | 5451 | 201.55 | 5701 | 7.45 | 75.58 | Module cleaning done Inverter-3 & 2 Row L,M,N,O, Total module cleaning 650 |  | 650
2015-03-20 | 1289 | 1391 | 1369 | 1382 | 73.98 | 5504.98 | 5292 | 212.98 | 5538 | 7.291 | 74.03 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-101 of The Inverter-4 during The Period of 12:20 To 12:25.WO#(7104864) & Grid supply failure from 8:07 to 8:13 (WO#7098699) & Module cleaning done Inverter- 4 Row -H,I,J,K, Total module cleaning- 650 | 7098699 7104864 | 650
2015-03-21 | 1130 | 1198 | 1159 | 1213 | 56.1 | 4756.1 | 4575 | 181.1 | 4801 | 7.105 | 65.85 | Grid failure from - early morning to 9:26. Module cleaning done Inverter-1 Row D,E,F,G,Total module cleaning 650 | 7165762 | 650
2015-03-22 | 1222 | 1295 | 1272 | 1303 | 61.11 | 5153.11 | 4953 | 200.11 | 5186 | 6.875 | 73.52 | NO any Issue
2015-03-23 | 1238 | 1317 | 1294 | 1292 | 62.83 | 5203.83 | 5006.25 | 197.58 | 5242 | 7.116 | 71.79 | Module cleaning done Inverter-1 & 4 Row A,B,C,& A,B,C, Total module cleaning 640 & Inverter No-4 AJB No- 104 MCB Trip 12:40 to 14:02 WO#7318204 | 7318204 | 640
2015-03-24 | 1255 | 1334 | 1317 | 1396 | 64.21 | 5366.21 | 5168.25 | 197.96 | 5385 | 7.155 | 73.35 | Module cleaning done Inverter-4 Row D,E,F,G, Total module cleaning 660 |  | 660
2015-03-25 | 1164 | 1227 | 1233 | 1288 | 58.06 | 4970.06 | 4787.25 | 182.81 | 5014 | 6.696 | 72.98 | Module cleaning done Inverter-4 Row H,I,J,K,L, & Tracker Total module cleaning 720 |  | 720
2015-03-26 | 978 | 1035 | 1074 | 1062 | 44.13 | 4193.13 | 4023.75 | 169.38 | 4217 | 5.582 | 73.63 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 --tive in AJB-116 of The Inverter-3 during The Period of 10:35 To 10:40.WO#(7506678) & Module cleaning done Inverter- 3 ROW- ,P,Q,R,S,T, Total module cleaning 630 | 7506678 | 630
2015-03-27 | 990 | 1079 | 1091 | 1058 | 47.59 | 4265.59 | 4097.25 | 168.34 | 4291 | 5.613 | 74.51 | Module cleaning done Inverter-3 & 2 Row L,M,N,O, & Total module cleaning 660 |  | 660
2015-03-28 | 1108 | 1199 | 1199 | 1182 | 53.72 | 4741.72 | 4569.75 | 171.97 | 4756 | 6.255 | 74.1 | Module cleaning done Inverter-1 & 2 Row ,H,I,J,K, & Total module cleaning 670 |  | 670
2015-03-29 | 599 | 627 | 627 | 599 | 22.46 | 2474.46 | 2353.5 | 120.96 | 2512 | 3.007 | 81.42 | Grid supply failure from 16:51 to 18:02 (WO#7717067) | 7717067
2015-03-30 | 1323 | 1369 | 1402 | 1411 | 60.95 | 5565.95 | 5362.5 | 203.45 | 5613 | 7.373 | 74.19 | Module cleaning done Inverter-1 Row ,A,B,C,D,E,F,G, & Total module cleaning 685 |  | 685
2015-03-31 | 1306 | 1373 | 1374 | 1411 | 60.49 | 5524.49 | 5325.75 | 198.74 | 5536 | 7.335 | 73.56 | Module cleaning done Inverter-4 Row ,A,B,C,D,E, & Total module cleaning 630 & Today I Replaced The D.C.12Amp Fuse Link of The String- 01 --tive in AJB-106 of The Inverter-2 during The Period of 10:35 To 10:40.WO#(7849439) & Replace the silica gel | 7849439 | 630
2015-04-01 | 1232 | 1295 | 1294 | 1337 | 57.1 | 5215.1 | 5001.75 | 213.35 |  |  |  | Module cleaning done Inverter-4 Row ,F,G,H,I, & Total module cleaning 650 |  | 650
2015-04-02 | 1187 | 1249 | 1250 | 1324 | 53.11 | 5063.11 | 4883.25 | 179.86 |  |  |  | Module cleaning done Inverter-4 Row ,J,K,L, & Trackers Total module cleaning 610 |  | 610
2015-04-03 | 1278 | 1346 | 1391 | 1433 | 61.73 | 5509.73 | 5315.25 | 194.48 | 5558 | 7.148 | 75.78 | Module cleaning done Inverter-3 Row P,Q,R,S,T & Total module cleaning 630 |  | 630
2015-04-04 | 848 | 882 | 938 | 893 | 37.29 | 3598.29 | 3458.25 | 140.04 | 3628 | 4.589 | 77.05 | Module cleaning done Inverter-2 & 3 Row L,M,N,O & Total module cleaning 660. & Grid supply failure from 18:12 to 18:30 (WO#8175587) & couldy day | 817587 | 660
2015-04-05 | 978 | 1034 | 1091 | 1049 | 48.29 | 4200.29 | 4029.75 | 170.54 | 4237 | 5.48 | 75.35 | Grid supply failure from - 9:06 to 9:12 & couldy day
2015-04-06 | 1023 | 1109 | 1137 | 1103 | 54.15 | 4426.15 | 4233 | 193.15 | 4434 | 5.7 | 75.81 | Module cleaning done Inverter-2 Row ,H,I,J,K,& Total module cleaning 670. & Grid supply failure from 10:02 to 10:22 (WO#8286657) | 8286657 | 670
2015-04-07 | 1075 | 1187 | 1175 | 1170 | 58.04 | 4665.04 | 4501.5 | 163.54 | 4705 |  |  | Module cleaning done Inverter-2 &1 Row E,F,G, & Total module cleaning 620 |  | 620
2015-04-08 | 1063 | 1142 | 1125 | 1108 | 54.36 | 4492.36 | 4311 | 181.36 | 4515 |  |  | Module cleaning done Inverter-1 Row ,A,B,C,D & Total module cleaning 590 |  | 590
2015-04-09 | 1209 | 1266 | 1256 | 1257 | 66.75 | 5054.75 | 4861.5 | 193.25 | 5229 |  |  | NO any Issue
2015-04-10 | 1074 | 1108 | 1102 | 1107 | 54.42 | 4445.42 | 4276.5 | 168.92 | 4602 |  |  | Module cleaning done Inverter-4 Row ,A,B,C,D, & Total module cleaning 580 |  | 580
2015-04-11 | 1001 | 1063 | 1063 | 1105 | 51.39 | 4283.39 | 4117.5 | 165.89 | 4374 | 5.664 | 75.26 | Module cleaning done Inverter-4 Row ,E,F,G,H, & Total module cleaning 650 & Rain |  | 650
2015-04-12 | 990 | 1069 | 1085 | 1078 | 81.28 | 4303.28 | 4032 | 271.28 | 4269 | 5.527 | 75.28 | Grid supply failure From 9:45 to 9:49 & 16:03 to 16:09 (WO#8750195) (WO#8816841) | 8750195 8816841
2015-04-13 | 1175 | 1283 | 1306 | 1332 | 66.44 | 5162.44 | 4997.25 | 165.19 | 5151 | 6.605 | 76.01 | NO any Issue
2015-04-14 | 1199 | 1328 | 1351 | 1387 | 70.66 | 5335.66 | 5152.5 | 183.16 | 5387 | 6.933 | 75.73 | NO any Issue
2015-04-15 | 1199 | 1329 | 1346 | 1368 | 72.83 | 5314.83 | 5128.5 | 186.33 | 5358 | 6.899 | 75.69 | L.T PANEL P.M
2015-04-16 | 1170 | 1295 | 1311 | 1355 | 72.03 | 5203.03 | 5014.5 | 188.53 | 5250 | 6.898 | 74.18 | Module cleaning done Inverter-4 Row ,A,B,C,D,E,& Total module cleaning 630. & Grid supply failure from 13:17 to 13:24 (WO#9086294) | 9086294 | 630
2015-04-17 | 1130 | 1254 | 1278 | 1321 | 67.26 | 5050.26 | 4869.7 | 180.56 | 5085 | 6.719 | 73.76 | Module cleaning done Inverter-4 Row ,F,G,H,I, & Total module cleaning 650 |  | 650
2015-04-18 | 1148 | 1272 | 1290 | 1356 | 63.62 | 5129.62 | 4934.25 | 195.37 | 5182 | 6.814 | 74.12 | Module cleaning done Inverter-4 Row ,J,K,L, & Total module cleaning 660 |  | 660
2015-04-19 | 1159 | 1289 | 1328 | 1375 | 68.45 | 5219.45 | 5011.5 | 207.95 | 5217 | 6.911 | 73.57 | NO any Issue
2015-04-20 | 1204 | 1306 | 1368 | 1385 | 69.55 | 5332.55 | 5134.5 | 198.05 | 5340 | 6.908 | 75.34 | Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 09++tive in AJB-104 of The Inverter-1 & 09--tive AJB-105 during The Period of 10:15 To 10:25.WO#(9402652) & Module cleaning done Inverter-3 Row ,P,Q,R,S,T, & Total module cleaning 620 | 9402652 | 620
2015-04-21 | 1125 | 1222 | 1260 | 1262 | 61.65 | 4930.65 | 4764.75 | 165.9 | 4981 | 6.461 | 75.13 | Module cleaning done Inverter-3 &2 Row ,L,M,N,O, & Total module cleaning 690 |  | 690
2015-04-22 | 1199 | 1323 | 1340 | 1350 | 67.97 | 5279.97 | 5074.5 | 205.47 | 5287 | 6.804 | 75.73 | Module cleaning done Inverter-2 Row ,H,I,J,K, & Total module cleaning 710 |  | 710
2015-04-23 | 1255 | 1362 | 1374 | 1388 | 72.53 | 5451.53 | 5249.25 | 202.28 | 5457 | 7.071 | 75.21 | Module cleaning done Inverter-2 & 1 Row ,D,E,F,G, & Total module cleaning 680 |  | 680
2015-04-24 | 1243 | 1311 | 1329 | 1354 | 69.73 | 5306.73 | 5115 | 191.73 | 5318 | 6.809 | 76.12 | Module cleaning done Inverter-1 & 4 Row ,A,B,C, & ,A,B,C, & Total module cleaning 650 |  | 650
2015-04-25 | 1216 | 1278 | 1289 | 1325 | 64.76 | 5172.76 | 4985.25 | 187.51 | 5186 | 6.684 | 75.62 | Module cleaning done Inverter-4 Row-,D,E,F,G, & Total module cleaning 650 |  | 650
2015-04-26 | 1182 | 1250 | 1260 | 1305 | 64.53 | 5061.53 | 4879.5 | 182.03 | 5079 | 6.625 | 74.72 | NO any Issue
2015-04-27 | 1192 | 1249 | 1261 | 1329 | 66.38 | 5097.38 | 4912.5 | 184.88 | 5145 | 6.705 | 74.78 | Module cleaning done Inverter-4 Row-,H,I,J,K, & Total module cleaning 660 |  | 660
2015-04-28 | 1199 | 1266 | 1272 | 1359 | 65.69 | 5161.69 | 4972.5 | 189.19 | 5177 | 6.695 | 75.36 | Module cleaning done Inverter-4 & 3 Row-,L, -R,S,T,& Tracker & Total module cleaning 620 & Control Building P.M & Inverter P.M (1&2) |  | 620
2015-04-29 | 1164 | 1233 | 1267 | 1315 | 66.15 | 5045.15 | 4860 | 185.15 |  |  |  | Module cleaning done Inverter-3 Row- N,O,P,Q, & Total module cleaning 630 & C.R Panel P.M & Inverter P.M (3&4) & Internet Failure (POE POWER ADAPTER FAILURE)14:45 |  | 630
2015-04-30 | 1182 | 1249 | 1334 | 1345 | 69.77 | 5179.77 | 4989.75 | 190.02 |  |  |  | Module cleaning done Inverter-3 & 2 Row- J,K,L,M & Total module cleaning 680 |  | 680
2015-05-01 | 1098 | 1188 | 1233 | 1236 | 61.55 | 4816.55 | 4656.75 | 159.8 |  |  |  | Grid supply failure from 14:59 to 15:15
2015-05-02 | 1124 | 1243 | 1271 | 1251 | 64.5 | 4953.5 | 4764 | 189.5 |  |  |  | NO any Issue
2015-05-03 | 1165 | 1283 | 1317 | 1316 | 70.08 | 5151.08 | 4948.5 | 202.58 |  |  |  | NO any Issue
2015-05-04 | 1204 | 1346 | 1346 | 1345 | 71.88 | 5312.88 | 5091 | 221.88 |  |  |  | Module cleaning done Inverter-1 & 2 Row- G,H,I, & Total module cleaning 650 |  | 650
2015-05-05 | 1215 | 1295 | 1295 | 1298 | 70.55 | 5173.55 | 4989 | 184.55 |  |  |  | Module cleaning done Inverter-1 Row- ,C,D,E,F, & Total module cleaning 660 |  | 660
2015-05-06 | 1216 | 1283 | 1277 | 1305 | 68.76 | 5149.76 | 4954.5 | 195.26 |  |  |  | Module cleaning done Inverter-1 & 4 Row- ,A,B &,A,B,C,D, & Total module cleaning 670 |  | 670
2015-05-07 | 1215 | 1278 | 1278 | 1344 | 67.67 | 5182.67 | 4985.25 | 197.42 |  |  |  | Module cleaning done Inverter-4 Row- ,E,F,G,H, & Total module cleaning 690 |  | 690
2015-05-08 | 1046 | 1091 | 1091 | 1154 | 51.67 | 4433.67 | 4260 | 173.67 |  |  |  | Module cleaning done Inverter-4 Row- ,I,J,K,L, & Total module cleaning 670 |  | 670
2015-05-09 | 1204 | 1266 | 1300 | 1379 | 71.97 | 5220.97 | 5037.75 | 183.22 |  |  |  | Module cleaning done Inverter-3 & Trackers Row- ,Q,R,S,T, & Total module cleaning 630 |  | 630
2015-05-10 | 1193 | 1255 | 1295 | 1364 | 71.89 | 5178.89 | 4984.5 | 194.39 |  |  |  | NO any Issue
2015-05-11 | 1148 | 1210 | 1273 | 1327 | 68.18 | 5026.18 | 4839 | 187.18 |  |  |  | Module cleaning done Inverter-3 & Row- ,M,N,O,P, & Total module cleaning 650 |  | 650
2015-05-12 | 1130 | 1198 | 1085 | 1297 | 65.11 | 4775.11 | 4600.5 | 174.61 |  |  |  | Inverter#3 did not wake up due to auto reset indication so reset it at 9:35am and started the inverter. & Module cleaning done Inverter-3 & 2 Row- ,J,K,L, & Total module cleaning 680 | WO#11388926 | 680
2015-05-13 | 877 | 973 | 984 | 998 | 48.71 | 3880.71 | 3741 | 139.71 |  |  |  | 5 KV UPS System D.C, Volt Low so Bypass the system plant Trip 15:15 to 16:10 WO# & Module cleaning done Inverter-2 & Row- ,G,H,I, & Total module cleaning 650 & Cloud and Rain |  | 650
2015-05-14 | 785 | 831 | 848 | 858 | 42.33 | 3364.33 | 3271.5 | 92.83 |  |  |  | Night time 11KV Grid Failure so our plant VCB Trip plant started 9:05 & Two Time Grid Failure From-10:58 to 11:21 & 14:25 to 14:35 & Module cleaning done Inverter-1 Row- ,D,E,F, & Total module cleaning 640 & Cloud and Rain |  | 640
2015-05-15 | 1171 | 1249 | 1272 | 1100 | 70.46 | 4862.46 | 4687.5 | 174.96 |  |  |  | Grid Failure From -11:09 to 11:16 WO# & Module cleaning done Inverter-1 Row- ,A,B,C, & Total module cleaning 350 |  | 350
2015-05-16 | 1232 | 1301 | 1334 | 1340 | 69.15 | 5276.15 | 5082.75 | 193.4 |  |  |  | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-104 of The Inverter-4 during The Period of 19:35 To 9:40.WO#() & Module cleaning done Inverter- 4 ROW- ,A,B,C,D,E, Total module cleaning 600 |  | 600
2015-05-17 | 1232 | 1317 | 1340 | 1395 | 69.86 | 5353.86 | 5155.5 | 198.36 |  |  |  | Array P.M
2015-05-18 | 1205 | 1283 | 1301 | 1377 | 71.37 | 5237.37 | 5038.5 | 198.87 |  |  |  | Module cleaning done Inverter-4 Row- ,F,G,H, & Total module cleaning 600 |  | 600
2015-05-19 | 1187 | 1295 | 1300 | 1382 | 69.57 | 5233.57 | 5041.5 | 192.07 |  |  |  | Module cleaning done Inverter-4 Row- ,I,J,K,L, & Total module cleaning 670 & Grid Failure From -16:15 to 16:23 WO# & Combiner P.M (AJB-100 to 117 -Crystallin side 750 KW ) |  | 670
2015-05-20 | 1204 | 1306 | 1306 | 1405 | 73.69 | 5294.69 | 5099.25 | 195.44 |  |  |  | Module cleaning done Inverter-3 & Trackers Row- ,P,Q,R,S,T, & Total module cleaning 650 & Combiner P.M (AJB-100 to 105 -Thinfilm side 250 KW ) |  | 650
2015-05-21 | 1154 | 1261 | 1300 | 1347 | 70.45 | 5132.45 | 4947 | 185.45 | 5149 |  |  | Module cleaning done Inverter-3 & 2 Row- ,L,M,N,O, & Total module cleaning 680 & Seeds P.M |  | 690
2015-05-22 | 1170 | 1305 | 1317 | 1356 | 72.4 | 5220.4 | 5025.75 | 194.65 | 5282 |  |  | Module cleaning done Inverter- 2 Row- ,I,J,K, & Total module cleaning 710 |  | 710
2015-05-23 | 1136 | 1284 | 1272 | 1302 | 68.58 | 5062.58 | 4887 | 175.58 | 5086 | 6.521 | 76.01 | Module cleaning done Inverter-2 & 1 Row- ,F,G,H, & Total module cleaning 650 & Grid Failure From -08:07 to 08:15 WO#12532233 | 12532233 | 650
2015-05-24 | 1125 | 1249 | 1238 | 1275 | 64 | 4951 | 4769.25 | 181.75 | 4992 | 6.427 | 75.7 | NO any Issue
2015-05-25 | 1103 | 1210 | 1199 | 1242 | 56.27 | 4810.27 | 4664.5 | 145.77 | 4840 | 6.495 | 72.63 | Module cleaning done Inverter- 1 Row- C,D,E, & Total module cleaning 600 & Grid Failure From -07:20 to 08:05 WO#12736715 | 12736715 | 600
2015-05-26 | 1136 | 1221 | 1215 | 1256 | 57.6 | 4885.6 | 4695 | 190.6 | 4915 | 6.432 | 74.47 | Module cleaning done Inverter- 1 & 4 Row- ,A,B, & A,B,C,D, & Total module cleaning- 610 |  | 610
2015-05-27 | 1125 | 1210 | 1204 | 1273 | 56.94 | 4868.94 | 4692 | 176.94 | 4892 | 6.428 | 74.17 | Module cleaning done Inverter- 4 Row- ,E,F,G, & Total module cleaning- 560 |  | 560
2015-05-28 | 1119 | 1210 | 1205 | 1297 | 57.01 | 4888.01 | 4706.25 | 181.76 | 4906 | 6.458 | 74.04 | Module cleaning done Inverter- 4 Row- ,H,I,J, & Total module cleaning- 596 |  | 596
2015-05-29 | 1142 | 1238 | 1238 | 1340 | 64.66 | 5022.66 | 4850.25 | 172.41 | 5075 | 6.649 | 74.39 | Module cleaning done Inverter- 4 & 3 & Trackers Row- ,K,L,& R,S,T, & Total module cleaning 660 & Grid Failure From -12:52 to 12:57 WO#13149762 & Tracker P.M | 13149762 | 660
2015-05-30 | 1148 | 1238 | 1278 | 1336 | 67.14 | 5067.14 | 4875.75 | 191.39 | 5088 | 6.727 | 73.71 | Module cleaning done Inverter- 3 Row- ,N,O,P,Q, & Total module cleaning- 660 |  | 660
2015-05-31 | 1108 | 1193 | 1243 | 1284 | 50.45 | 4878.45 | 4718.25 | 160.2 | 4903 | 6.76 | 70.69 | Grid failure from night time so our plant side V.C.B. trip Morning 8:00a.m on V.C.B. plant started 8:00a.m.WO#13316368 | 13316368 | 610
2015-06-01 | 1108 | 1198 | 1255 | 1285 | 58.15 | 4904.15 | 4728.75 | 175.4 | 4951 | 6.549 | 73.68 | Module cleaning done Inverter- 2 Row- ,H,I,J, & Total module cleaning- 670 |  | 670
2015-06-02 | 1006 | 1120 | 1136 | 1145 | 52.89 | 4459.89 | 4286.25 | 173.64 | 4499 | 4.53 | 96.79 | Module cleaning done Inverter- 2 Row- ,H,I,J, & Total module cleaning- 670 |  | 670
2015-06-03 | 961 | 1051 | 1046 | 1088 | 26.49 | 4172.49 | 4040.25 | 132.24 | 4243 | 5.546 | 74.56 | Module cleaning done Inverter- 1 Row- E,F,G, & Total module cleaning 580 & Grid Failure From -12:55 to 13:05 WO# & Trackers 4 S.Q. m.m. 4 core cable B Phase Ground folt (Tracker Inverter no-3 S.M.A. power supply failure) | 14331961 13587960 | 580
2015-06-04 | 950 | 1012 | 1007 | 1013 | 19.57 | 4001.57 | 3864.75 | 136.82 | 4064 | 5.63 | 70.35 | Module cleaning done Inverter- 1 Row- A,B,C,D, 550 & Total module cleaning 550 & Grid Failure From -08:20 to 08:45 WO#13640469 | 13640469 | 550
2015-06-05 | 1069 | 1119 | 1108 | 1129 | 22.58 | 4447.58 | 4283.25 | 164.33 | 4488 | 6.185 | 70.72 | Module cleaning done Inverter- 4 Row- ,A,B,C,D,E, & Total module cleaning- 630 |  | 630
2015-06-06 | 1130 | 1193 | 1187 | 1253 | 22.95 | 4785.95 | 4619.25 | 166.7 | 4831 | 6.494 | 72.5 | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning- 594 |  | 594
2015-06-07 | 1057 | 1131 | 1125 | 1206 | 22.27 | 4541.27 | 4377.75 | 163.52 | 4596 | 6.273 | 71.4 | Grid Failure From -17:48 to 17:55 WO# & Inverter no-1 ABB, From- 17:55 inverter not started (sleep mode)
2015-06-08 | 374 | 402 | 401 | 412 | 6.37 | 1595.37 | 1486.5 | 108.87 | 1626 | 2.083 | 76.08 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Total module cleaning- 650 |  | 650
2015-06-09 | 808 | 865 | 871 | 945 | 17.2 | 3506.2 | 3370.5 | 135.7 | 3559 | 4.714 | 73.58 | Module cleaning done Inverter- 3 Row- ,P,Q,R,S,T, & Total module cleaning- 630 |  | 630
2015-06-10 | 475 | 695 | 729 | 821 | 17.96 | 2737.96 | 2676.75 | 61.21 | 2853 | 4.949 | 56.18 | Today Eight time Grid failure-8:00 to 8:50 , 12:32 to 12:42, 14:50 to 14:55, 15:20 to 15:26 , 15:50 to 15:55, 16:46 to 16:50, 17:15 to 17:19, 17:31 to 17:59 & Inverter no-1,2,3, Emergency stop reset Inverter started 9:10 & Inverter no-1 Grid folt Err code NONFOLT(8189 A.C. VOLT LOW) 15:20 TO 16:20 | WO#14227355 WO#14238706
2015-06-11 | 729 | 786 | 809 | 833 | 14.4 | 3171.4 | 3025.5 | 145.9 | 3219 | 4.037 | 77.71 | Module cleaning done Inverter- 3 Row- ,L,M,N,O, 670 & Total module cleaning 670 & Grid Failure From -12:58 to 13:06 WO# |  | 670
2015-06-12 | 1041 | 1136 | 1130 | 1200 | 21.1 | 4528.1 | 4404 | 124.1 | 4559 | 5.874 | 75.64 | NO any Issue
2015-06-13 | 1023 | 1114 | 1120 | 1174 | 21.32 | 4452.32 | 4363.5 | 88.82 | 4504 | 5.711 | 76.86 | NO any Issue
2015-06-14 | 1012 | 1096 | 1085 | 1163 | 21.18 | 4377.18 | 4134.75 | 242.43 | 4411 | 5.692 | 75.53 | NO any Issue
2015-06-15 | 944 | 1035 | 1023 | 1084 | 21.1 | 4107.1 | 3939 | 168.1 | 4160 | 5.492 | 73.82 | Module cleaning done Inverter- 3 Row- ,P,Q,R,S,T, & Total module cleaning 650 & Grid Failure From -12:01 to 12:07 WO# |  | 650
2015-06-16 | 927 | 1001 | 984 | 1054 | 21.08 | 3987.08 | 3840 | 147.08 | 4037 | 5.227 | 75.27 | Module cleaning done Inverter- 3 Row- ,L,M,N,O, & Total module cleaning- 670 |  | 670
2015-06-17 | 851 | 904 | 894 | 942 | 18.64 | 3609.64 | 3479.25 | 130.39 | 3671 | 4.908 | 72.9 | Module cleaning done Inverter- 1 & 2 Row- ,G,H,I,J,K, & Total module cleaning 900 & Grid Failure From -07:40 to 08:00 & 10:24 to 10:39 WO# | 14626095 | 900
2015-06-18 | 924 | 984 | 972 | 1020 | 19.95 | 3919.95 | 3787.5 | 132.45 | 3972 | 5.165 | 74.95 | Module cleaning done Inverter- 1 Row- ,A,B,C,D,E, & Total module cleaning 950 & Grid Failure From -12:10 to 12:15 WO#14683274 | 14683274 | 950
2015-06-19 | 718 | 757 | 757 | 775 | 14.53 | 3021.53 | 2890.5 | 131.03 | 3071 | 3.884 | 77.06 | Module cleaning done Inverter- 4 Row- ,A,B,C,D,E, & Total module cleaning- 630 |  | 630
2015-06-20 | 1007 | 1080 | 1069 | 1161 | 21.7 | 4338.7 | 4174.5 | 164.2 | 4370 | 5.65 | 75.38 | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning- 594 |  | 564
2015-06-21 | 955 | 1025 | 1018 | 1119 | 15.77 | 4132.77 | 3978 | 154.77 | 4186 | 5.453 | 74.81 | NO any Issue
2015-06-22 | 661 | 700 | 712 | 749 | 14.09 | 2836.09 | 2725.5 | 110.59 | 2887 | 3.588 | 78.42 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Trackers & Total module cleaning 750 & Grid Failure From -08:13 to 08:22 WO#14882219 & cloudy day | 14882219 | 750
2015-06-23 | 515 | 554 | 565 | 555 | 10.24 | 2199.24 | 2083.5 | 115.74 | 2239 | 2.71 | 80.52 | Module cleaning done Inverter- 3 Row- ,P,Q,R,S,T, & Total module cleaning- 650 & cloudy day |  | 650
2015-06-24 | 186 | 203 | 198 | 197 | 3.44 | 787.44 | 699 | 88.44 | 842 | 998 | 82.23 | Grid Failure From- 15:08 to 16:05 Inverters note started sleep mode because D.C.Valltege low heavy rain & Grid Failure From- 17:13 to 17:39 | 14998049 14997953
2015-06-25 | 865 | 939 | 944 | 952 | 19.67 | 3719.67 | 3575.25 | 144.42 | 3792 | 4.759 | 77.66 | Grid Failure From- 14:22 to 14:30 WO#15038762 | 15038762
2015-06-26 | 973 | 1051 | 1052 | 1077 | 20.81 | 4173.81 | 4017.75 | 156.06 | 4212 | 5.35 | 76.73 | Grid Failure From- 07:54 to 8:02 WO#1508660 | 15086600
2015-06-27 | 938 | 1006 | 1006 | 1035 | 20.5 | 4005.5 | 3858 | 147.5 | 4057 | 5.192 | 76.15 | Grid Failure From- 15:00 to 15:20 WO#15158620 | 15158620
2015-06-28 | 1103 | 1199 | 1198 | 1258 | 24.12 | 4782.12 | 4599.75 | 182.37 | 4823 | 6.312 | 74.47 | NO any Issue
2015-06-29 | 814 | 876 | 877 | 896 | 17.64 | 3480.64 | 3330.75 | 149.89 | 3514 | 4.414 | 77.59 | Module cleaning done Inverter- 4 Row- ,A,B,C,D,E, & Total module cleaning- 630 |  | 630
2015-06-30 | 966 | 1040 | 1040 | 1099 | 21.64 | 4166.64 | 4026 | 140.64 | 4225 | 5.515 | 74.66 | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning 594 & Grid Failure From -13:13 to 13:20 WO#15323914 | 15323914 | 594
2015-07-01 | 944 | 1024 | 1029 | 1090 | 21.21 | 4108.21 | 3948.75 | 159.46 | 4146 | 5.407 | 74.73 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Total module cleaning- 690 |  | 690
2015-07-02 | 996 | 1068 | 1074 | 1157 | 22.39 | 4317.39 | 4153.5 | 163.89 | 4353 | 5.674 | 74.77 | Module cleaning done Inverter- 3 & Trackers Row- ,P,Q,R,S,T, & Total module cleaning- 710 |  | 710
2015-07-03 | 938 | 1018 | 1046 | 1074 | 21.58 | 4097.58 | 3944.25 | 153.33 | 4142 | 5.458 | 73.96 | Module cleaning done Inverter- 3 Row- ,L,M,N,O, & Total module cleaning 670 & Grid Failure From -11:36 to 11:42 WO#15472920 | 15472920 | 670
2015-07-04 | 950 | 1057 | 1091 | 1068 | 21.33 | 4187.33 | 4037.25 | 150.08 | 4235 | 5.562 | 74.21 | Module cleaning done Inverter- 2 Row- ,I,J,K, & Total module cleaning 710 & Grid Failure From -18:50 to 18:02 WO#15545727 | 15545727 | 710
2015-07-05 | 802 | 882 | 899 | 904 | 18.17 | 3505.17 | 3358.5 | 146.67 | 3549 | 4.575 | 75.6 | NO any Issue
2015-07-06 | 741 | 831 | 831 | 827 | 17.18 | 3247.18 | 3116.25 | 130.93 | 3294 | 4.168 | 77.02 | Module cleaning done inverter -1 Row- G,H & Total module cleaning 504 & Cloudy day |  | 504
2015-07-07 | 622 | 690 | 684 | 669 | 14.34 | 2679.34 | 2564.25 | 115.09 | 2730 | 3.522 | 75.54 | Module cleaning done Inverter- 1 Row- ,D,E,F, & Total module cleaning 462 & Grid Failure From -11:36 to 11:46 & 15:01 to 15:40 WO# | 15702683 15713587 | 462
2015-07-08 | 616 | 656 | 656 | 657 | 11.97 | 2596.97 | 2469.75 | 127.22 | 2639 | 3.24 | 79.38 | Module cleaning done inverter -1 Row- A,B,C, & Total module cleaning 540
2015-07-09 | 747 | 797 | 797 | 810 | 15.66 | 3166.66 | 3026.25 | 140.41 | 3212 | 3.991 | 78.44 | Module cleaning done inverter -4 Row- A,B,C,D,E, & Total module cleaning 630 |  | 630
2015-07-10 | 757 | 814 | 814 | 832 | 17.38 | 3234.38 | 3093.75 | 140.63 | 3283 | 4.14 | 77.28 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning 594 |  | 594
2015-07-11 | 826 | 893 | 888 | 920 | 18.82 | 3545.82 | 3403.5 | 142.32 | 3605 | 4.584 | 76.65 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Total module cleaning- 690 & Grid Failure From -18:03 to 18:09 WO# | 16007430 | 690
2015-07-12 | 915 | 989 | 995 | 1022 | 20.65 | 3941.65 | 3792 | 149.65 | 3983 | 5.459 | 71.11 | NO any Issue
2015-07-13 | 1024 | 1108 | 1108 | 1159 | 22.66 | 4421.66 | 4252.5 | 169.16 | 4460 | 5.799 | 74.96 | NO any Issue
2015-07-14 | 1023 | 1109 | 1119 | 1166 | 22.27 | 4439.27 | 4280.25 | 159.02 | 4486 | 5.863 | 74.57 | Module cleaning done Inverter- 3 & Trackers Row- ,Q,R,S,T, & Total module cleaning- 354 & Grid Failure From -16:57 to 17:03 WO# | 16151488 | 354
2015-07-15 | 893 | 961 | 989 | 1012 | 19.12 | 3874.12 | 3726.75 | 147.37 | 3928 | 5.116 | 74.83 | Module cleaning done Inverter- 3 Row- ,N,O,P,, & Total module cleaning- 546 & Grid Failure From -17:58 to 18:04 WO# | 16208984 | 546
2015-07-16 | 916 | 995 | 1012 | 1021 | 20.44 | 3964.44 | 3783 | 181.44 | 4002 | 5.148 | 75.76 | Module cleaning done inverter -2 & 3 Row- ,L,M, & Total module cleaning 504 |  | 504
2015-07-17 | 803 | 887 | 899 | 896 | 18.67 | 3503.67 | 3389.25 | 114.42 | 3551 | 4.481 | 77.23 | Module cleaning done inverter -2 Row- ,J,K, & Total module cleaning 570 |  | 570
2015-07-18 | 819 | 922 | 905 | 917 | 19 | 3582 | 3433.5 | 148.5 | 3621 | 4.652 | 75.86 | Inverter-2 AJB -106 String -7 MC4 connector bourned so replace connector and string started WO#() & Module cleaning done inverter -2 & 1 Row- ,I,J, & Total module cleaning 504 |  | 504
2015-07-19 | 464 | 497 | 492 | 492 | 9.42 | 1954.42 | 1845.75 | 108.67 | 1995 | 2.332 | 83.38
2015-07-20 | 452 | 486 | 492 | 490 | 8.89 | 1928.89 | 1797 | 131.89 |  |  |  | Internet failure & Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning 489 |  | 489
2015-07-21 | 328 | 345 | 356 | 356 | 6.54 | 1391.54 | 1339.5 | 52.04 |  |  |  | Grid Failure From-11:40 to 14:08 WO#
2015-07-22 | 458 | 486 | 492 | 494 | 9.53 | 1939.53 | 1818 | 121.53
2015-07-23 | 825 | 899 | 910 | 913 | 18.76 | 3565.76 | 3411 | 154.76 |  |  |  | 11K.V side (G.O.D. Swich) R, phase sparking so maintains R, phase sutdown plant-10:03 to 10:20 WO#
2015-07-24 | 634 | 679 | 684 | 691 | 14.48 | 2702.48 | 2586 | 116.48 |  |  |  | Grid Failure From-15:45 to 16:33 WO#
2015-07-25 | 390 | 424 | 418 | 418 | 7.9 | 1657.9 | 1543.5 | 114.4
2015-07-26 | 164 | 175 | 175 | 172 | 2.81 | 688.81 | 610.5 | 78.31
2015-07-27 | 152 | 164 | 170 | 159 | 2.53 | 647.53 | 551.25 | 96.28
2015-07-28 | [5 empty] | 0 |  | 0 |  |  |  | Grid Failure From-28-7-2015-08:58 to 30-7-2015 -14:43 WO#16824672 | 16824672
2015-07-29 | [5 empty] | 0 |  | 0 |  |  |  | Grid Failure From-28-7-2015-08:58 to 30-7-2015 -14:43 WO#16824672 | 16824672
2015-07-30 | 204 | 220 | 226 | 218 | 4.2 | 872.2 | 782.25 | 89.95 |  |  |  | Grid Failure From-28-7-2015-08:58 to 30-7-2015 -14:43 WO#16824672 | 16824672
2015-07-31 | 690 | 758 | 758 | 769 | 15.74 | 2990.74 | 2845.5 | 145.24 |  |  |  | Grid Failure From-08:42 to 10:30 WO#
2015-08-01 | 605 | 656 | 661 | 665 | 13.16 | 2600.16 | 2491.5 | 108.66
2015-08-02 | 706 | 769 | 764 | 763 | 15.03 | 3017.03 | 2865.75 | 151.28
2015-08-03 | 984 | 1079 | 910 | 1098 | 21.46 | 4092.46 | 3964.25 | 128.21 |  |  |  | Inverter no-3 morning time note wakeup Err-no-ISU (8185) Folt reset manualy inverter started -10:01 WO# & Grid Failure From-15:40 to 15:49 WO#17070345 | 17070345
2015-08-04 | 967 | 1058 | 1057 | 1078 | 21.82 | 4181.82 | 4021.5 | 160.32 |  |  |  | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630
2015-08-05 | 825 | 899 | 899 | 920 | 17.57 | 3560.57 | 3386.25 | 174.32 |  |  |  | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning- 594 & Grid Failure From -06:30 to 06:40 WO#17177576 | 17177576 | 594
2015-08-06 | 792 | 859 | 853 | 896 | 17.74 | 3417.74 | 3301.5 | 116.24 |  |  |  | Module cleaning done inverter -4 Row- ,I,J,K,L,, & Total module cleaning -690 |  | 690
2015-08-07 | 887 | 972 | 973 | 1013 | 19.99 | 3864.99 | 3714 | 150.99 |  |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 |  | 604
2015-08-08 | 950 | 1040 | 1046 | 1079 | 21.91 | 4136.91 | 3973.5 | 163.41 |  |  |  | Module cleaning done Inverter- 3&2 Row- ,L,M,N, & Total module cleaning- 714 & Grid Failure From -15:03 to 15:10 WO#17364939 | 1736439 | 714
2015-08-09 | 899 | 509 | 983 | 1030 | 20.78 | 3441.78 | 3305.25 | 136.53 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -12:20 to 15:55 WO#
2015-08-10 | 548 | 356 | 605 | 603 | 12.36 | 2124.36 | 2007 | 117.36 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -13:20 to 17:05 WO# & Module cleaning done inverter -2 Row- ,J,K, & Total module cleaning -567 |  | 567
2015-08-11 | 746 | 272 | 814 | 820 | 15.7 | 2667.7 | 2520.75 | 146.95 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -10:00 to 16:00 WO# & Module cleaning done inverter -2&1 Row- ,H,I, & Total module cleaning -504 |  | 504
2015-08-12 | 470 | 514 | 515 | 514 | 9.69 | 2022.69 | 1906.5 | 116.19 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -10:20 to 10:40 WO#
2015-08-13 | 361 | 396 | 395 | 396 | 7.57 | 1555.57 | 1470 | 85.57
2015-08-14 | 486 | 543 | 532 | 542 | 10.52 | 2113.52 | 2010.75 | 102.77 |  |  |  | Two time Grid Failure From-9:50 to 9:59 WO#17658237 & 14:20 to 14:40 WO#17660923 | 17658237 17660923
2015-08-15 | 752 | 831 | 831 | 831 | 16.44 | 3261.44 | 3112.5 | 148.94
2015-08-16 | 860 | 944 | 938 | 958 | 17.74 | 3717.74 | 3558 | 159.74
2015-08-17 | 814 | 899 | 888 | 909 | 19.19 | 3529.19 | 3368.25 | 160.94
2015-08-18 | 820 | 904 | 859 | 931 | 18.95 | 3532.95 | 3384.75 | 148.2 |  |  |  | Inverter no-3 morning time note wakeup Err-no-ISU (8185) Folt reset manualy inverter started -09:40 WO#
2015-08-19 | 989 | 1092 | 1086 |  | 17.03 | 3184.03 | 3030 | 154.03 |  |  |  | Inverter no-4 morning time not wakeup Err code-0252 (IGBT SWICH) WO#
2015-08-20 | 775 | 706 | 837 |  | 10.34 | 2328.34 | 2201.25 | 127.09 |  |  |  | Inverter no-2 ABB sutdown to inverter 11:20 to 12:25 replace the Than card inverter started 12:25 WO#() & Inverter no-1,2,3,SMA Trackers sutdown to inverters 10:40 to 14:10 Mager testing Folt Faund inverter no-3 Folt issue sold out WO#() & Combiner P.M (750 Kw side)
2015-08-21 | 983 | 1074 | 1073 |  | 33.02 | 3163.02 | 2998.5 | 164.52 |  |  |  | Combiner P.M (250K.w) & Seeds P.M
2015-08-22 | 786 | 860 | 860 |  | 28.24 | 2534.24 | 2403.75 | 130.49
2015-08-23 | 871 | 943 | 944 |  | 29.99 | 2787.99 | 2645.25 | 142.74
2015-08-24 | 904 | 984 | 978 |  | 31.99 | 2897.99 | 2752.5 | 145.49 |  |  |  | Inverter no-1,2,3,4, inverters Filter cleaning
2015-08-25 | 854 | 928 | 921 | 769 | 31.07 | 3503.07 | 3345 | 158.07 |  |  |  | Inverter no-4 inverter started 10:15 a.m WO#()
2015-08-26 | 842 | 915 | 911 | 897 | 29.35 | 3594.35 | 3406.5 | 187.85 |  |  |  | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630
2015-08-27 | 1007 | 1103 | 1102 | 1075 | 35.62 | 4322.62 | 4136.25 | 186.37 |  |  |  | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594
2015-08-28 | 966 | 1063 | 1052 | 1039 | 33.76 | 4153.76 | 3963 | 190.76 |  |  |  | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 & Grid Failure From-10:00 to 10:05 WO#() |  | 690
2015-08-29 | 1007 | 1096 | 1079 | 1081 | 35.21 | 4298.21 | 4108.5 | 189.71
2015-08-30 | 825 | 894 | 888 | 896 | 27.64 | 3530.64 | 3374.25 | 156.39 |  |  |  | Two time Grid Failure From-07:09 to 07:21 & 11:28 to 11:38 WO#()
2015-08-31 | 803 | 876 | 876 | 832 | 29 | 3416 | 3234 | 182 |  |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-13:57 to 14:07 WO#(18593384) | 18593384 | 604
2015-09-01 | 1012 | 1102 | 1120 | 1086 | 37.87 | 4357.87 | 4167 | 190.87 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 & Two Time Grid Failure From-06:18 to 06:25 & 10:15 to 10:20 WO#(18632721 & 18635335) | 18632721 18635330 | 714
2015-09-02 | 972 | 1086 | 1085 | 1031 | 37.99 | 4211.99 | 4020.75 | 191.24 |  |  |  | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 & Grid Failure From-10:50 to 10:59 WO#(18695171) | 18695171 | 840
2015-09-03 | 972 | 1091 | 1069 | 1066 | 32.91 | 4230.91 | 3996 | 234.91 |  |  |  | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630
2015-09-04 | 1058 | 1164 | 1130 | 1010 | 36.4 | 4398.4 | 4277.25 | 121.15 |  |  |  | Module cleaning done inverter -1 Row- ,A,B,C,D,E, & Total module cleaning -483 & Grid Failure From-16:07 to 16:58 WO#(18814517) | 18814517 | 483
2015-09-05 | 955 | 1041 | 1012 | 965 | 33.45 | 4006.45 | 3814.5 | 191.95
2015-09-06 | 1091 | 1192 | 1148 | 1109 | 36.48 | 4576.48 | 4370.25 | 206.23
2015-09-07 | 1063 | 1142 | 1108 | 1040 | 38.06 | 4391.06 | 4217.25 | 173.81 |  |  |  | Inverter no-4 shutdown 13:00 to 13:28 for maintance Replace IGBT 'Y' Phase inverter started 13:28 WO#() & Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630
2015-09-08 | 871 | 933 | 910 | 962 | 31.53 | 3707.53 | 3546.75 | 160.78 |  |  |  | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594
2015-09-09 | 1046 | 1159 | 1153 | 1176 | 35.72 | 4569.72 | 4375.5 | 194.22 |  |  |  | Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 07++tive in AJB-116 of The Inverter-3 & 03--tive Line AJB-100 Inverter no-4 during The Period of 10:30 To 10:45.WO#(19058966) & Module cleaning done Inverter-4 Row ,I,J,K,L, & Total module cleaning 690 | 19058966 | 690
2015-09-10 | 1028 | 1125 | 1114 | 1148 | 33.08 | 4448.08 | 4287 | 161.08 |  |  |  | Two time Grid Failure From-14:36 to 14:47 & 16:25 to 17:55 WO#()
2015-09-11 | 1154 | 1267 | 1261 | 1271 | 40.2 | 4993.2 | 4802.25 | 190.95 |  |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-18:35 to 19:05 WO#() |  | 604
2015-09-12 | 1023 | 1113 | 1119 | 1132 | 34.94 | 4421.94 | 4258.5 | 163.44 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 & Grid Failure From-17:05 to 18:30 WO#(19203752) | 19203752 | 714
2015-09-13 | 1046 | 1148 | 1154 | 1199 | 38.52 | 4585.52 | 4433.25 | 152.27 |  |  |  | Three Time Grid Failure From-07:02 to 07:10 & 09:07 to 9:34 & 11:28 to 11:33 WO#() & Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 03++tive in AJB-101 of The Inverter-4 & 03--tive Line AJB-102 Inverter no-4 during The Period of 10:45 To 11:00.WO#(19237302) | 19225941 19232703 19235820 19237302
2015-09-14 | 1102 | 1210 | 1227 | 1265 | 39.33 | 4843.33 | 4659.75 | 183.58 |  |  |  | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 |  | 840
2015-09-15 | 1063 | 1187 | 1175 | 1213 | 39.88 | 4677.88 | 4487.25 | 190.63 |  |  |  | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630
2015-09-16 | 1125 | 1261 | 1238 | 1273 | 39.55 | 4936.55 | 4756.5 | 180.05 |  |  |  | Module cleaning done inverter -1 Row- ,A,B,C,D, E, & Total module cleaning -483 |  | 483
2015-09-17 | 1001 | 1091 | 1075 | 1092 | 35.8 | 4294.8 | 4139.25 | 155.55 |  |  |  | Module cleaning done inverter -4 Row- ,A,B,C,D, E, & Total module cleaning -630 |  | 630
2015-09-18 | 656 | 718 | 701 | 731 | 23.53 | 2829.53 | 2710.5 | 119.03 |  |  |  | Grid Failure From-14:40 to 14:54 WO#19495606 & Module clean by Rain | 19495606
2015-09-19 | [5 empty] | 0 |  | 0 |  |  |  | Grid Failure From-yesterday night to 18:05 WO# & Module clean by Rain & Main Transformer P.M
2015-09-20 | 17 | 11 | 11 | 16 | 0.54 | 55.54 | 1.5 | 54.04 |  |  |  | Grid Failure From-08:00 to 16:20 WO#(A.C.Voltage low) & Module clean by Rain
2015-09-21 | 305 | 453 | 452 | 361 | 14.73 | 1585.73 | 1489.5 | 96.23 |  |  |  | Inverter no-4 morning time not wake up Err no-0012 A.C.Voltage low reset Err code inverter started 11:25WO#19640583 & Inverter no-1 ABB 250 KVA Bloware than card failure Auto trip 13:00 to 13:35 WO#19640666 & Module clean by Rain | 19640583 19640666
2015-09-22 | 622 | 757 | 758 | 750 | 23.23 | 2910.23 | 2792.25 | 117.98 |  |  |  | Inverter no-1 ABB 250 KVA morning time note wake up Blowre than card Failure By pass 3 phase supply blowre & inverter started 10:08 WO#19676055 Module clean by Rain | 19676055
2015-09-23 | 898 | 984 | 984 | 1004 | 33.23 | 3903.23 | 3744 | 159.23 | 3950 | 5.29 | 72.77 | Grid Failure From-10:02 to 10:54 WO#(19734203) & Module clean by Rain | 19734203
2015-09-24 | 1120 | 1255 | 1243 | 1293 | 41.7 | 4952.7 | 4755.75 | 196.95 | 5000 | 6.56 | 74.288 | Today I Replaced The D.C.12Amp Fuse Link of The String- 05++tive in AJB-101 of The Inverter-1 during The Period of 10:30 To 10:45.WO#(19839635) | 19839635
2015-09-25 | 673 | 712 | 707 | 735 | 23.84 | 2850.84 | 2713.5 | 137.34 | 2910 | 5.09 | 55.7221 | Grid Failure (low voltege) From-08:15 to 12:27 WO#19835946 | 19835946
2015-09-26 | 1176 | 1289 | 1278 | 1329 | 42.39 | 5114.39 | 4914.75 | 199.64 | 5170 | 6.82 | 73.8854 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 & Grid Failure From-12:41 to 12:50 WO#(19898067) | 19898067 | 630
2015-09-27 | 1091 | 1204 | 1192 | 1258 | 37.67 | 4782.67 | 4594.5 | 188.17 |  |  |  | Grid Failure From-16:28 to 17:58 WO#(19957162) | 19957162 | 594
2015-09-28 | 1181 | 1317 | 1301 | 1376 | 42.59 | 5217.59 | 5033.25 | 184.34 | 5280 |  |  | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 & Grid Failure From-09:22 to 09:32 WO#(19991956) | 19991956 | 594
2015-09-29 | 1035 | 1126 | 1114 | 1167 | 37.01 | 4479.01 | 4279.5 | 199.51 | 4530 |  |  | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 |  | 690
2015-09-30 | 972 | 1068 | 1068 | 92.04 | 37.44 | 3237.48 | 3075 | 162.48 | 3250 |  |  | Grid Failure From-08:30 to 10:05 WO#(20099787) & Inverter No-4 sleep mode 10:07 to 17:05 Err code - sleep mode inverter WO#20108412 | 20099787 20108412
2015-10-01 | 1188 | 1300 | 1328 | 1300 | 42.34 | 5158.34 | 5001 | 157.34 | 5260 |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 |  | 604
2015-10-02 | 1136 | 1267 | 1278 | 1300 | 41.14 | 5022.14 | 4816.5 | 205.64
2015-10-03 | 1046 | 1164 | 1153 | 1200 | 37.65 | 4600.65 | 4351.5 | 249.15 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 |  | 714
2015-10-04 | 1153 | 1289 | 1267 | 1200 | 41.36 | 4950.36 | 4848 | 102.36 |  |  |  | Grid Failure From-09:06 to 09:13 WO#(20317939) | 20317939
2015-10-05 | 1131 | 1238 | 1221 | 1200 | 40.32 | 4830.32 | 4674 | 156.32 |  |  |  | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 & Grid Failure From-07:48 to 07:55 WO#(20355081) | 20355081 | 840
2015-10-06 | 1142 | 1250 | 1227 | 1200 | 40.37 | 4859.37 | 4737 | 122.37 | 4960 | 6.51 | 74.2597 | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630
2015-10-07 | 1142 | 1249 | 1227 | 1300 | 40.43 | 4958.43 | 4737 | 221.43 | 4970 | 6.53 | 74.1815 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,E, & A,B,C,D,E, & Total module cleaning -1103 |  | 1103
2015-10-08 | 1125 | 1233 | 1221 | 1300 | 40.52 | 4919.52 | 4693.5 | 226.02 | 4930 | 6.5 | 73.9241 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,E, & A,B,C,D,E,F,G,H, & Total module cleaning -2188 |  | 2188
2015-10-09 | 1080 | 1170 | 1193 | 1200 | 39.06 | 4682.06 | 4498.5 | 183.56 | 4720 | 6.29 | 73.1382 | Module cleaning done inverter -2 & 3 Row- ,K,L,M, & Total module cleaning -770 & Grid Failure From-13:42 to 13:55 & 16:43 to 16:54 WO#(20521472) |  | 770
2015-10-10 | 1040 | 1136 | 1147 | 1100 | 48.64 | 4471.64 | 4370.25 | 101.39 | 4600 | 6.09 | 73.6196 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-09:45 to 09:55 & 16:31 to 16:42 & 17:19 to 17:25 WO#() | 20561787 20580052 20580124 | 798
2015-10-11 | 486 | 526 | 537 | 500 | 20.57 | 2069.57 | 1987.5 | 82.07 |  |  |  | Grid Failure From-06:15 to 12:37 WO#()
2015-10-12 | 927 | 1006 | 1012 | 1000 | 36.98 | 3981.98 | 3877.5 | 104.48 | 4070 | 5.72 | 69.3507 | 6 Time Grid Failure From-08:45 to 08:56 & 9:00 to 9:22 & 10:11 to 10:28 & 15:52 to 15:58 & 17:05 to 17:52 & 17:37 to 17:43 WO#() | 20657087 20657369 20659381 20674817 20675269
2015-10-13 | 1023 | 1114 | 1125 | 1200 | 39.87 | 4501.87 | 4332.75 | 169.12 | 4480 | 6.27 | 69.6407 | Night time grid failure to 8:32 WO#20699781 & 17:51 to 17:56 | 20699781 20719213
2015-10-14 | 1103 | 1199 | 1210 | 1200 | 43.14 | 4755.14 | 4599 | 156.14 | 4830 | 6.4 | 73.5563 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 & Grid Failure From-16:28 to 16:33 WO#(20757004) | 20757004 | 630
2015-10-15 | 1091 | 1181 | 1193 | 1200 | 42.53 | 4707.53 | 4519.5 | 188.03 | 4750 | 6.29 | 73.603 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 & L.T PANEL P.M |  | 594
2015-10-16 | 1051 | 1131 | 1136 | 1189 | 41.24 | 4548.24 | 4344 | 204.24 | 4570 | 6.07 | 73.3804 | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 |  | 690
2015-10-17 | 1007 | 1085 | 1097 | 1121 | 42.3 | 4352.3 | 4163.25 | 189.05 | 4390 | 5.96 | 71.7911 | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-16:28 to 16:33 WO#(20757004) | 20757004 | 604
2015-10-18 | 1012 | 1097 | 1097 | 1147 | 43.66 | 4396.66 | 4191 | 205.66 | 4410 | 5.9 | 72.8516
2015-10-19 | 966 | 1046 | 1068 | 1072 | 41.89 | 4193.89 | 3993 | 200.89 | 4210 | 5.7 | 71.988 | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 |  | 714
2015-10-20 | 1018 | 1096 | 1154 | 1100 | 44.15 | 4412.15 | 4224 | 188.15 | 4450 | 5.86 | 74.0142 | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 |  | 840
2015-10-21 | 984 | 1063 | 1130 | 1200 | 43 | 4420 | 4163.25 | 256.75 | 4390 | 5.7 | 75.0658 | Today I Replaced The 3 D.C.12Amp Fuse Link of The String- 04--tive in AJB-101 of The Inverter-4 & String no-2 & 4 --tive line AJB -105 Inverter no-4 during The Period of 09:40 To 09:50.WO#(21052510) & Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 | 21052510 | 630
2015-10-22 | 1017 | 1142 | 1176 | 1200 | 44.92 | 4579.92 | 4381.5 | 198.42 | 4610 | 5.96 | 75.3889 | Module cleaning done inverter -1 Row- ,A,B,C,D,E, & Total module cleaning -483 |  | 483
2015-10-23 | 1063 | 1222 | 1227 | 1100 | 46.77 | 4658.77 | 4572.75 | 86.02 | 4810 | 6.19 | 75.7368 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630
2015-10-24 | 1074 | 1249 | 1221 | 1248 | 46.88 | 4838.88 | 4620.75 | 218.13 | 4860 | 6.2 | 76.4007 | Grid Failure From-17:21 to 17:32 WO#21218179 | 21218179
2015-10-25 | 826 | 933 | 922 | 936 | 36.13 | 3653.13 | 3478.5 | 174.63 | 3690 | 4.82 | 74.616 | Grid Failure From-11:10 to 11:22 WO#21252902 | 21252902
2015-10-26 | 1034 | 1153 | 1124 | 1146 | 43.24 | 4500.24 | 4280.25 | 219.99 | 4510 | 5.89 | 74.6301 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594
2015-10-27 | 1046 | 1136 | 1109 | 1126 | 42.96 | 4459.96 | 4249.5 | 210.46 | 4480 | 5.78 | 75.5445 | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 |  | 690
2015-10-28 | 1120 | 1216 | 1192 | 1261 | 46.51 | 4835.51 | 4620 | 215.51 | 4860 | 6.35 | 74.5959 | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-08:57 to 09:15 WO#(21392605) & Today Replace Transformers New Bridhar & slicagel (2,3,4,) | 21392605 | 604
2015-10-29 | 1193 | 1306 | 1272 | 1373 | 50.11 | 5194.11 | 4953.75 | 240.36 | 5210 | 6.62 | 76.7065 | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 & Grid Failure From-16:49 to 16:55 WO#() Transformers p.m & Inverter P.M (1,2,) | 21451062 | 714
2015-10-30 | 1181 | 1289 | 1278 | 1360 | 50.75 | 5158.75 | 4926 | 232.75 | 5170 | 6.44 | 78.2451 | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 & Inverter P.M (3,4) |  | 840
2015-10-31 | 1165 | 1277 | 1301 | 1341 | 50.36 | 5134.36 | 4899.75 | 234.61 | 5140 | 6.41 | 78.1552 | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630
2015-11-01 | 1068 | 1171 | 1193 | 1218 | 46.26 | 4696.26 | 4467.75 | 228.51 | 4710 | 6.01 | 76.38
2015-11-02 | 989 | 1108 | 1102 | 1134 | 43.21 | 4376.21 | 4188 | 188.21 | 4410 | 5.71 | 75.27 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,E, & A,B, & Total module cleaning -645 & Grid Failure From-08:49 to 08:54 WO#(21624101) | 21624101 | 645
2015-11-03 | 950 | 1068 | 1046 | 1066 | 40.78 | 4170.78 | 3984 | 186.78 | 4200 | 5.5 | 74.42 | Module cleaning done inverter - 4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-08:32 to 08:53 WO#(21667547) | 21667547 | 630
2015-11-04 | 882 | 973 | 944 | 965 | 36.66 | 3800.66 | 3608.25 | 192.41 | 3810 | 5.04 | 73.67 | Module cleaning done inverter - 4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-14:50 to 16:37 WO#(21738513) | 21738513 | 594
2015-11-05 | 1018 | 1119 | 1091 | 1119 | 42.26 | 4389.26 | 4187.25 | 202.01 | 4420 | 5.73 | 75.18 | Module cleaning done inverter -4,3,& Trackers Row- ,J,K,L,& S,T, & Total module cleaning -612 |  | 612
2015-11-06 | 865 | 955 | 916 | 968 | 37.27 | 3741.27 | 3571.5 | 169.77 | 3780 | 5.07 | 72.66 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-09:45 to 10:14 & 13:53 to 14:35 WO#(21826715) | 21826715 21838639 | 756
2015-11-07 | 899 | 984 | 961 | 1005 | 38.68 | 3887.68 | 3714 | 173.68 | 3930 | 5.14 | 74.52 | Module cleaning done inverter - 3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-15:57 to 16:05 WO#(21892950) | 21892950 | 777
2015-11-08 | 932 | 1018 | 1006 | 1010 | 40.31 | 4006.31 | 3804.75 | 201.56 | 4020 | 5.27 | 74.34
2015-11-09 | 933 | 1023 | 1023 | 1046 | 40.21 | 4065.21 | 3867.75 | 197.46 | 4090 | 5.3 | 75.21 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2015-11-10 | 927 | 1018 | 1035 | 1042 | 39.75 | 4061.75 | 3855.75 | 206 | 4080 | 5.26 | 75.6 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2015-11-11 | 928 | 1040 | 1040 | 1046 | 40.31 | 4094.31 | 3890.25 | 204.06 | 4110 | 5.29 | 75.72
2015-11-12 | 955 | 1068 | 1069 | 1072 | 42.03 | 4206.03 | 4004.25 | 201.78 | 4230 | 5.47 | 75.37
2015-11-13 | 972 | 1091 | 1091 | 1083 | 42.67 | 4279.67 | 4068 | 211.67 | 4300 | 5.62 | 74.57
2015-11-14 | 1001 | 1137 | 1125 | 1136 | 44.15 | 4443.15 | 4226.25 | 216.9 | 4460 | 5.82 | 74.69 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498
2015-11-15 | 995 | 1142 | 1114 | 1120 | 43.54 | 4414.54 | 4199.25 | 215.29 | 4430 | 5.68 | 76.01
2015-11-16 | 893 | 1012 | 983 | 1006 | 40.13 | 3934.13 | 3750.75 | 183.38 | 3997 | 5.22 | 74.63 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-07:49 to 08:07 & 14:01 to 14:59 & 17:10 to 17:27 WO#() | 22307137 22318269 22324208 | 630
2015-11-17 | 1001 | 1096 | 1069 | 1048 | 42.43 | 4256.43 | 4057.5 | 198.93 | 4280 | 5.56 | 75.02 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-16:13 to 16:20 & 17:00 to 17:28 WO#() | 22403483 | 594
2015-11-18 | 995 | 1092 | 1062 | 1069 | 42.67 | 4260.67 | 4043.25 | 217.42 | 4280 | 5.68 | 73.44 | Module cleaning done inverter -4 & 3 Row- ,J,K,L, & S,T, & Trackers & Total module cleaning -612 & Grid Failure From-09:49 to 10:04 WO#() | 22414913 | 612
2015-11-19 | 1029 | 1125 | 1098 | 1122 | 43.88 | 4417.88 | 4211.25 | 206.63 | 4430 | 5.75 | 75.09 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2015-11-20 | 1029 | 1136 | 1108 | 1146 | 45.53 | 4464.53 | 4250.25 | 214.28 | 4480 | 5.84 | 74.76 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2015-11-21 | 995 | 1091 | 1097 | 1120 | 43.84 | 4346.84 | 4138.5 | 208.34 | 4360 | 5.68 | 74.81 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 & seeds P.M |  | 798
2015-11-22 | 898 | 989 | 1007 | 1010 | 39.67 | 3943.67 | 3781.5 | 162.17 | 3950 | 4.79 | 80.37
2015-11-23 | 860 | 967 | 977 | 994 | 37.9 | 3835.9 | 3639 | 196.9 | 3850 | 5.02 | 74.74 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2015-11-24 | 650 | 741 | 724 | 726 | 27.72 | 2868.72 | 2704.5 | 164.22 | 2890 | 3.69 | 76.33 | Module cleaning done inverter -4 & 1 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Grid Failure From-15:09 to 15:17 WO#() | 22716056 | 498
2015-11-25 | 735 | 814 | 797 | 779 | 31.13 | 3156.13 | 2985 | 171.13 | 3180 | 4.23 | 73.27 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630
2015-11-26 | 803 | 893 | 877 | 800 | 34.25 | 3407.25 | 3303.75 | 103.5 | 3500 | 4.66 | 73.2 | Module cleaning done inverter -4 Row- ,G,H,I & Total module cleaning -594 |  | 594
2015-11-27 | 984 | 1108 | 1079 | 1116 | 41.73 | 4328.73 | 4126.5 | 202.23 | 4350 | 5.65 | 75.04 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Grid Failure From-17:08 to 17:19 WO#(22855523) | 22855523 | 612
2015-11-28 | 864 | 961 | 962 | 982 | 40.1 | 3809.1 | 3629.25 | 179.85 | 3840 | 5.2 | 71.97 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-11:13 to 11:45 WO#(22889812) | 22889812 | 756
2015-11-29 | 1024 | 1112 | 1147 | 1157 | 46.17 | 4486.17 | 4299.75 | 186.42 | 4520 | 6 | 73.42 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07--tive in AJB-105 of The Inverter-1 during The Period of 11:10 To 11:15.WO#(22939578) & Trackers P.M | 22939578
2015-11-30 | 848 | 939 | 956 | 943 | 37.36 | 3723.36 | 3540 | 183.36 | 3875 | 5.1 | 74.055 | Module cleaning done inverter -2 & 3 Row- ,K,L,M, & Total module cleaning -777 & Transformer No-2 300kva P.M |  | 777
2015-12-01 | 825 | 1006 | 1000 | 985 | 39.24 | 3855.24 | 3672.75 | 182.49 | 3890 | 5.21 | 72.77 | today ABB engineer has come at site for replacing blower than card so for replacing purpose we took shut down at 15:50 and switching on at 16:45. But that card couldn’t work so they will get to fix some other card by this week. & Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 | 23044484 | 798
2015-12-02 | 984 | 1119 | 1091 | 1072 | 43.36 | 4309.36 | 4107 | 202.36 | 4330 | 5.71 | 73.9 | Today I Replaced The D.C.12Amp Fuse Link of The String- 05--tive in AJB-105 of The Inverter-1 during The Period of 10:15 To 10:20.WO#() & Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-16:59 to 17:22 WO#() | 23332248 23824011 | 546
2015-12-03 | 1080 | 1193 | 1165 | 1150 | 46.83 | 4634.83 | 4419.75 | 215.08 | 4650 | 6.23 | 72.74 | Module cleaning done inverter -4 & 1 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 |  | 498
2015-12-04 | 1045 | 1154 | 1119 | 1200 | 45.65 | 4563.65 | 4305 | 258.65 | 4520 | 6.15 | 71.63 | Module cleaning done inverter -4 Row- C,D,E,F & Total module cleaning -630 & Grid failure from - 12:40 to 12:49 WO# | 23332366 | 630
2015-12-05 | 973 | 1062 | 1040 | 1078 | 42.11 | 4195.11 | 3977.25 | 217.86 | 4210 | 5.72 | 71.73
2015-12-06 | 1001 | 1097 | 1070 | 1121 | 43.48 | 4332.48 | 4116 | 216.48 | 4340 | 5.9 | 71.69 | Module cleaning done inverter -4 Row- G,H,I, & Total module cleaning -594 |  | 594
2015-12-07 | 932 | 1018 | 995 | 1052 | 41.97 | 4038.97 | 3840.75 | 198.22 | 4058 | 5.7 | 69.3889 | Module cleaning done inverter -4 & Trackers Row- ,J,K,L,& S,T, & Total module cleaning -612 |  | 612
2015-12-08 | 933 | 1063 | 1069 | 1084 | 43.45 | 4192.45 | 3991.5 | 200.95 | 4205 | 5.7 | 71.9025 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2015-12-09 | 899 | 983 | 1011 | 1008 | 40.58 | 3941.58 | 3751.5 | 190.08 | 3940 | 5.33 | 72.04 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2015-12-10 | 916 | 1035 | 1035 | 1000 | 41.3 | 4027.3 | 3891 | 136.3 | 4110 | 5.33 | 75.15 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2015-12-11 | 938 | 1085 | 1063 | 1026 | 42.87 | 4154.87 | 3965.25 | 189.62 | 4180 | 5.38 | 75.72 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid failure from - 10:32 to 10:38 WO#() | 23500607 | 546
2015-12-12 | 1086 | 1199 | 1170 | 1149 | 47.56 | 4651.56 | 4432.5 | 219.06 | 4660 | 6.08 | 74.7 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D & A,B & Total module cleaning -498 |  | 498
2015-12-13 | 1063 | 1164 | 1119 | 1111 | 46.31 | 4503.31 | 4296 | 207.31 | 4520 | 5.96 | 73.91 | Module cleaning done inverter -4 Row- C,D,E,F, & Total module cleaning -630 & Grid failure from - 14:04 to 14:09 WO#() | 23602126 | 630
2015-12-14 | 1068 | 1171 | 1126 | 1121 | 46.58 | 4532.58 | 4314 | 218.58 | 4540 | 5.98 | 73.99 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594
2015-12-15 | 1108 | 1226 | 1187 | 1203 | 48.83 | 4772.83 | 4545.75 | 227.08 | 4780 | 6.29 | 74.06 | Today I Replaced The D.C.12Amp Fuse Link of The String- 05--tive in AJB-115 of The Inverter-1 during The Period of 10:20 To 10:25.WO#() & Module cleaning done inverter -3&4 Trackers Row- ,J,K,L, & S,T, & Total module cleaning -612 | 23684627 | 612
2015-12-16 | 1069 | 1171 | 1142 | 1191 | 46.91 | 4619.91 | 4393.5 | 226.41 | 4630 | 6.14 | 73.49 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2015-12-17 | 1040 | 1147 | 1147 | 1184 | 47.32 | 4565.32 | 4353 | 212.32 | 4590 | 5.94 | 75.31 | Module cleaning done inverter -2 & 3 Row- ,K,L,M, & Total module cleaning -777 & Grid failure from - 17:09 to 17:13 WO#() | 23827201 | 777
2015-12-18 | 1063 | 1176 | 1205 | 1184 | 48.66 | 4676.66 | 4453.5 | 223.16 | 4680 | 6.08 | 75.02 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2015-12-19 | 1012 | 1154 | 1147 | 1113 | 46.46 | 4472.46 | 4283.25 | 189.21 | 4480 | 5.8 | 75.28 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2015-12-20 | 1023 | 1187 | 1159 | 1127 | 46.69 | 4542.69 | 4332 | 210.69 | 4560 | 5.98 | 74.32
2015-12-21 | 967 | 1074 | 1057 | 1000 | 42.7 | 4140.7 | 3933 | 207.7 | 4150 | 5.35 | 75.6
2015-12-22 | 916 | 1012 | 990 | 927 | 39.94 | 3884.94 | 3687.75 | 197.19 | 3900 | 5.06 | 75.12 | Inverter No-1,2,3,4, Filter Cleaning & Inverter No- 4 (P.M)
2015-12-23 | 916 | 1006 | 983 | 921 | 39.78 | 3865.78 | 3663.75 | 202.03 | 3880 | 5.08 | 74.44
2015-12-24 | 1000 | 1103 | 1080 | 1021 | 43.69 | 4247.69 | 4039.5 | 208.19 | 4260 | 5.61 | 74.01
2015-12-25 | 972 | 1068 | 1040 | 974 | 42.62 | 4096.62 | 3886.5 | 210.12 | 4110 | 5.4 | 74.18
2015-12-26 | 1030 | 1131 | 1103 | 1079 | 45.08 | 4388.08 | 4169.25 | 218.83 | 4400 | 5.81 | 73.81
2015-12-27 | 977 | 1085 | 1057 | 1049 | 43.78 | 4211.78 | 4008.75 | 203.03 | 4230 | 5.68 | 72.58
2015-12-28 | 198 | 221 | 209 | 225 | 10.26 | 863.26 | 768.75 | 94.51 |  |  |  | Grid Failure From-08:20 to 14:40 WO#24330844
2015-12-29 | 566 | 1051 | 1029 | 1029 | 48.01 | 3723.01 | 3531.75 | 191.26 | 3740 | 5.74 | 63.5 | Inverter no- 1 ABB (250KW) Auto trip 10:00 to 17:00 wo# | 24379670
2015-12-30 | 712 | 1024 | 995 | 970 | 45.03 | 3746.03 | 3550.5 | 195.53 | 3770 | 5.51 | 66.68 | Inverter-no-1 ABB was shut down from 12:30 to 14:00 for replacing the IGBT blower by ABB engineer but job could't completed
2016-12-31 | 628 | 808 | 972 | 949 | 45.39 | 3402.39 | 3230.25 | 172.14 | 3430 | 5.35 | 62.48 | Inverter-no-1 ABB was shut down from 13:25 to 16:00 & Inverter-no-2 was shut down from14:00 to 15:30 for replacing the IGBT blower by ABB engineer but job could't completed
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0

## 2016
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2016
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 1104500525 | 7802195 | 2100570073/ 2100567820/ 2100567898
2016-01-01 | 966 | 1080 | 1046 | 1034 | 49.08 | 4175.08 | 3960 | 215.08 | 4180 | 5.76 | 70.73
2016-01-02 | 865 | 966 | 939 | 934 | 43.44 | 3747.44 | 3560.25 | 187.19 | 3770 | 5.14 | 71.48 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -594 & Grid Failure From- 14:03 to 14:08WO# | 24587769 | 594
2016-01-03 | 876 | 979 | 938 | 940 | 43.52 | 3776.52 | 3585.75 | 190.77 | 3800 | 5.18 | 71.5
2016-01-04 | 877 | 978 | 944 | 986 | 43.77 | 3828.77 | 3599.25 | 229.52 | 3840 | 5.24 | 71.42 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594
2016-01-05 | 904 | 1012 | 973 | 1077 | 45.85 | 4011.85 | 3841.5 | 170.35 | 4030 | 5.43 | 72.33 | Module cleaning done inverter -4 & 3 Row- ,I,J,K,L, & S,T, & Total module cleaning -818 |  | 818
2016-01-06 | 888 | 989 | 972 | 1085 | 48.93 | 3982.93 | 3782.25 | 200.68 | 4000 | 5.33 | 73.14 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-01-07 | 865 | 961 | 1001 | 1050 | 48.21 | 3925.21 | 3732.75 | 192.46 | 3950 | 5.26 | 73.19 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-01-08 | 921 | 1040 | 1125 | 1124 | 51.44 | 4261.44 | 4018.5 | 242.94 | 4270 | 5.58 | 74.58 | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -798 |  | 798
2016-01-09 | 905 | 1080 | 1108 | 1069 | 50.06 | 4212.06 | 4015.5 | 196.56 | 4220 | 5.43 | 75.74 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-01-10 | 904 | 1114 | 1102 | 1058 | 41.29 | 4219.29 | 4039.5 | 179.79 | 4210 | 5.51 | 74.47
2016-01-11 | 860 | 1051 | 1018 | 981 | 38.31 | 3948.31 | 3763.5 | 184.81 | 3980 | 5.27 | 73.61% | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From- 14:00 to 14:07 WO# |  | 498
2016-01-12 | 802 | 956 | 972 | 930 | 37.22 | 3697.22 | 3491.25 | 205.97 | 3720 | 5 | 72.51 | Inverter-no-1 ABB was shut down from 16:05 & Inverter-2 was shut down 16:25 for replacing the IGBT blower by ABB engineer but job could't completed & Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630
2016-01-13 | 962 | 1080 | 1046 | 1063 | 49.8 | 4200.8 | 4004.25 | 196.55 | 4250 | 5.5 | 75.31 | Module cleaning done inverter - 4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From- 10:30 to 10:42 & 15:25 to 15:36 WO# |  | 594
2016-01-14 | 995 | 1102 | 1058 | 1059 | 50.25 | 4264.25 | 4104.75 | 159.5 | 4280 | 5.51 | 75.71% | Grid Failure From- 8:32 to 8:35 WO#25122514 | 25122514
2016-01-15 | 1012 | 1114 | 1085 | 1077 | 52.34 | 4340.34 | 4134.75 | 205.59 | 4370 | 5.7 | 74.72 | Module cleaning done inverter - 4 & 3 Trackers Row- ,J,K,L, & S,T, Total module cleaning -612 & Grid Failure From- 11:55 to 12:02 & 17:04 to 17:08 & 17:32 TO 17:35 WO# | 25178460 25190550 25191566 | 612
2016-01-16 | 876 | 961 | 933 | 907 | 42.58 | 3719.58 | 3516.75 | 202.83 | 3740 | 4.79 | 76.1 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-01-17 | 786 | 853 | 826 | 807 | 32.22 | 3304.22 | 3138 | 166.22 | 3330 | 4.3 | 75.47 | Grid Failure From- 7:30 to 9:20 WO# | 25282478
2016-01-18 | 752 | 809 | 786 | 761 | 30.61 | 3138.61 | 2967.75 | 170.86 | 3150 | 4.04 | 75.99 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-01-19 | 859 | 938 | 915 | 910 | 37.54 | 3659.54 | 3467.25 | 192.29 | 3670 | 4.72 | 75.78 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2016-01-20 | 1023 | 1137 | 1125 | 1140 | 54.04 | 4479.04 | 4255.5 | 223.54 | 4490 | 5.67 | 77.18 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-01-21 | 1097 | 1236 | 1255 | 1222 | 61.01 | 4871.01 | 4652.25 | 218.76 | 4870 | 6.55 | 72.46 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Change the pyranometer & Change the inverter no-1 ABB new Blower fan |  | 498
2016-01-22 | 792 | 905 | 905 | 885 | 30.11 | 3517.11 | 3357 | 160.11 | 3550 | 4.92 | 70.32 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-14:15 to 17:08 | 25545549 | 630
2016-01-23 | 1102 | 1300 | 1273 | 1245 | 47.88 | 4967.88 | 4739.25 | 228.63 | 4980 | 6.87 | 70.65 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594
2016-01-24 | 1091 | 1278 | 1238 | 1208 | 46.87 | 4861.87 | 4638.75 | 223.12 | 4870 | 6.77 | 70.11 | Grid Failure From- 15:35 to 15:43 WO# | 25639141
2016-01-25 | 1091 | 1249 | 1216 | 1173 | 45.06 | 4774.06 | 4563 | 211.06 | 4790 | 6.65 | 70.2 | Module cleaning done inverter -4 & 3 & Trackers Row- ,J,K,L, & S,T, & Total module cleaning -612 |  | 612
2016-01-26 | 1091 | 1216 | 1193 | 1181 | 44.1 | 4725.1 | 4500.75 | 224.35 | 4730 | 6.45 | 71.47 |  |  | 756
2016-01-27 | 968 | 1114 | 1079 | 1098 | 40.41 | 4299.41 | 4132.5 | 166.91 | 4350 | 5.85 | 72.47 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 777
2016-01-28 | 995 | 1113 | 1086 | 1114 | 40.41 | 4348.41 | 4148.25 | 200.16 | 4370 | 5.97 | 71.34 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-15:06 to 15:12 | 25775460
2016-01-29 | 899 | 1012 | 983 | 1021 | 38.08 | 3953.08 | 3758.25 | 194.83 | 3980 | 6.05 | 64.11 | Module cleaning done inverter - 2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-14:52 to 15:15 & Transformer P.M | 258770143 | 798
2016-01-30 | 1068 | 1193 | 1210 | 1236 | 44.18 | 4751.18 | 4518 | 233.18 | 4770 | 6.34 | 73.33 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-01-31 | 1058 | 1187 | 1210 | 1223 | 43.45 | 4721.45 | 4527.75 | 193.7 | 4740 | 6.34 | 72.86
2016-02-01 | 944 | 1069 | 1097 | 1079 | 39.2 | 4228.2 | 4014 | 214.2 | 4250 | 5.72 | 72.41 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498
2016-02-02 | 1006 | 1198 | 1164 | 1128 | 42.38 | 4538.38 | 4343.25 | 195.13 | 4560 | 6.04 | 73.58 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-16:38 to 16:47 | 25944632 | 630
2016-02-03 | 1108 | 1271 | 1233 | 1193 | 44.49 | 4849.49 | 4593 | 256.49 | 4870 | 6.41 | 74.04 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594
2016-02-04 | 1199 | 1357 | 1317 | 1295 | 47.57 | 5215.57 | 5013.75 | 201.82 | 5220 | 6.92 | 73.52 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-02-05 | 1130 | 1278 | 1244 | 1256 | 44.6 | 4952.6 | 4732.5 | 220.1 | 4970 | 6.61 | 73.28 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-02-06 | 984 | 1198 | 1159 | 1194 | 44.34 | 4579.34 | 4385.25 | 194.09 | 4610 | 6.28 | 71.54 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Two Time Grid Failure From -7:55 to 8:13 & 8:20 to 8:45 & Inverter no-1 ABB 8:20 Auto trip D.C. Bracker of manual Auto reset inverter started 9:35 | 25946601 25946588 25946589 | 777
2016-02-07 | 1080 | 1222 | 1210 | 1215 | 48.72 | 4775.72 | 4554.75 | 220.97 | 4790 | 6.34 | 73.63
2016-02-08 | 1170 | 1323 | 1334 | 1296 | 50.01 | 5173.01 | 4920 | 253.01 | 5170 | 6.92 | 72.81 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2016-02-09 | 1086 | 1255 | 1260 | 1196 | 47.32 | 4844.32 | 4640.25 | 204.07 | 4860 | 6.43 | 73.66 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-02-10 | 1119 | 1323 | 1284 | 1220 | 48.16 | 4994.16 | 4780.5 | 213.66 | 5020 | 6.6 | 74.13 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-9:42 to 9:50 WO# | 25957936 | 498
2016-02-11 | 1068 | 1255 | 1187 | 1133 | 44.37 | 4687.37 | 4446.75 | 240.62 | 4660 | 6.34 | 71.63 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-16:50 to 16:58 WO# | 25961555 | 630
2016-02-12 | 1086 | 1221 | 1181 | 1145 | 44.53 | 4677.53 | 4463.25 | 214.28 | 4690 | 6.31 | 72.44 | Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 03--tive in AJB-102 of The Inverter-4 & 07--tive AJB-104 Inverter NO-4 during The Period of 16:45 To 17:00.WO#() & Module cleaning done Inverter-4 Row ,G,H,I, & Total module cleaning 594 |  | 594
2016-02-13 | 1091 | 1238 | 1205 | 1221 | 44.88 | 4799.88 | 4584.75 | 215.13 | 4810 | 6.34 | 73.94 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-02-14 | 1102 | 1238 | 1187 | 1225 | 46.5 | 4798.5 | 4590 | 208.5 | 4820 | 6.39 | 73.51
2016-02-15 | 1080 | 1222 | 1181 | 1208 | 45.87 | 4736.87 | 4518 | 218.87 | 4750 | 6.3 | 73.48 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-02-16 | 911 | 1017 | 1024 | 981 | 38.14 | 3971.14 | 3783.75 | 187.39 | 3990 | 5.23 | 74.35 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-02-17 | 848 | 961 | 961 | 913 | 35.05 | 3718.05 | 3534 | 184.05 | 3740 | 4.91 | 74.24 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2016-02-18 | 915 | 1063 | 1035 | 982 | 38.43 | 4033.43 | 3851.25 | 182.18 | 4060 | 5.46 | 72.47 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-02-19 | 928 | 1035 | 1006 | 992 | 36.73 | 3997.73 | 3806.25 | 191.48 | 4020 | 5.35 | 73.23 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498
2016-02-20 | 802 | 893 | 865 | 890 | 31.53 | 3481.53 | 3307.5 | 174.03 | 3510 | 4.45 | 76.87 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Combiner P.M |  | 630
2016-02-21 | 865 | 978 | 950 | 976 | 35.83 | 3804.83 | 3633.75 | 171.08 | 3840 | 5.21 | 71.83 | Two time Grid Failure From-12:53 to 14:08 & 14:17 to 14:22WO# & SEEDS P.M | 25995899 25995901
2016-02-22 | 1057 | 1193 | 1153 | 1205 | 44.54 | 4652.54 | 4444.5 | 208.04 | 4670 | 6.2 | 73.41 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594
2016-02-23 | 1216 | 1379 | 1379 | 1398 | 53.44 | 5425.44 | 5178.75 | 246.69 | 5430 | 7.25 | 72.99 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-02-24 | 1035 | 1176 | 1199 | 1165 | 45.15 | 4620.15 | 4417.5 | 202.65 | 4640 | 6.11 | 74.01 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-02-25 | 836 | 1086 | 1074 | 1042 | 40.93 | 4078.93 | 3900.75 | 178.18 | 4120 | 5.56 | 72.22 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Two Time Grid Failure From -7:50 to 8:20 & 11:20 to 8:27 & Inverter no-1 ABB 8:20 Auto trip D.C. Bracker of manual Auto 7:50 reset inverter started 9:28 | 26005473 26005832 | 777
2016-02-26 | 1154 | 1328 | 1300 | 1278 | 48.86 | 5108.86 | 4884.75 | 224.11 | 5123 | 6.5 | 76.8181 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2016-02-27 | 1215 | 1385 | 1251 | 1353 | 51.49 | 5255.49 | 5109 | 146.49 | 5336 | 6.7 | 77.62 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-02-28 | 1176 | 1340 | 1312 | 1334 | 50.11 | 5212.11 | 4984.5 | 227.61 | 5230 | 6.95 | 73.34
2016-02-29 | 1102 | 1261 | 1227 | 1251 | 47.46 | 4888.46 | 4641 | 247.46 | 4910 | 6.6 | 72.5 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-14:56 to 15:06 WO# | 26016220 | 498
2016-03-01 | 781 | 1170 | 1159 | 1172 | 45.59 | 4327.59 | 4193.25 | 134.34 | 4210 | 5.6 | 0.73273 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From -10:01 to 10:09 & Inverter no-1 ABB 10::09 Auto trip D.C. Bracker of manual Auto reset inverter started 12:00 | 26018866 26015567 | 630
2016-03-02 | 853 | 955 | 978 | 934 | 37.26 | 3757.26 | 3575.25 | 182.01 | 3930 | 5.31 | 0.72136 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594
2016-03-03 | 888 | 1012 | 961 | 1004 | 39.51 | 3904.51 | 3744 | 160.51 | 3920 | 5.34 | 71.54 | Inverter #3 didn’t wake up in the morning due to DC breaker tripped , this problem occur due to grid outage from 2:30am to 6:00am.Inverter started 9:14 & Module clean by rain | 26029140
2016-03-04 | 1034 | 1122 | 1170 | 1159 | 46.3 | 4531.3 | 4384.5 | 146.8 | 4610 | 6.2 | 72.47
2016-03-05 | 667 | 752 | 741 | 762 | 28.53 | 2950.53 | 2808.75 | 141.78 | 2990 | 3.96 | 73.59 | Module cleaning done Inverter-4 Row ,A,B,C,D,E, & Total module cleaning 630 & Grid Failure From-10:50 to 14:00 WO# | 26028652 | 630
2016-03-06 | 1142 | 1312 | 1294 | 1341 | 56.01 | 5145.01 | 4924.5 | 220.51 | 5162 | 6.87 | 73.23 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04--tive in AJB-105 of The Inverter-4 during The Period of 10:05 To 10:10.WO#() | 26030635
2016-03-07 | 1131 | 1294 | 1278 | 1333 | 58.28 | 5094.28 | 4872 | 222.28 | 5101 | 6.73 | 73.87
2016-03-08 | 1176 | 1351 | 1234 | 1414 | 62.83 | 5237.83 | 5104.5 | 133.33 | 5353 | 7.15 | 72.96 | Module cleaning done Inverter-4 Row ,F,G,H, & Total module cleaning 594 |  | 594
2016-03-09 | 1114 | 1289 | 1275 | 1349 | 60.76 | 5087.76 | 4883.25 | 204.51 | 5130 | 6.91 | 72.35 | Module cleaning done inverter -4 & 3 Trackers Row- ,I,J,K,L, & ,S,T, & Total module cleaning -710 & Grid Failure From-10:48 to 10:53 |  | 710
2016-03-10 | 1102 | 1272 | 1295 | 1335 | 59.55 | 5063.55 | 4869.75 | 193.8 | 5090 | 6.76 | 73.38 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-17:29 to 17:56 |  | 756
2016-03-11 | 1142 | 1368 | 1351 | 1360 | 65.41 | 5286.41 | 5055 | 231.41 | 5280 | 7.03 | 73.2 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-03-12 | 1035 | 1272 | 1249 | 1155 | 58.92 | 4769.92 | 4568.25 | 201.67 | 4875 |  |  | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Morning Time Grid Failure Inverter No-2,3,4, started 8:35 & Inverter No-1 started 9:20 (D.C. Bracker Auto trip) |  | 798
2016-03-13 | 1108 | 1261 | 1244 | 1248 | 59.43 | 4920.43 | 4700.25 | 220.18 | 4888 |  |  | Grid Failure From-11:07 to 11:11
2016-03-14 | 1164 | 1371 | 1328 | 1366.88 | 64.24 | 5294.12 | 5079 | 215.12 | 5309 |  |  | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-7:26 to 7:51 & 11:20 to 11:30 | 26046664 26047323 | 546
2016-03-15 | 978 | 1159 | 1142 | 1172 | 52.57 | 4503.57 | 4313.25 | 190.32 | 4520 | 6.1 | 72.22 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-09:05 to 9:51 | 260447572 | 498
2016-03-16 | 1159 | 1300 | 1284 | 1380 | 61.65 | 5184.65 | 4949.25 | 235.4 | 5190 | 6.9 | 73.31 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03++tive in AJB-101 of The Inverter-4 during The Period of 10:05 To 10:10 & Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 | 26049799 | 630
2016-03-17 | 1131 | 1278 | 1306 | 1368 | 60.54 | 5143.54 | 4920.75 | 222.79 | 5150 | 6.77 | 74.14 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594
2016-03-18 | 1148 | 1340 | 1339 | 1398 | 60.3 | 5285.3 | 5049 | 236.3 | 5290 | 6.88 | 74.94 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-03-19 | 1051 | 1204 | 1193 | 1243 | 52.04 | 4743.04 | 4544.25 | 198.79 | 4770 | 6.22 | 74.74 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-14:52 to 14:58 & 15:56 to 16:05 | 26066161 26066162 | 756
2016-03-20 | 1148 | 1317 | 1278 | 1338 | 58.38 | 5139.38 | 4920.75 | 218.63 | 5150 | 7.03 | 71.4 | Grid Failure From-13:46 to 13:52 & 16:08 to 16:30 | 26066355 26066361
2016-03-21 | 1164 | 1334 | 1323 | 1335 | 54.54 | 5210.54 | 4984.5 | 226.04 | 5220 | 7.07 | 73.96 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-03-22 | 1216 | 1363 | 1340 | 1390 | 56.49 | 5365.49 | 5128.5 | 236.99 | 5370 | 7.28 | 71.89 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2016-03-23 | 916 | 1362 | 1345 | 1420 | 57.48 | 5100.48 | 4861.5 | 238.98 | 5110 | 7.48 | 66.58 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Inverter No-1 ABB (250 KW) Auto trip Err code- (8189) D.C. Bracker off 14:30 (inverter stoped) WO# | 26070546 | 546
2016-03-24 |  | 1295 | 1284 | 1354 | 54.19 | 3987.19 | 3783.75 | 203.44 | 4012 | 7.14 | 54.76
2016-03-25 |  | 1080 | 1068 | 1156 | 42.41 | 3346.41 | 3191.5 | 154.91 | 3390 | 5.93 | 55.71 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-09:11 to 9:26 | 26071335 | 498
2016-03-26 |  | 831 | 825 | 882 | 31.93 | 2569.93 | 2401.5 | 168.43 | 2610 | 4.45 | 57.16 | cloudy day
2016-03-27 |  | 1148 | 1193 | 1326 | 48 | 3715 | 3531 | 184 | 3750 | 6.57 | 55.63 | Grid Failure From-08:52 to 09:10 & Inverter No-2 ABB 250 KW Trip -9:10 Auto Run Lost Reset Err Inverter started 9:37 | 26079827 26079828
2016-03-28 |  | 1073 | 1063 | 1170 | 42.73 | 3348.73 | 3157.5 | 191.23 | 3380 | 5.77 | 57.09
2016-03-29 | 181 | 854 | 1199 | 1333 | 48.32 | 3615.32 | 3474 | 141.32 | 3660 | 6.83 | 52.22 | Grid Failure From- 8:41 to 8:48 & 11:49 to 11:59 & Inverter No-2 ABB 250 KW Trip -9:40 Auto Run Lost Reset Err Inverter started 12:00 & Inverter No-1 ABB 250kw Resolved the issue change the R,D,I Card inverter started 15:10 | 26070546 26080565 26080994 26081477
2016-03-30 | 1108 | 1233 | 1221 | 1345 | 49.05 | 4956.05 | 4714.5 | 241.55 | 4960 | 6.81 | 70.98 | no module cleaning
2016-03-31 | 995 | 1091 | 1079 | 1208 | 44.31 | 4417.31 | 4239.75 | 177.56 | 4440 | 6.12 | 70.71 | Module cleaning done Inverter-4 Row ,A,B,C,D,E, & Total module cleaning 630 & Grid Failure From-13:40 to 13:50 & 14:13 to 14:58 | 26087168 26087178 | 630
2016-04-01 | 1040 | 1147 | 1137 | 1321 | 43.58 | 4688.58 | 4475.25 | 213.33 | 4700 | 6.32 | 72.48 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594
2016-04-02 | 887 | 1063 | 1052 | 1263 | 40 | 4305 | 4117.5 | 187.5 | 4070 | 5.8 | 68.3942 | Module cleaning done inverter -4 & 3 Trackers Row- ,I,J,K,L, & ,S,T, & Total module cleaning -710 & Grid Failure From-08:00 to 08:13 & 10:04 to 10:13 & 12:09 to 12:15 & Inverter No-1 ABB (250 KW) Auto trip 08:13 Err code- (8189) D.C. Bracker off Inverter started 09:30 WO# | 26092349 26092348 26092355 | 710
2016-04-03 | 984 | 1142 | 1130 | 1344 | 47.64 | 4647.64 | 4452 | 195.64 | 4950 | 6.3 | 76.5803
2016-04-04 | 939 | 1024 | 1057 | 1211 | 43.54 | 4274.54 | 4080 | 194.54 | 4300 | 5.62 | 74.57 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-11:02 to 11:10 | 26098344 | 756
2016-04-05 | 1063 | 1170 | 1284 | 1373 | 49.52 | 4939.52 | 4712.25 | 227.27 | 4960 | 6.57 | 73.58 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 Grid Failure From-16:21 to 16:28 | 26099407 | 777
2016-04-06 | 938 | 1074 | 1170 | 1239 | 43.21 | 4464.21 | 4319.25 | 144.96 | 4500 | 5.74 | 76.41 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-15:51 to 18:00 | 26100997 | 798
2016-04-07 | 882 | 1068 | 1114 | 1150 | 41.05 | 4255.05 | 4060.5 | 194.55 | 4280 | 5.87 | 71.06 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-10:20 to 11:24 & 16:43 to 17:02 | 26101088 | 546
2016-04-08 | 1097 | 1374 | 1351 | 1391 | 50.55 | 5263.55 | 5053.5 | 210.05 | 5270 | 6.71 | 76.54 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498
2016-04-09 | 1085 | 1346 | 1323 | 1371 | 51.5 | 5176.5 | 4937.25 | 239.25 | 5190 | 6.7 | 75.49 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-13:00 to 13:06 & D.O Fuse of "Y" phase blown at 17:18 pm, Fuse was replaced and plant started at 17:55 | 26108015 26110490 | 630
2016-04-10 | 1119 | 1305 | 1283 | 1323 | 50.5 | 5080.5 | 4853.25 | 227.25 | 5090 | 6.52 | 76.08 | Grid Failure From-07:25 to 07:38 | 26110549
2016-04-11 | 1227 | 1397 | 1368 | 1416 | 51.77 | 5459.77 | 5233.5 | 226.27 | 5460 | 6.87 | 77.46 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-17:58 to 19:24 |  | 594
2016-04-12 | 1159 | 1300 | 1278 | 1342 | 47.89 | 5126.89 | 4905 | 221.89 | 5150 | 6.55 | 76.63 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-04-13 | 1182 | 1323 | 1300 | 1393 | 49.32 | 5247.32 | 5037.75 | 209.57 | 5250 | 6.76 | 75.69 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-04-14 | 1181 | 1317 | 1295 | 1425 | 49.73 | 5267.73 | 4986 | 281.73 | 5280 | 6.74 | 76.35 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-04-15 | 1176 | 1323 | 1311 | 1444 | 51.76 | 5305.76 | 5133.75 | 172.01 | 5312 | 6.75 | 76.7% | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & L.T. Panal P.M |  | 798
2016-04-16 | 1114 | 1244 | 1267 | 1348 | 49.03 | 5022.03 | 4794.75 | 227.28 | 5030 | 6.45 | 76.01% | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-04-17 | 1063 | 1176 | 1215 | 1289 | 46.48 | 4789.48 | 4574.25 | 215.23 | 4822 | 6.13 | 76.67% | Grid Failure From- 13:26 to 13:33 & 13:40 & 13:49 & 16:10 to 16:15 | 26126850
2016-04-18 | 1097 | 1272 | 1295 | 1365 | 48.97 | 5077.97 | 4866.75 | 211.22 | 5100 | 6.39 | 77.79% | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-08:52 to 9:05 | 26126929 | 498
2016-04-19 | 1136 | 1340 | 1328 | 1391 | 50.41 | 5245.41 | 5025.75 | 219.66 | 5263 | 6.58 | 77.96% | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630
2016-04-20 | 1159 | 1345 | 1318 | 1377 | 49.97 | 5248.97 | 5031.75 | 217.22 | 5253 | 6.47 | 79.13% | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594
2016-04-21 | 1232 | 1397 | 1339 | 1433 | 52.55 | 5453.55 | 5220 | 233.55 | 5463 | 6.99 | 76.17% | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-04-22 | 1210 | 1362 | 1318 | 1432 | 51.81 | 5373.81 | 5139.75 | 234.06 | 5400 | 6.11 | 86.14% | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756
2016-04-23 | 1125 | 1261 | 1210 | 1344 | 47.01 | 4987.01 | 4778.25 | 208.76 | 5000 | 6.5 | 74.97% | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-17:17 to 17:27 | 26139894 | 777
2016-04-24 | 1137 | 1278 | 1226 | 1369 | 47.48 | 5057.48 | 4828.5 | 228.98 | 5060 | 6.57 | 75.07%
2016-04-25 | 983 | 1096 | 1069 | 1173 | 43.2 | 4364.2 | 4178.25 | 185.95 | 4390 | 5.87 | 72.89% | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-09:22 to 09:32 | 26144105 | 798
2016-04-26 | 645 | 713 | 695 | 762 | 25.64 | 2840.64 | 2684.25 | 156.39 | 2870 | 3.6 | 77.7% | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-04-27 | 1142 | 1300 | 1212 | 1409 | 52.5 | 5115.5 | 4977.75 | 137.75 | 5230 | 6.77 | 75.29% | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Grid Failure From-09:40 to 09:45 | 26146070 | 498
2016-04-28 | 1079 | 1238 | 1372 | 1323 | 49.13 | 5061.13 | 4758 | 303.13 | 4990 | 6.5 | 74.82% | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-17:10 to 17:53 & Today I Replaced The D.C.12Amp Fuse Link of The String- 05++tive in AJB-117 of The Inverter-3 during The Period of 10:35 To 10:40 | 26147097 26147351 | 630
2016-04-29 | 1086 | 1283 | 1283 | 1298 | 49.3 | 4999.3 | 4803 | 196.3 | 5004 | 6.55 | 74.46% | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Today I Replaced The D.C.12Amp Fuse Link of The String- 01--tive in AJB-101 of The Inverter-1 during The Period of 18:35 To 18:40 |  | 594
2016-04-30 | 1102 | 1295 | 1266 | 1294 | 49.18 | 5006.18 | 4779 | 227.18 | 5012 | 6.61 | 73.9% | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-05-01 | 1108 | 1278 | 1260 | 1297 | 48.71 | 4991.71 | 4782 | 209.71 | 5010 | 6.57 | 74.32%
2016-05-02 | 922 | 1080 | 1065 | 1090 | 37 | 4194 | 3991.5 | 202.5 | 4210 | 5.65 | 72.63% | Module clean by Rain & Grid Failure From-17:55 to 22:20 | 26160730
2016-05-03 | 1010 | 1300 | 1290 | 1350 | 50.37 | 5000.37 | 4831.5 | 168.87 | 5014 | 6.93 | 70.52% | Inverter No-1 ABB (250 KW) Morning time not wake up Err code- (8189) D.C. Bracker off Inverter started 09:15 & Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 | 26160727 | 630
2016-05-04 | 945 | 1052 | 1051 | 1118 | 40.14 | 4206.14 | 4005.75 | 200.39 | 4220 | 5.58 | 73.71% | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-17:55 to 18:05 |  | 594
2016-05-05 | 887 | 995 | 989 | 1020 | 38.12 | 3929.12 | 3747.75 | 181.37 | 3950 | 5.56 | 69.24% | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-05-06 | 1012 | 1136 | 1131 | 1264 | 45.37 | 4588.37 | 4426.5 | 161.87 | 4610 | 6.44 | 69.77% | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-14:37 to 14:42 |  | 756
2016-05-07 | 989 | 1109 | 1108 | 1253 | 43.13 | 4502.13 | 4293.75 | 208.38 | 4523 | 6.13 | 71.91% | Grid Failure From-17:27 to 17:43 & Today I Replaced The D.C.12Amp Fuse Link of The String- 04--tive in AJB-105 of The Inverter-4 during The Period of 10:10 To 10:15 | 26175697 26169117
2016-05-08 | 967 | 1085 | 1074 | 1242 | 43.1 | 4411.1 | 4206 | 205.1 | 4440 | 6.3 | 0.6869 | Grid Failure From-08:47 to 09:14 | 26175729
2016-05-09 | 984 | 1108 | 1103 | 1236 | 43.69 | 4474.69 | 4330.5 | 144.19 | 4530 | 6.29 | 70.19% | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-17:35 to 17:45 | 26178351 | 777
2016-05-10 | 989 | 1108 | 1102 | 1295 | 46.86 | 4540.86 | 4329.75 | 211.11 | 4560 | 6.28 | 70.77% | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798
2016-05-11 | 1001 | 1131 | 1182 | 1317 | 48.15 | 4679.15 | 4482.75 | 196.4 | 4691 | 6.34 | 72.12% | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546
2016-05-12 | 1012 | 1142 | 1261 | 1325 | 48.83 | 4788.83 | 4581.75 | 207.08 | 4800 | 6.44 | 72.65% | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 |  | 498
2016-05-13 | 1023 | 1210 | 1288 | 1330 | 50.31 | 4901.31 | 4713 | 188.31 | 4910 | 6.51 | 73.51% | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630
2016-05-14 | 1063 | 1283 | 1307 | 1372 | 51.11 | 5076.11 | 4850.25 | 225.86 |  |  |  | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594
2016-05-15 | 1029 | 1283 | 1272 | 1334 | 49.7 | 4967.7 | 4760.25 | 207.45 |  |  |  | Grid Failure From -12:43 to 12:52 | 26187259
2016-05-16 | 1029 | 1272 | 1260 | 1321 | 48.55 | 4930.55 | 4723.5 | 207.05 |  |  |  | no module cleaning & No any issue
2016-05-17 | 1046 | 1227 | 1216 | 1269 | 46.7 | 4804.7 | 4568.25 | 236.45 |  |  |  | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612
2016-05-18 | 1108 | 1221 | 1209 | 1263 | 46.94 | 4847.94 | 4671.75 | 176.19 |  |  |  | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Array P.M (750 kw PolyCrystallin side) |  | 756
2016-05-19 | 1108 | 1215 | 1199 | 1284 | 46.36 | 4852.36 | 4600.5 | 251.86 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Array P.M (250 Kw Thinfilm side) |  | 777
2016-05-20 | 1103 | 1210 | 1199 | 1320 | 45.86 | 4877.86 | 4689 | 188.86 |  |  |  | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Combiner P.M (750 kw PolyCrystallin side) |  | 798
2016-05-21 | 955 | 1035 | 1023 | 1173 | 40.77 | 4226.77 | 4044 | 182.77 |  |  |  | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-14:55 to 16:21 & Combiner P.M (250 Kw Thinfilm side) | 26201454 | 546
2016-05-22 | 933 | 1012 | 1012 | 1140 | 41.43 | 4138.43 | 3957.75 | 180.68 |  |  |  | Grid Failure From-10:32 to 10:41 & 14:15 to 14:55 | 26201531 26201620
2016-05-23 | 1085 | 1193 | 1210 | 1325 | 50.71 | 4863.71 | 4670 | 193.71 |  |  |  | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Grid Failure From-16:28 to 10:35 | 26203336 | 498
2016-05-24 | 1041 | 1159 | 1204 | 1281 | 48.31 | 4733.31 | 4514.25 | 219.06 | 4740 |  |  | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Cloudy day |  | 630
2016-05-25 | 938 | 1080 | 1085 | 1140 | 42.28 | 4285.28 | 4093.5 | 191.78 | 4300 | 5.67 | 73.92% | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Cloudy day |  | 594
2016-05-26 | 905 | 1012 | 1012 | 1060 | 40.04 | 4029.04 | 3846 | 183.04 | 4050 | 5.5 | 71.77% | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Grid Failure From-12:54 to 13:08 & Cloudy day | 26213053 | 612
2016-05-27 | 983 | 1096 | 1091 | 1191 | 46.14 | 4407.14 | 4201.5 | 205.64 | 4420 | 6.44 | 66.89% | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From- 12:25 to 12:55 & Cloudy day | 26213473 | 756
2016-05-28 | 990 | 1103 | 1097 | 1177 | 44.57 | 4411.57 | 4206 | 205.57 | 4420 | 6 | 71.8% | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Cloudy day |  | 777
2016-05-29 | 1023 | 1136 | 1136 | 1220 | 47.08 | 4562.08 | 4363.5 | 198.58 | 4571 | 6.2 | 71.86% | Cloudy day
2006-05-30 | 1063 | 1182 | 1193 | 1293 | 52.67 | 4783.67 | 4586.25 | 197.42 | 4794 | 6.48 | 72.11% | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Cloudy day |  | 798
2016-05-31 | 1028 | 1159 | 1188 | 1258 | 52.37 | 4685.37 | 4465.5 | 219.87 | 4690 | 6.34 | 72.1% | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Cloudy day |  | 546
2016-06-01 | 1086 | 1215 | 1243 | 1335 | 55.69 | 4934.69 | 4719.75 | 214.94 | 4951 | 6.67 | 72.35%
2016-06-02 | 1063 | 1193 | 1216 | 1303 | 54.13 | 4829.13 | 4645.5 | 183.63 | 4860 | 6.59 | 71.88% | Grid Failure From-17:28 to 17:33 | 26228906
2016-06-03 | 1097 | 1249 | 1272 | 1348 | 56.68 | 5022.68 | 4809.75 | 212.93 | 5020 | 6.75 | 72.49% | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 |  | 498
2016-06-04 | 1097 | 1278 | 1260 | 1348 | 64.63 | 5047.63 | 4860.75 | 186.88 | 5080 | 6.85 | 72.28% | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-15:26 to 15:31 | 26236085 | 630
2016-06-05 | 1102 | 1289 | 1273 | 1337 | 64.04 | 5065.04 | 4821 | 244.04 | 5050 | 6.82 | 72.17%
2016-06-06 | 1097 | 1272 | 1249 | 1317 | 64.13 | 4999.13 | 4806 | 193.13 | 5011 | 6.66 | 73.33% | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594
2016-06-07 | 831 | 922 | 746 | 967 | 49.18 | 3515.18 | 3378.75 | 136.43 | 3540 | 5.71 | 60.43% | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Grid Failure From-09:55 to 11:58 & Inverter No- 3 morning time not wake up Reset Err code (Emergency stop) Inverter started 9:30 | 26237681 26237680 | 612
2016-06-08 | 864 | 994 | 967 | 1089 | 44.94 | 3958.94 | 3747.75 | 211.19 | 3980 | 5.35 | 72.51% | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From- 07:00 to 10:05 | 26239070 | 765
2016-06-09 | 1063 | 1176 | 1159 | 1299 | 52.43 | 4749.43 | 4552.5 | 196.93 | 4751 | 6.33 | 73.15% | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777
2016-06-10 | 752 | 843 | 825 | 930 | 30.92 | 3380.92 | 3231 | 149.92 | 3400 | 4.58 | 72.35% | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Cloudy day & Grid Failure From-06:53 to 07:55 | 26241421 | 798
2016-06-11 | 780 | 859 | 876 | 936 | 33.16 | 3484.16 | 3333 | 151.16 | 3520 | 4.63 | 74.1% | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Cloudy day & Grid Failure From-13:10 to 13:24 | 26246410 | 546
2016-06-12 | 996 | 1108 | 1137 | 1180 | 46.25 | 4467.25 | 4297.5 | 169.75 | 4481 | 5.91 | 73.9% | Grid Failure From-14:20 to 14:27 & Cloudy day | 26247134
2016-06-13 | 943 | 1052 | 1080 | 1117 | 43.45 | 4235.45 | 4004.25 | 231.2 | 4250 | 5.57 | 74.37% | Cloudy day
2016-06-14 | 803 | 898 | 893 | 937 | 33.41 | 3564.41 | 3422.25 | 142.16 | 3600 | 4.64 | 75.62% | Cloudy day
2016-06-15 | 961 | 1086 | 1074 | 1108 | 42.74 | 4271.74 | 4060.5 | 211.24 | 4280 | 5.55 | 75.16% | Cloudy day
2016-06-16 | 945 | 1063 | 1052 | 1071 | 37.36 | 4168.36 | 3859.5 | 308.86 | 4190 | 5.4 | 75.63% | Cloudy day
2016-06-17 | 961 | 1085 | 1074 | 1108 | 41.87 | 4269.87 | 4083 | 186.87 | 4270 | 5.55 | 74.99% | Cloudy day
2016-06-18 | 1045 | 1187 | 1181 | 1216 | 47.29 | 4676.29 | 4470 | 206.29 | 4690 | 6.09 | 75.06% | Cloudy day
2016-06-19 | 543 | 605 | 594 | 602 | 17.89 | 2361.89 | 2218.5 | 143.39 | 2390 | 3.08 | 75.63% | Cloudy day
2016-06-20 | 820 | 911 | 916 | 959 | 29.14 | 3635.14 | 3501 | 134.14 | 3640 | 4.77 | 74.38% | Grid Failure From-15:48 to 16:10 & Cloudy day | 26285676
2016-06-21 | 447 | 491 | 446 | 506 | 15.2 | 1905.2 | 1858 | 47.2 | 1940 | 2.61 | 72.45% | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & ,A,B,C,D,E,F, & Total module cleaning -1158 & Grid Failure From-09:45 to 13:10 & Cloudy day | 26285801 | 1158
2016-06-22 | 164 | 181 | 170 | 215 | 5.9 | 735.9 | 679.5 | 56.4 | 805 | 1.1 | 71.33% | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-07:45 to 13:45 & 15:35 to 15:40 & 16:48 to 16:54 & Cloudy day | 26286960 26290185 | 594
2011-06-23 | 887 | 990 | 989 | 1051 | 33.14 | 3950.14 | 3613.5 | 336.64 | 3960 | 4.6 | 83.91% | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Cloudy day |  | 612
2016-06-24 | 860 | 961 | 973 | 1026 | 29.09 | 3849.09 | 3841.5 | 7.59 | 3870 | 4.5 | 83.82% | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Cloudy day |  | 756
2016-06-25 | 859 | 961 | 961 | 1021 | 31.37 | 3833.37 | 3632.25 | 201.12 | 3840 | 4.4 | 85.0611 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Cloudy day |  | 777
2016-06-26 | 814 | 904 | 898 | 936 | 28.5 | 3580.5 | 3411.75 | 168.75 |  |  |  | Cloudy day
2016-06-27 | 938 | 1046 | 1041 | 1081 | 30.4 | 4136.4 | 3948.75 | 187.65 |  |  |  | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Cloudy day |  | 798
2016-06-28 | 928 | 1029 | 1023 | 1116 | 33.09 | 4129.09 | 3960 | 169.09 |  |  |  | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Cloudy day & Grid Failure From-18:10 to 18:27 |  | 546
2016-06-29 | 469 | 515 | 515 | 536 | 14.46 | 2049.46 | 1975.5 | 73.96 |  |  |  | Module cleaning By Rain & Grid Failure From-13:20 to 13:42 | 26312420
2016-06-30 | 582 | 633 | 633 | 655 | 17.92 | 2520.92 | 2324.25 | 196.67 |  |  |  | Module cleaning done inverter - 4 Row- A,B,C,D,E,F, & Total module cleaning -792 & Grid Failure From-17:43 to 17:50 & Cloudy day | 26312801 | 792
2016-07-01 | 803 | 887 | 882 | 957 | 29.42 | 3558.42 | 3445.5 | 112.92 |  |  |  | Cloudy day & Grid Failure From-16:42 to 16:45
2016-07-02 | 616 | 673 | 667 | 724 | 21.3 | 2701.3 | 2519.25 | 182.05 |  |  |  | Module cleaning By Rain & Grid Failure From-11:40 to 12:25 | 26340427
2016-07-03 | 769 | 860 | 848 | 914 | 28.11 | 3419.11 | 3290.25 | 128.86 |  |  |  | Module cleaning By Rain & Grid Failure From-16:53 to 18:03 |  | 26321795
2016-07-04 | 147 | 158 | 164 | 182 | 4.78 | 655.78 | 580.5 | 75.28 |  |  |  | Module cleaning By Rain & Grid Failure From-10:26 to 11:22 & 11:40 to 13:20 & 15:00 to 16:42 | 26321972 26322069 26322087
2016-07-05 | 983 | 1096 | 1096 | 1151 | 33.23 | 4359.23 | 4129.5 | 229.73 |  |  |  | Module cleaning By Rain
2016-07-06 | 888 | 984 | 984 | 1025 | 29.51 | 3910.51 | 3729 | 181.51 |  |  |  | Module cleaning By Rain
2016-07-07 | 786 | 871 | 871 | 897 | 27.33 | 3452.33 | 3311.25 | 141.08 |  |  |  | Cloudy day
2016-07-08 | 729 | 808 | 808 | 835 | 25.33 | 3205.33 | 3032.25 | 173.08 |  |  |  | Module cleaning By Rain
2016-07-09 | 441 | 469 | 475 | 482 | 13.55 | 1880.55 | 1762.5 | 118.05 |  |  |  | Cloudy day
2016-07-10 | 447 | 492 | 486 | 500 | 14.01 | 1939.01 | 1807.5 | 131.51 |  |  |  | Cloudy day
2016-07-11 | 599 | 650 | 656 | 678 | 19.37 | 2602.37 | 2465.25 | 137.12 |  |  |  | Module cleaning By Rain & Today I Replaced The D.C.12Amp Fuse Link of The String- 07++tive in AJB-100 of The Inverter-4 during The Period of 10:00 To 10:10 | 26333796
2016-07-12 | 226 | 244 | 243 | 232 | 6.14 | 951.14 | 833 | 118.14 |  |  |  | Module cleaning By Rain & Grid Failure From-12:44 to 12:53 | 26335963
2016-07-13 | 272 | 294 | 283 | 0 | 8.02 | 857.02 | 738.75 | 118.27 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217
2016-07-14 | 814 | 910 | 876 | 0 | 23.64 | 2623.64 | 2484.75 | 138.89 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217
2016-07-15 | 814 | 921 | 922 | 0 | 26.99 | 2683.99 | 2533.5 | 150.49 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217
2016-07-16 | 548 | 605 | 610 | 0 | 17.93 | 1780.93 | 1675.5 | 105.43 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-17:53 to 18:03 | 26336217 26339370
2016-07-17 | 600 | 667 | 515 | 0 | 21.22 | 1803.22 | 1703.25 | 99.97 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-12:13 to 12:28 & 17:40 to 17:50 & Inverter no-3 ABB 250KW Auto trip 14:25 Err code D14 ALM (108A) Reset Err code Inverter started-15:08 | 26336217 26343266 26343722 26344456
2016-07-18 | 785 | 865 | 865 | 0 | 27.63 | 2542.63 | 2380 | 162.63 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-17:25 to 17:35 | 26336217 26347162
2016-07-19 | 645 | 701 | 611 | 0 | 22.02 | 1979.02 | 1964 | 15.02 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:02 Err code D14 ALM (108A) Reset Err code Inverter started-13:50 | 26336217
2016-07-20 | 798 | 877 | 972 | 0 | 28.34 | 2675.34 | 2410 | 265.34 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217
2016-07-21 | 745 | 814 | 814 | 0 | 25.87 | 2398.87 | 2267 | 131.87 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-09:59 to 10:32 | 26336217 26350357
2016-07-22 | 854 | 944 | 949 | 0 | 30.83 | 2777.83 | 2680 | 97.83 |  |  |  | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-06:15 to 06:25 & 14:15 to 14:20 | 26336217 26350606
2016-07-23 | 944 | 1046 | 1029 | 0 | 33.55 | 3052.55 | 2900 | 152.55 |  |  |  | Cloudy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:30 Err code D14 ALM (108A) Reset Err code Inverter started-13:45 & Grid Failure From-18:38 to 19:25 | 26336217 26351121 26354403
2016-07-24 | 791 | 876 | 882 | 0 | 28.46 | 2577.46 | 2474 | 103.46 |  |  |  | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217
2016-07-25 | 368 | 390 | 390 | 0 | 11.27 | 1159.27 | 1043 | 116.27 |  |  |  | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-10:44 to 10:55 | 26336217 26358319
2016-07-26 | 752 | 831 | 803 | 0 | 26.26 | 2412.26 | 2274 | 138.26 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:30 Err code D14 ALM (108A) Reset Err code Inverter started-13:45 | 26336217 26364369
2016-07-27 | 379 | 390 | 407 | 0 | 12.24 | 1188.24 | 1105.5 | 82.74 |  |  |  | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217
2016-07-28 | 407 | 441 | 221 | 0 | 12.59 | 1081.59 | 963 | 118.59 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:30 Err code D14 ALM (108A) Inverter steel sut Down | 26336217
2016-07-29 | 644 | 701 | 333 | 0 | 21.86 | 1699.86 | 1585.5 | 114.36 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Morning time wake up & than Auto trip 13:30 Err code D14 ALM (108A) Inverter steel sut Down & Transformer P.M | 26336217
2016-07-30 | 780 | 865 | 0 | 0 | 26.73 | 1671.73 | 1552.5 | 119.23 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip Err code D14 ALM (108A) Inverter steel sut Down & Inverters Filter cleaning (1,2,3,4,) | 26336217
2016-07-31 | 729 | 803 | 764 | 0 | 24.82 | 2320.82 | 2210 | 110.82 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW By Pass Inverter realy morning time Auto start Resolve Err code D14 ALM (108A) | 26336217
2016-08-01 | 747 | 815 | 808 | 0 | 25.02 | 2395.02 | 2262.75 | 132.27 | 2345 | 3.9 | 58.6045 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-15:45 to 16:19 | 26336217 26376332
2016-08-02 | 441 | 474 | 486 | 0 | 14.04 | 1415.04 | 1314.75 | 100.29 | 1440 | 1.56 | 89.97% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-03 | 265 | 283 | 294 | 0 | 7.71 | 849.71 | 739.5 | 110.21 | 865 | 0.999 | 84.39% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-04 | 781 | 859 | 871 | 0 | 28.56 | 2539.56 | 2403 | 136.56 | 2584 | 4.1 | 61.4273 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-05 | 650 | 712 | 729 | 0 | 21.8 | 2112.8 | 2017.5 | 95.3 | 2142 | 3.86 | 54.09% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:40 to 15:50 WO# | 26336217 26380329
2016-08-06 | 282 | 300 | 311 | 0 | 8.7 | 901.7 | 840 | 61.7 | 930 | 1.57 | 57.73% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:15 to 16:37 WO# | 26336217 26386258
2016-08-07 | 374 | 401 | 413 | 0 | 11.77 | 1199.77 | 1088.25 | 111.52 | 1211 | 2 | 59.02% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-08 | 288 | 317 | 322 | 0 | 9.15 | 936.15 | 846.75 | 89.4 | 985 | 1.32 | 72.73% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:30 to 08:50 WO# | 26336217 26389343
2016-08-09 | 305 | 328 | 333 | 0 | 9.33 | 975.33 | 873.75 | 101.58 | 984 | 1.31 | 73.21% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-10 | 221 | 240 | 244 | 0 | 6.7 | 711.7 | 624 | 87.7 | 755 | 1.29 | 57.04% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From- 11:07 to 11:10 WO# | 26336217 26394284
2016-08-11 | 379 | 415 | 435 | 0 | 13.16 | 1242.16 | 1159.5 | 82.66 | 1295 | 2.3 | 54.88% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-09:30 to 09:55 & 16:10 to 16:40 WO# | 26336217 26394870 26394898
2016-08-12 | 638 | 702 | 718 | 0 | 22.54 | 2080.54 | 1965 | 115.54 | 2102 | 3.66 | 55.98% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-10:27 to 10:36 WO# | 26336217 26394967
2016-08-13 | 752 | 825 | 842 | 0 | 26.7 | 2445.7 | 2301.75 | 143.95 | 2455 | 4.24 | 56.43% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:26 to 16:33 WO# | 26336217 26399788
2016-08-14 | 933 | 1034 | 1052 | 0 | 35.42 | 3054.42 | 2918.25 | 136.17 | 3064 | 5.29 | 56.45% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & G.O.D, Swich ,B, Phase Luge rusted so Replace New Luge | 26336217
2016-08-15 | 769 | 854 | 859 | 0 | 26.88 | 2508.88 | 2383.5 | 125.38 | 2520 | 4.47 | 54.95% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Today I Replaced The D.C.12Amp Fuse Link of The String- 05---tive in AJB-107 of The Inverter-2 during The Period of 10:00 To 10:05 | 26336217 26400127
2016-08-16 | 729 | 814 | 809 | 0 | 26.4 | 2378.4 | 2270.25 | 108.15 | 2413 | 4.21 | 55.86% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:38 to 16:48 & 17:35 to 17:40 WO# | 26336217 26407752 26407754
2016-08-17 | 916 | 1029 | 1028 | 0 | 33.63 | 3006.63 | 2862.75 | 143.88 | 3043 | 5.52 | 53.73% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-18 | 933 | 1052 | 1052 | 0 | 34.43 | 3071.43 | 2928.75 | 142.68 | 3093 | 5.67 | 53.17% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:25 to 15:36 WO# | 26336217
2016-08-19 | 548 | 610 | 611 | 0 | 19.64 | 1788.64 | 1694.25 | 94.39 | 1822 | 3.1 | 57.28% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-20 | 249 | 272 | 277 | 0 | 7.77 | 805.77 | 717 | 88.77 | 835 | 1.42 | 57.31% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:22 to 16:28 WO# & Combiner P.M | 26336217 26413413
2016-08-21 | 322 | 361 | 367 | 0 | 10.8 | 1060.8 | 978 | 82.8 | 1100 | 1.85 | 57.95% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:44 to 07:52 WO# & SEEDS P.M | 26336217 26413466
2016-08-22 | 520 | 577 | 582 | 0 | 18.57 | 1697.57 | 1595 | 102.57 | 1731 | 3 | 56.24% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:58 to 08:11 & 18:06 to 18:24 WO# | 26336217 26413842 26414448
2016-08-23 | 159 | 181 | 181 | 0 | 4.88 | 525.88 | 455.25 | 70.63 | 558 | 0.981 | 55.44% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-24 | 294 | 333 | 340 | 0 | 9.32 | 976.32 | 873 | 103.32 | 996 | 1.64 | 59.19% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-25 | 407 | 481 | 480 | 0 | 16.16 | 1384.16 | 1280 | 104.16 | 1422 | 2.49 | 55.66% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-26 | 554 | 616 | 622 | 0 | 18.03 | 1810.03 | 1682.25 | 127.78 | 1833 | 3.15 | 56.72% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-27 | 825 | 939 | 927 | 0 | 30.29 | 2721.29 | 2566.5 | 154.79 | 2733 | 5.01 | 53.17% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-08-28 | 464 | 526 | 532 | 0 | 16.98 | 1538.98 | 1443 | 95.98 | 1562 | 2.78 | 54.76% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-12:28 to 13:28 WO# | 26336217 26431636
2016-08-29 | 627 | 706 | 706 | 0 | 21.57 | 2060.57 | 1961.25 | 99.32 | 2093 | 3.5 | 58.28% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-12:58 to 13:05 WO# | 26336217 26431958
2018-08-30 | 436 | 499 | 492 | 0 | 17.24 | 1444.24 | 1360 | 84.24 | 1492 | 2.8 | 51.94% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-10:22 to 10:59 & 13:59 to 15:48 WO# | 26336217 26433094 26435469
2016-08-31 | 548 | 616 | 616 | 0 | 19.03 | 1799.03 | 1679.25 | 119.78 | 1822 | 3.11 | 57.1% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-01 | 701 | 792 | 792 | 0 | 26.2 | 2311.2 | 2194 | 117.2 | 2341 | 4.05 | 56.34% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-02 | 808 | 915 | 910 | 0 | 30 | 2663 | 2509.5 | 153.5 | 2672 | 4.81 | 54.14% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-03 | 1018 | 1148 | 803 | 0 | 38.21 | 3007.21 | 2873.25 | 133.96 | 3030 | 6.2 | 47.63% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Inverter No-3 ABB 250 KW Morning time note wake up Err code- Emergency stop satemaster Relay By pass Inverter started 11:25 WO# | 26336217 26440841
2016-09-04 | 1012 | 1136 | 1136 | 0 | 38.49 | 3322.49 | 3173.25 | 149.24 | 3342 | 6.12 | 53.22% | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:20 to 15:30 WO# | 26336217 26445915
2016-09-05 | 910 | 1029 | 1023 | 0 | 34.71 | 2996.71 | 2853 | 143.71 | 3010 | 5.5 | 53.34% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-06 | 809 | 910 | 911 | 0 | 39.41 | 2669.41 | 2559 | 110.41 | 2688 | 4.98 | 52.61% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:33 to 09:12 & 17:15 to 17:49 & 18:10 to 18:17 WO# | 26336217 26446442 26449700 26449709
2016-09-07 | 819 | 922 | 910 | 0 | 32.29 | 2683.29 | 2560.5 | 122.79 | 2694 | 4.89 | 53.7% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-13:26 to 14:11 & 15:12 to 15:21 WO# | 26336217 26450567
2016-09-08 | 950 | 1080 | 1074 | 0 | 34.87 | 3138.87 | 3000 | 138.87 | 3150 | 5.7 | 53.86% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-09 | 996 | 1136 | 1125 | 0 | 37.17 | 3294.17 | 3154.5 | 139.67 | 3320 | 6.12 | 52.87% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:53 to 17:01 WO# | 26336217 26453610
2016-09-10 | 887 | 1001 | 1001 | 0 | 32.47 | 2921.47 | 2791.5 | 129.97 | 2941 | 5.39 | 53.18% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-11 | 966 | 1085 | 1068 | 0 | 35.44 | 3154.44 | 3005.25 | 149.19 | 3160 | 5.94 | 51.85% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-12 | 967 | 1086 | 1086 | 0 | 37.48 | 3176.48 | 3029.25 | 147.23 | 3192 | 5.99 | 51.94% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-13 | 1040 | 1179 | 1193 | 0 | 38.91 | 3450.91 | 3294 | 156.91 | 3462 | 6.41 | 52.64% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-14 | 1041 | 1184 | 1187 | 0 | 39.52 | 3451.52 | 3300.75 | 150.77 | 3465 | 6.4 | 52.77% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-15 | 983 | 1119 | 1119 | 0 | 38.39 | 3259.39 | 3126 | 133.39 | 3302 | 6.19 | 51.99% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-11:50 to 11:56 & 13:16 to 13:25 & 16:00 to 16:12 WO# | 26336217 26460513 26466933 26469676
2016-09-16 | 741 | 814 | 837 | 0 | 29.13 | 2421.13 | 2332.5 | 88.63 | 2662 | 4.54 | 57.15% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-10:08 to 10:17 & 12:58 to 13:07 WO# | 26336217 26469738 26472264
2016-09-17 | 786 | 865 | 887 | 0 | 30.86 | 2568.86 | 2464.5 | 104.36 | 2582 | 4.8 | 52.43% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-09:05 to 09:10 WO# | 26336217 26472456
2016-09-18 | 327 | 356 | 362 | 0 | 10.67 | 1055.67 | 988.5 | 67.17 | 1102 | 1.86 | 57.75% | Today I Replaced The D.C.12Amp Fuse Link of The String-08++tive in AJB-108 of The Inverter-2 during The Period of 11:00 To 11:10 & Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:37 to 07:42 & 16:20 to 16:37 & 18:10 to 18:30 WO# | 26336217 26476746 26476871 26476897 26476906
2016-09-19 | 555 | 617 | 616 | 0 | 19.23 | 1807.23 | 1698 | 109.23 | 1832 | 3.15 | 56.68% | Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:18 to 07:23 WO# | 26336217 26476946
2016-09-20 | 983 | 1113 | 1108 | 0 | 37.45 | 3241.45 | 3109.5 | 131.95 | 3272 | 5.86 | 54.42% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:20 to 08:25 WO# | 26336217 26477125
2016-09-21 | 911 | 1035 | 1040 | 0 | 35.98 | 3021.98 | 2903.25 | 118.73 | 3062 | 6.14 | 48.61% | Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure (Low voltage)From-08:03 to 08:08 & 11:06 to 12:10 & 16:44 to 16:49 WO# | 26336217 26478142 26478240 26479500
2016-09-22 | 401 | 441 | 453 | 0 | 10.34 | 1305.34 | 1226.25 | 79.09 | 1332 | 2.19 | 59.28% | Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-17:28 to 17:33 WO# | 26336217 26481144
2016-09-23 | 1102 | 1261 | 1238 | 0 | 40.85 | 3641.85 | 3493.5 | 148.35 | 3655 | 6.66 | 53.49% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:50 to 08:00 & 11:55 to 12:01 WO# | 26336217 26481238 26481420
2016-09-24 | 1091 | 1243 | 1238 | 0 | 40.95 | 3612.95 | 3459.75 | 153.2 | 3623 | 6.51 | 54.24% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-25 | 1058 | 1205 | 1199 | 0 | 40.97 | 3502.97 | 3338.25 | 164.72 | 3515 | 6.35 | 53.95% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217
2016-09-26 | 1063 | 1209 | 1198 | 0 | 41.11 | 3511.11 | 3387 | 124.11 | 3522 | 6.44 | 53.3% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:36 to 15:41 WO# | 26336217 26490687
2016-09-27 | 1096 | 1278 | 1272 | 0 | 41.79 | 3687.79 | 3532.5 | 155.29 | 3692 | 6.78 | 53.07% | Module cleaning done inverter -3 Row- ,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:25 to 16:30 & 17:45 TO 17:56 WO# | 26336217 26491679 26491670 | 630
2016-09-28 | 1029 | 1210 | 1210 | 0 | 41.46 | 3490.46 | 3366 | 124.46 | 3525 | 6.49 | 52.94% | Module cleaning done inverter -3&2 Row- ,K,L,M,N, & Total module cleaning -987 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:07 to 08:14 & 09:24 TO 09:32 WO# | 26336217 26491735 26491736 | 987
2016-09-29 | 1108 | 1294 | 1283 | 0 | 42.48 | 3727.48 | 3572.25 | 155.23 | 3720 | 6.7 | 54.12% | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:52 to 16:57 WO# | 26336217 26494557 | 798
2016-09-30 | 1001 | 1159 | 1142 | 0 | 38.3 | 3340.3 | 3196.5 | 143.8 | 3485 | 6.5 | 52.26% | Module cleaning done inverter -1 Row- ,A,B,C,D,E,F,G, & Total module cleaning -882 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 | 882
2016-10-01 | 520 | 583 | 588 | 0 | 17.84 | 1708.84 | 1609.5 | 99.34 | 1935 | 3.5 | 53.88% | Module cleaning done inverter -3 Row- ,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day | 26336217 | 630
2016-10-02 | 910 | 1034 | 1035 | 0 | 32.91 | 3011.91 | 2891.25 | 120.66 | 3090 | 4.56 | 66.05% | Today I Replaced The D.C.12Amp Fuse Link of The String-09++tive in AJB-104 of The Inverter-2 during The Period of 11:30 To 11:35 & Rainy & Rainy cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:15 to 08:21 WO# | 26336217 26500713 26500990
2016-10-03 | 741 | 843 | 836 | 0 | 29.24 | 2449.24 | 2447.25 | 1.99 | 2402 | 3.15 | 74.32% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day & Grid Failure From-09:24 to 09:48 & 13:58 to 16:02 WO# | 26336217 26501207 26501213
2016-10-04 | 548 | 610 | 611 | 0 | 20.13 | 1789.13 | 1650 | 139.13 | 1922 | 3.06 | 61.22% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day & Grid Failure From-10:14 to 10:22 WO# | 26336217 26501268
2016-10-05 | 102 | 113 | 113 | 0 | 3.23 | 331.23 | 260.25 | 70.98 | 369 | 0.52 | 69.16% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down, Rainy & cloudy day & Grid Failure From-07:45 to 07:55 & 09:30 to 12:58 WO# | 26336217 26504090
2016-10-06 | 266 | 294 | 300 | 0 | 8.16 | 868.16 | 771 | 97.16 | 892 | 1.47 | 59.14% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down, Rainy & cloudy day | 26336217
2006-10-07 | 706 | 803 | 803 | 0 | 24.52 | 2336.52 | 2216 | 120.52 | 2365 | 4.9 | 47.04% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down, Rainy & cloudy day & Grid Failure From-15:10 to 15:18 WO# | 26336217 26505577
2016-10-08 | 831 | 950 | 961 | 0 | 31.92 | 2773.92 | 2646.75 | 127.17 | 2803 | 5.14 | 53.15% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day & Grid Failure From-15:10 to 15:18 WO# | 26336217 26512433
2016-10-09 | 769 | 870 | 864 | 0 | 29.35 | 2532.35 | 2392.5 | 139.85 | 2550 | 4.65 | 53.45% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day | 26336217
2016-10-10 | 831 | 956 | 956 | 0 | 34.96 | 2777.96 | 2654 | 123.96 | 2810 | 5.17 | 52.97% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day & Grid Failure From-07:33 to 07:41 & 10:28 to 10:33 WO# | 26336217 26512676 26512677
2016-10-11 | 893 | 1012 | 1017 | 0 | 34.43 | 2956.43 | 2837.25 | 119.18 | 3001 | 5.5 | 53.18% | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day & Grid Failure From-09:51 to 09:59 & 17:27 to 17:33 WO# | 26336217 26513009 26514105
2016-10-12 | 1058 | 1210 | 1216 | 0 | 44.01 | 3528.01 | 3381 | 147.01 | 3540 | 6.62 | 52.12% | Module cleaning done inverter -3 Row- ,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day | 26336217 | 630
2016-10-13 | 1034 | 1192 | 1187 | 0 | 39.38 | 3452.38 | 3319.5 | 132.88 | 3470 | 6.39 | 52.93% | Module cleaning done inverter -3&2 Row- ,K,L,M,N, & Total module cleaning -987 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:05 to 07:20 WO# | 26336217 26514435 | 987
2016-10-14 | 995 | 1154 | 1137 | 0 | 38.94 | 3324.94 | 3162.75 | 162.19 | 3350 | 6.06 | 53.88% | Module cleaning done inverter -1&2 Row- ,H,I,J, & Total module cleaning -798 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:06 to 15:26 & 17:30 to 18:03 WO# | 26336217 26515543 26515553 | 798
2006-10-15 | 1040 | 1187 | 1175 | 0 | 39.23 | 3441.23 | 3291 | 150.23 | 3460 | 6.39 | 52.77% | Module cleaning done inverter -1&3 Row-A,B,C,D ,P,Q,R,S,T & Total module cleaning -777 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel shut down & L.T pannel P.M | 26336217 | 777
2016-10-16 | 832 | 939 | 933 | 0 | 32.26 | 2736.26 | 2606.25 | 130.01 | 2760 | 4.96 | 54.24% | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel shut down | 26336217
2006-10-17 | 1007 | 1147 | 1148 | 0 | 38.71 | 3340.71 | 3185.25 | 155.46 | 3347 | 6.15 | 53.04% | Module cleaning done inverter -1&3 Row-,M,N,O, & Total module cleaning -651 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel shut down | 26336217 | 651
2016-10-18 | 859 | 978 | 978 | 165 | 32.22 | 3012.22 | 2875.5 | 136.72 | 3040 | 5.23 | 56.65% | Module cleaning done inverter -4 Row-,A,B,C,D,E,F, & Total module cleaning -792 & Inverter No-4 250 KW Schneider Resolve The issue Replce D.C to D.C CONVERTER & P.C.B Inverter started-15:15 & Grid Faillure From-12:45 to 14:20 WO# | 26525947 | 792
2016-10-19 | 1103 | 1272 | 1266 | 1090 | 41.69 | 4772.69 | 4557 | 215.69 | 4771 | 6.62 | 70.24% | Module cleaning done inverter -4 Row-,G,H,I,J, & Total module cleaning -774 & Inverter No-4 250 KW Schneider Morning time note wakeup Err code-0252 IGBT SWICH Reset Err code Inverter started 08:50 WO# | 26526236 | 774
2016-10-20 | 1085 | 1250 | 1256 | 1080 | 41.82 | 4712.82 | 4488.75 | 224.07 | 4735 | 6.51 | 70.89% | Module cleaning done inverter -4&3 Row-,K,L,&,O,P,Q,R,S,T, & Total module cleaning -918 & Inverter No-4 250 KW Schneider Inverter Auto trip15:50 Err code-0252 IGBT SWICH Reset Err code Inverter started 016:55 & Grid Failure From-06:33 to 06:42 WO# | 26526615 26526614 | 918
2016-10-21 | 1052 | 1221 | 1221 | 996 | 40.92 | 4530.92 | 4314.75 | 216.17 | 4590 | 5.9 | 75.83% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 |  | 714
2016-10-22 | 910 | 1051 | 1045 | 924 | 34.26 | 3964.26 | 3798.75 | 165.51 | 4025 | 6.1 | 64.31% | Module cleaning done inverter -1&2 Row-,I,J,K, & Total module cleaning -840 & Today I Replaced The D.C.12Amp Fuse Link of The String-09--tive in AJB-102 of The Inverter-4 during The Period of 18:15 To 18:20 & Grid Failure From-12:15 to 12:57 & 15:33 to 15:39 & 17:10 to 17:15 WO# | 26533210 26533222 26533225 26533227 | 840
2016-10-23 | 972 | 1108 | 1086 | 885 | 38.09 | 4089.09 | 3885.75 | 203.34 | 4125 | 6.05 | 66.45%
2016-10-24 | 1029 | 1171 | 1159 | 1020 | 40.38 | 4419.38 | 4215 | 204.38 | 4510 | 6.5 | 67.63% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 &Grid Failure From- 16:59 to 17:05 WO# | 26535312 | 777
2016-10-25 | 922 | 1051 | 1040 | 943 | 35.83 | 3991.83 | 3798.75 | 193.08 | 4048 | 5.9 | 66.87% | Module cleaning done inverter -1&4 Row-,A,B,C,D,& A,B,C,D, & Total module cleaning -768 &Grid Failure From- 13:30 to 13:39 WO# | 26539160 | 768
2016-10-26 | 995 | 1131 | 1119 | 1180 | 38.95 | 4463.95 | 4261.5 | 202.45 | 4502 | 6.2 | 70.77% | Module cleaning done inverter -4 Row-,E,F,G,H, & Total module cleaning -756 &Grid Failure From- 16:37 to 16:41 WO# | 26545259 | 756
2016-10-27 | 1051 | 1193 | 1199 | 656 | 40.7 | 4139.7 | 3920.25 | 219.45 | 4152 | 6.36 | 63.63% | Module cleaning done inverter -4 Row-,I,J,K,L,& Trackers & Total module cleaning -726 |  | 726
2016-10-28 | 1046 | 1210 | 1210 | 1108 | 41.41 | 4615.41 | 4394.25 | 221.16 | 4640 | 6.43 | 70.33% | Module cleaning done inverter -3 Row-,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter No-4 250 KW Schneider Auto trip 16:05 Err code-0252 IGBT SWICH Reset Err code But Inverter Not started (Inverter steel sleep mode) WO# | 26545794 | 630
2016-10-29 | 956 | 1108 | 955 | 0 | 38.04 | 3057.04 | 2900 | 157.04 | 3120 | 5.8 | 52.43% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning-714 & Inverter no-3 ABB 250 KW Auto trip 08:05 Err code-(32A6) Net Loss Reset Err code Inverter started-09:35 & Transformer P.M, Grid Failure From-07:55 to 08:05 & 17:25 to 17:40 WO# | 26545789 26545790 26549957 | 714
2016-10-30 | 904 | 1040 | 1024 | 435 | 36.43 | 3439.43 | 3264.75 | 174.68 | 3480 | 5.44 | 62.35% | Grid Failure From-11:55 to 12:03 WO# | 26551194
2016-10-31 | 967 | 1108 | 1091 | 365 | 38.93 | 3569.93 | 3375 | 194.93 | 3600 | 5.87 | 59.77% | Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter started at 13:37 pm & Grid Failure From-09:52 to 10:06 WO# | 26551446 26551254
2016-11-01 | 921 | 1057 | 1040 | 735 | 37.56 | 3790.56 | 3588.75 | 201.81 | 3820 | 5.53 | 67.33% | Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter started at 11:04 am & Grid Failure From-17:30 to 17:38 WO# | 26551988 26554098
2016-11-02 | 854 | 967 | 955 | 25 | 35.34 | 2836.34 | 2681.25 | 155.09 | 2890 | 5.15 | 54.69% | Module cleaning done inverter -1 Row-A,B,C,D,E,F & Total module cleaning -672 & Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter still shut down & Grid Failure From-8:51 to 9:01 & 10:30 to 10:38 & 17:17 to 17:46 WO# | 26554859 26554159 26554164 26554858 | 672
2016-11-03 | 899 | 1017 | 1001 | 270 | 36.58 | 3223.58 | 3057.75 | 165.83 | 3270 | 5.45 | 58.48% | Module cleaning done inverter -3&4 Row-R,S,T,A,B,C,D & Total module cleaning -600 & Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter Start at 11:50 under observation scheider service engineer many time trip after 12:50 inverter stop to still shut down & Grid Failure From-9:57 to 10:14 & 10:55 to 11:08 WO# | 26555226 26554909 26555191 | 600
2016-11-04 | 859 | 967 | 967 | 0 | 34.7 | 2827.7 | 2693.25 | 134.45 | 2880 | 5.1 | 55.04% | Module cleaning done inverter -3 Row-N,O,P,Q & Total module cleaning -672 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-15:01 to 15:13 WO# | 26555226 26555622 | 672
2016-11-05 | 825 | 927 | 933 | 0 | 33.25 | 2718.25 | 2562.75 | 155.5 | 2760 | 4.89 | 55.01% | Module cleaning done inverter -2&3 Row-K,L,M & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-11:13 to 11:26 WO# | 26555226 26555793 | 777
2016-11-06 | 871 | 1001 | 989 | 0 | 35.2 | 2896.2 | 2742.75 | 153.45 | 2930 | 5.21 | 54.81% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down | 26555226
2016-11-07 | 978 | 1131 | 1119 | 0 | 38.58 | 3266.58 | 3108.75 | 157.83 | 3280 | 5.9 | 54.18% | Module cleaning done inverter -1&2 Row-H,I,J & Total module cleaning -798 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-16:00 to 16:13 WO# | 26555226 26561410 | 798
2016-11-08 | 990 | 1119 | 1103 | 0 | 39.12 | 3251.12 | 3105.75 | 145.37 | 3280 | 6.04 | 52.93% | Module cleaning done inverter -1 Row-,A,B,C,D,E,F,G, & Total module cleaning -832 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-08:37 to 09:13 WO# | 26555226 26561463 | 832
2016-11-09 | 1028 | 1170 | 1147 | 0 | 40.17 | 3385.17 | 3226.5 | 158.67 | 3401 | 6.24 | 53.12% | Module cleaning done inverter -4 Row-,A,B,C,D,E,F, & Total module cleaning -792 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 792
2016-11-10 | 1052 | 1193 | 1170 | 0 | 40.55 | 3455.55 | 3282.75 | 172.8 | 3460 | 6.37 | 52.94% | Module cleaning done inverter -4 Row-,G,H,I,J, & Total module cleaning -774 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 774
2016-11-11 | 1012 | 1153 | 1142 |  | 40.77 | 3347.77 | 3192 | 155.77 | 3370 | 6.17 | 53.24% | Module cleaning done inverter -4&3 Row-,K,L,& ,O,P,Q,R,S,T,& Trackers & Total module cleaning -978 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 978
2016-11-12 | 1018 | 1154 | 1165 |  | 40.51 | 3377.51 | 3223.5 | 154.01 | 3409 | 6.1 | 54.47% | Module cleaning done inverter -3&2 Row-L,M,N & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-13:03 to 13:11 WO# | 26555226 26569497 | 714
2016-11-13 | 994 | 1136 | 1142 |  | 40.3 | 3312.3 | 3173.25 | 139.05 | 3340 | 6.12 | 53.19% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-10:14 to 10:17 & 14:50 to 15:03 WO# | 26555226 26569541 26569893
2016-11-14 | 928 | 107 | 1069 |  | 38.42 | 2142.42 | 2033.25 | 109.17 | 2170 | 5.65 | 37.43% | Module cleaning done inverter -2 Row-I,J,K & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW DC Breaker failure Error code (8188) at 9:34 to still shut down & Grid Failure From-7:35 to 7:44 & 9:29 to 9:34 WO# | 26555226 26570188 26570187 26569933 | 840
2016-11-15 | 944 |  | 1096 |  | 39.22 | 2079.22 | 1969.5 | 109.72 | 2090 | 5.8 | 35.12% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW DC Breaker failure Error code (8188) 14/11/16 at 9:34 to still shut down & Grid Failure From-13:26 to 13:32 & Transformer No-2 300kva Padmavahini Filled Aprox 25 Litter oil WO# | 26555226 26570188 26579104 | 777
2016-11-16 | 972 |  | 1091 |  | 39.26 | 2102.26 | 1995 | 107.26 | 2110 | 5.84 | 35.21% | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -654 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW DC Breaker failure Error code (8188) 14/11/16 at 9:34 to still shut down & Grid Failure From-10:00 to 10:04 WO# | 26555226 26570188 26580408 | 654
2016-11-17 | 989 | 1 | 1097 |  | 39.76 | 2126.76 | 2023.5 | 103.26 | 2035 | 5.9 | 33.62% | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW Resolved The Error code (8188) DC Breaker Failure Replased The NEW DC Breaker Than Inverter started 17:40 & Grid Failure From-09:58 to 10:03 WO# | 26555226 26580460 | 702
2016-11-18 | 984 | 1097 | 1103 |  | 39.69 | 3223.69 | 3084 | 139.69 | 3250 | 6.02 | 52.62% | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Trackers & Total module cleaning -924 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-10:36 to 10:42 WO# Array PM | 26555226 26581054 | 924
2016-11-19 | 973 | 1086 | 1085 |  | 39.72 | 3183.72 | 3021 | 162.72 | 3190 | 5.97 | 52.08% | Module cleaning done inverter -3 Row-O,P,Q,R,S,T & Total module cleaning -630 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down WO# | 26555226 | 630
2016-11-20 | 983 | 1102 | 1114 |  | 40.15 | 3239.15 | 3096 | 143.15 | 3270 | 6.11 | 52.16% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-16:12 to 16:22 WO# Combiner PM | 26555226 26587011
2016-11-21 | 944 | 1046 | 1074 |  | 37.3 | 3101.3 | 2941.5 | 159.8 | 3120 | 5.79 | 52.52% | Module cleaning done inverter -2&3 Row-L,M,N & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# Seeds PM | 26555226 | 714
2016-11-22 | 984 | 1114 | 1125 |  | 39.8 | 3262.8 | 3101.25 | 161.55 | 3280 | 6.07 | 52.67% | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 840
2016-11-23 | 989 | 1125 | 1125 |  | 40.07 | 3279.07 | 3119.25 | 159.82 | 3300 | 6.11 | 52.64% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# & All Transformers cap oil & silica Gel Replaced Aprox 4 kg | 26555226 | 777
2016-11-24 | 1024 | 1142 | 1142 |  | 40.75 | 3348.75 | 3180 | 168.75 | 3368 | 6.29 | 52.19% | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 624
2016-11-25 | 1023 | 1147 | 1148 |  | 41.04 | 3359.04 | 3211.5 | 147.54 | 3390 | 6.42 | 51.47% | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-16:24 to 16:30 WO# | 26555226 | 702
2016-11-26 | 1001 | 1108 | 1113 |  | 39.84 | 3261.84 | 3104.25 | 157.59 | 3280 | 6.19 | 51.65% | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-08:23 to 08:42 WO# | 26555226 26595999 | 864
2016-11-27 | 1017 | 1131 | 1131 |  | 40.78 | 3319.78 | 3171 | 148.78 | 3330 | 6.37 | 50.95% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226
2016-11-28 | 1018 | 1136 | 1136 |  | 41.35 | 3331.35 | 3164.25 | 167.1 | 3354 | 6.38 | 51.24% | Module cleaning done inverter -3 Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Today 1 Module Del solar 230 watts Replaced as a 1`nd From Lower Last of The `T` Row,String-8 AJB-117 (OLD Module Sr.no-PB10B071470175) NEW MODULE-PB10B068470104 WO# | 26555226 | 690
2016-11-29 | 989 | 1113 | 1120 |  | 40.38 | 3262.38 | 3096 | 166.38 | 3280 | 6.26 | 51.07% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# & Trackers P.M | 26555226 | 714
2016-11-30 | 978 | 1081 | 1119 |  | 39.95 | 3217.95 | 3063 | 154.95 | 3240 | 6.1 | 51.77% | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 840
2016-12-01 | 860 | 972 | 995 |  | 36.75 | 2863.75 | 2745.75 | 118 | 2910 | 5.54 | 51.2% | Today replaced 5 Damaged moduleModule No-1-Lower side string No-5, ROW-B, Module No-2, AJB No-100, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1108800 New Module Sr No-NPC10BY1113787 Module No-2-Lower side string No-9, ROW-G, Module No-5, AJB No-102, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1112823 New Module Sr No-NPC10BY1113788 Module No-3-Lower side string No-2, ROW-I, Module No-36, AJB No-104, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1116365 New Module Sr No-NPC10BY1113786 Module No-4-Upper side string No-2, ROW-I, Module No-36, AJB No-104, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1116358 New Module Sr No-NPC10BY1113785 Module No-5-Upper side string No-6, ROW-L, Module No-1, AJB No-105, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1113851 New Module Sr No-NPC10BY1113784 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# & Grid Failure From-08:30 to 08:40 & 10:42 to 11:00 & 17:50 to 17:54 WO# | 26555226 26602753 26603751 26606915 26606916
2016-12-02 | 887 | 1001 | 1023 |  | 37.35 | 2948.35 | 2807.25 | 141.1 | 2980 | 5.5 | 52.81% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-17:05 to 17:10 WO# | 26555226 26607173
2016-12-03 | 842 | 955 | 967 |  | 36.11 | 2800.11 | 2682.75 | 117.36 | 2850 | 5.23 | 53.11% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-02:10 to 07:17 & 12:05 to 12:10 & 15:47 to 15:58 WO# | 26555226 26608739 26609879 26612908
2016-12-04 | 888 | 1007 | 1012 |  | 37.68 | 2944.68 | 2811 | 133.68 | 2975 |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-07:35 to 07:39 & 13:36 to 13:40 WO# | 26555226 26613522
2016-12-05 | 933 | 1063 | 1074 |  | 39.85 | 3109.85 | 2981.25 | 128.6 | 3240 |  | #DIV/0! | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-07:37 to 07:43 & 14:18 to 14:25 WO# | 26555226 26613719 26613721 | 777
2016-12-06 | 972 | 1108 | 1120 |  | 40.98 | 3240.98 | 3100.5 | 140.48 | 3270 |  | #DIV/0! | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 624
2016-12-07 | 956 | 1091 | 1108 |  | 40.74 | 3195.74 | 3038.25 | 157.49 | 3225 |  | #DIV/0! | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Grid Failure From-09:58 to 10:04 WO# | 26555226 26615274 | 702
2016-12-08 | 932 | 1068 | 1108 |  | 40.03 | 3148.03 | 3005.25 | 142.78 | 3180 |  | #DIV/0! | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-15:12 to 15:16 WO# | 26555226 26618416 | 864
2016-12-09 | 888 | 1040 | 1046 |  | 38.35 | 3012.35 | 2880 | 132.35 | 3045 | 5.82 | 50.99% | Module cleaning done inverter -3&Trackers, Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:35 to 10:48 WO# | 26555226 26618453 | 690
2016-12-10 | 906 | 1024 | 1028 |  | 36.68 | 2994.68 | 2840.25 | 154.43 | 3012 | 5.62 | 52.24% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-07:35 to 07:40 WO# | 26555226 26620348 | 714
2016-12-11 | 945 | 1074 | 1086 |  | 39.09 | 3144.09 | 3006.75 | 137.34 | 3180 | 5.97 | 51.92% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-09:12 to 09:17 WO# | 26555226 26624488
2016-12-12 | 1000 | 1125 | 1131 |  | 40.51 | 3296.51 | 3133.5 | 163.01 | 3305 | 6.2 | 51.96% | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 840
2016-12-13 | 961 | 1080 | 1091 |  | 39.61 | 3171.61 | 3033.5 | 138.11 | 3200 | 6 | 51.98% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:28 to 10:34 & 16:43 to 16:49 WO# | 26555226 | 777
2016-12-14 | 962 | 1079 | 1074 |  | 39.47 | 3154.47 | 2988 | 166.47 | 3160 | 5.95 | 51.76% | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624
2016-12-15 | 966 | 1086 | 1085 |  | 39.95 | 3176.95 | 3033.75 | 143.2 | 3200 | 6.08 | 51.3% | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 702
2016-12-16 | 973 | 1091 | 1103 |  | 40.04 | 3207.04 | 3046.5 | 160.54 | 3070 |  | #DIV/0! | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 864
2016-12-17 | 949 | 1063 | 1063 |  | 39.84 | 3114.84 | 2972.25 | 142.59 | 3125 |  | #DIV/0! | Module cleaning done inverter -3& Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:40 to 10:43 WO# | 26555226 26649548 | 690
2016-12-18 | 928 | 1034 | 1062 |  | 39.09 | 3063.09 | 2915.25 | 147.84 | 3125 |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226
2016-12-19 | 887 | 996 | 1094 |  | 37.68 | 3014.68 | 2812.5 | 202.18 | 3195 |  | #DIV/0! | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:14 to 10:18 & 13:27 to 13:39 WO# | 26555226 26658394 26658737 | 714
2016-12-20 | 927 | 1068 | 1079 |  | 39.75 | 3113.75 | 2982.75 | 131 | 3150 |  | #DIV/0! | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-11:20 to 11:30 & 17:02 to 17:06 WO# | 26555226 26659830 26659841 | 840
2006-12-21 | 995 | 1119 | 1126 |  | 41.12 | 3281.12 | 3132 | 149.12 | 3300 | 6.15 | 52.3% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 777
2016-12-22 | 973 | 1097 | 1096 |  | 39.65 | 3205.65 | 3060.75 | 144.9 | 3210 | 6.02 | 51.97% | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624
2016-12-23 | 933 | 1043 | 1050 |  | 38.74 | 3064.74 | 2909.25 | 155.49 | 3060 |  | #DIV/0! | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:25 to 10:30 WO# | 26555226 26661656 | 702
2016-12-24 | 927 | 1046 | 1068 |  | 39.33 | 3080.33 | 2949.75 | 130.58 | 3140 |  | #DIV/0! | Module cleaning done inverter -4 Row-H,I,J,K,L & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-9:52 to 9:58 & 10:39 to 10:47 WO# | 26555226 26664656 26664657 | 864
2016-12-25 | 1006 | 1142 | 1165 |  | 41.94 | 3354.94 | 3197.25 | 157.69 | 3380 |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-06:59 to 07:03 WO# | 26555226 26668775
2016-12-26 | 955 | 1068 | 1097 |  | 40.54 | 3160.54 | 3016.5 | 144.04 | 3100 |  | #DIV/0! | Module cleaning done inverter -3 Row-O,P,Q,R,S,T & Total module cleaning -630 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-9:27 to 9:31 WO# | 26555226 26671474 | 630
2016-12-27 | 933 | 1063 | 1068 |  | 39.8 | 3103.8 | 2946 | 157.8 | 3120 |  | #DIV/0! | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 714
2016-12-28 | 973 | 1108 | 1114 |  | 40.86 | 3235.86 | 3073.5 | 162.36 | 3320 |  | #DIV/0! | Module cleaning done inverter -2 Row-I,J,K & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down WO# | 26555226 | 840
2016-12-29 | 915 | 1029 | 1029 |  | 38.54 | 3011.54 | 2883 | 128.54 | 3040 | 5.82 | 50.91% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-13:58 to 14:08 & 15:49 to 15:53 & 16:01 to 16:06 WO# | 26555226 26674366 26674370 26674371 | 777
2016-12-30 | 894 | 1007 | 1006 |  | 37.17 | 2944.17 | 2810.25 | 133.92 | 2970 | 5.72 | 50.61% | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C,D & Total module cleaning -768 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-11:29 to 11:35 WO# | 26555226 26674448 | 768
2017-12-31 | 769 | 859 | 865 |  | 32.18 | 2525.18 | 2397 | 128.18 | 2550 | 4.78 | 52% | Module cleaning done inverter -4 Row-E,F,G,H,I & Total module cleaning -954 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-14:49 To 14:54 & 15:28 to 17:51 WO# | 26555226 26681621 26681628 | 954
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!

## 2017
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2017
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | Total NO- Of Clean Modules
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 1104500525 | 9170301408 | 2100570073/ 2100567820/ 2100567898
2018-01-01 | 944 | 1057 | 1069 |  | 34.24 | 3104.24 | 2958 | 146.24 | 3140 | 5.31 | 57.64% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226
1900-01-01 | 938 | 1046 | 1068 |  | 39.58 | 3091.58 | 2936.25 | 155.33 | 3090 | 5.31 | 56.72% | Module cleaning done inverter -4 Row-,J,K,L, & Total module cleaning -468 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut DownWO# | 26555226 | 468
2018-01-03 | 916 | 1034 | 1052 |  | 34.99 | 3036.99 | 2903.25 | 133.74 | 3050 | 5.65 | 52.61% | Today I Replaced The D.C.12Amp Fuse Link of The String-07--tive in AJB-111 of The Inverter-2 during The Period of 11:30 To 11:40 & Module cleaning done inverter -3 Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From 15:48 to 15:56 WO# | 26555226 26685039 26685046 | 690
2018-01-04 | 905 | 1058 | 1040 |  | 35.71 | 3038.71 | 2891.25 | 147.46 | 2940 |  | #DIV/0! | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From 13:54 to 14:00 & 15:35 to 15:42 WO# | 26555226 26685454 26685457 | 714
2018-01-05 | 847 | 966 | 950 |  | 32.51 | 2795.51 | 2658 | 137.51 | 1151 |  | #DIV/0! | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 840
2018-01-06 | 832 | 939 | 921 |  | 34.35 | 2726.35 | 2589 | 137.35 | 2500 |  | #DIV/0! | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 777
2018-01-07 | 712 | 797 | 786 |  | 28.8 | 2323.8 | 2196 | 127.8 | 3775 |  | #DIV/0! | Module cleaning done inverter -1 & 4 Row-A,B,C,D & A,B,C & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624
2018-01-08 | 859 | 972 | 961 |  | 36.5 | 2828.5 | 2688 | 140.5 | 3062 |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-14:00 to 14:10 WO# | 26555226 26693972
2018-01-09 | 854 | 961 | 967 |  | 36.89 | 2818.89 | 2691 | 127.89 |  |  | #DIV/0! | Module cleaning done inverter -4 Row-D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-14:35 to 14:41 WO# | 26555226 26695157 | 702
2018-01-10 | 854 | 973 | 984 |  | 37.55 | 2848.55 | 2736 | 112.55 |  |  | #DIV/0! | Module cleaning done inverter -4 Row-H,I,J,K,L & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-5:05 to 7:30 & 9:47 to 9:53 & 10:26 to 10:34 WO# | 26555226 26696781 26696790 26697527 | 864
2017-01-11 | 961 | 1125 | 1080 |  | 40.83 | 3206.83 | 3097.5 | 109.33 |  |  | #DIV/0! | Module cleaning done inverter -3 & Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:18 to 10:22 & 18::01 to 18:04 WO# | 26555226 26699268 26699344 | 690
2017-01-12 | 1029 | 1181 | 1186 |  | 42.52 | 3438.52 | 3242.25 | 196.27 |  |  | #DIV/0! | Module cleaning done inverter -3&2 Trackers Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 714
2017-01-13 | 938 | 1086 | 1052 |  | 40.12 | 3116.12 | 3003 | 113.12 |  |  | #DIV/0! | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-14:49 to 15:03 & 15:08 to 15:13 & 15:23 to 15:27 & 16:00 to 16:05 & 16:12 to 16:47 WO# | 26555226 26701808 26701809 26701813 | 840
2017-01-14 | 859 | 972 | 956 |  | 35 | 2822 | 2709.75 | 112.25 |  |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-16:07 to 16:15 & 16:32 to 16:40 & 16:44 to 17:30 & 17:54 to 18:00 WO# | 26555226 26706403 26706407 26706409 26706411
2017-01-15 | 871 | 989 | 972 |  | 33 | 2865 | 2727 | 138 |  |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226
2017-01-16 | 939 | 1075 | 1001 |  | 34.98 | 3049.98 | 2903.25 | 146.73 |  |  | #DIV/0! | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Today inverter No-3 ABB 250 KW Morning time note wake up Err code-(8189) Auto Reset ,F, Reset The Err code 3 Time inverter started 9:18 & Inverter no-1&3s Transformer maintance L.T & H.T, side tietnace & oil filing Aprox 50 liter WO# | 26555226 26707646 | 777
2017-01-17 | 1011 | 1151 | 1147 |  | 37.96 | 3346.96 | 3194.25 | 152.71 |  |  | #DIV/0! | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624
2017-01-18 | 961 | 1099 | 1114 |  | 36.56 | 3210.56 | 3055.5 | 155.06 |  |  | #DIV/0! | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 702
2017-01-19 | 741 | 865 | 865 |  | 28.32 | 2499.32 | 2363.25 | 136.07 |  |  | #DIV/0! | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226 | 864
2017-01-20 | 769 | 865 | 853 |  | 27.23 | 2514.23 | 2377.5 | 136.73 |  |  | #DIV/0! | Module cleaning done inverter -4&Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226 | 690
2017-01-21 | 141 | 158 | 153 |  | 4.85 | 456.85 | 396.75 | 60.1 |  |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day & Grid Failure From-09:44 to 10:40 & 10:55 to 16:01 | 26555226 26713302 26718386
2017-01-22 | 854 | 972 | 955 |  | 31.65 | 2812.65 | 2668.5 | 144.15 |  |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226
2017-01-23 | 831 | 956 | 950 |  | 31.15 | 2768.15 | 2649 | 119.15 |  |  | #DIV/0! | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day & Grid Failure From-10:10 to 10:29 | 26555226 26718525 | 714
2017-01-24 | 893 | 1029 | 1040 |  | 35.02 | 2997.02 | 2857.5 | 139.52 |  |  | #DIV/0! | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day & Grid Failure From-10:05 to 10:12 | 26555226 26720440 | 840
2017-01-25 | 831 | 961 | 956 |  | 29.46 | 2777.46 | 2638.5 | 138.96 |  |  | #DIV/0! | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26552526 | 777
2017-01-26 | 882 | 1012 | 1001 |  | 32.98 | 2927.98 | 2787.75 | 140.23 | 2950 | 5.09 | 56.49% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226
2017-01-27 | 1108 | 1289 | 1266 |  | 41.05 | 3704.05 | 3540 | 164.05 | 3720 | 6.58 | 55.1% | Module cleaning done inverter -1&4 Row-,A,B,C,D,&A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:02 to 10:13 WO# | 26555226 26726608 | 624
2017-01-28 | 848 | 995 | 972 |  | 33.48 | 2848.48 | 2722.5 | 125.98 | 2880 | 5.18 | 54.19% | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-08:50 to 09:14 & 09:28 to 09:45 & 9:48 to 11:20 & Today I Replaced The D.C.12Amp Fuse Link of The String-09++tive in AJB-116 of The Inverter-3 during The Period of 12:40 To 12:50 WO# | 26555226 26726819 26726820 26726821 26748457 | 702
2017-01-29 | 1091 | 1272 | 1244 |  | 39.83 | 3646.83 | 3486 | 160.83 | 3675 |  | #DIV/0! | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & TRANSFORMER P.M,WO# | 26555226
2017-01-30 | 1069 | 1238 | 1233 |  | 43.43 | 3583.43 | 3406.5 | 176.93 | 3650 |  | #DIV/0! | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 864
2017-01-31 | 1068 | 1244 | 1255 |  | 41.71 | 3608.71 | 3428.25 | 180.46 | 3610 | 6.47 | 54.38% | Module cleaning done inverter -3& Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 690
2017-02-01 | 1035 | 1232 | 1226 |  | 43.24 | 3536.24 | 3385.5 | 150.74 | 3560 | 6.39 | 54.3% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Grid Failure From-09:26 to 09:38 | 26555226 26733914 | 714
2017-02-02 | 1069 | 1256 | 1244 |  | 43.34 | 3612.34 | 3446.25 | 166.09 | 3630 | 6.47 | 54.68% | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 840
2017-02-03 | 932 | 1080 | 1063 |  | 37.56 | 3112.56 | 2992.5 | 120.06 | 3130 | 5.74 | 53.15% | Module cleaning done inverter -2 Row-,E,F,G,H, & Total module cleaning -77 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 777
2017-02-04 | 865 | 989 | 978 |  | 35.51 | 2867.51 | 2727 | 140.51 | 2890 | 5.21 | 54.06% | Module cleaning done inverter -1&4 Row-,A,B,C,D,& A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Grid Failure From-16:31 to 17:19 & 17:24 to 17:31 | 26555226 26741037 26741038 | 624
2017-02-05 | 1120 | 1307 | 1283 |  | 44.58 | 3754.58 | 3551.25 | 203.33 | 3765 | 6.76 | 54.28% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Today Received ABB 250 KW New Inverter Our site By pdpu WO# | 26555226
2017-02-06 | 1068 | 1238 | 1230 |  | 43.36 | 3579.36 | 3391.5 | 187.86 | 3580 | 6.42 | 54.35% | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 702
2017-02-07 | 1137 | 1328 | 1281 |  | 46.09 | 3792.09 | 3637.5 | 154.59 | 3810 | 7 | 53.05% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226
2017-02-08 | 966 | 1131 | 1113 |  | 40.78 | 3250.78 | 3122.25 | 128.53 | 3290 | 6.1 | 52.57% | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:21 to 10:50 & 16:19 to 16:37 & 17:20 to 17:23WO# | 26555226 26743973 26744000 26744002
2017-02-09 | 1137 | 1334 | 1306 | 927 | 46.77 | 4750.77 | 4406.25 | 344.52 | 4612 | 7.06 | 63.67% | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider Replaced The New Inverter ABB 250 KW All working Fine Inverter started 11:30 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Site has taken shutdown due to Installation of New Inverter 10:18 to 10:23 WO# | 26555226 26744972 26744059 | 864
2017-02-10 | 1119 | 1300 | 1272 | 1270 | 45.9 | 5006.9 | 4785 | 221.9 | 5020 | 6.74 | 72.59% | Module cleaning done inverter -4 Row-O,P,Q,R,S,T & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short WO# | 26744972 | 690
2017-02-11 | 1018 | 1171 | 1148 | 1074 | 41.5 | 4452.5 | 4269 | 183.5 | 4480 | 6.12 | 71.35% | Module cleaning done inverter -2&3 Row-L,M,N, & Total module cleaning -714 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-12:20 to 12:24 WO# | 26744972 26751482 | 714
2017-02-12 | 1048 | 1215 | 1187 | 1083 | 43.1 | 4576.1 | 4365.75 | 210.35 | 4605 | 6.35 | 70.68% | Inverter no-4 ABB One AJB Down due to cable Lenth short WO# | 26744972
2017-02-13 | 809 | 922 | 916 | 847 | 32.8 | 3526.8 | 3374.75 | 152.05 | 3565 | 4.46 | 77.91% | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-12:13 to 12:47 WO# | 26744972 26756715 | 840
2017-02-14 | 842 | 972 | 995 | 988 | 36.02 | 3833.02 | 3663 | 170.02 | 3862 |  | #DIV/0! | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-15:40 to 16:24 WO# | 26744972 26757428 | 777
2017-02-15 | 888 | 1034 | 1068 | 1043 | 37.1 | 4070.1 | 3883.5 | 186.6 | 4100 |  | #DIV/0! | Module cleaning done inverter -1&4 Row-,A,B,C,D,&A,B,C, & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short WO# | 26744972 | 690
2017-02-16 | 820 | 973 | 990 | 973 | 34.96 | 3790.96 | 3633 | 157.96 | 3840 | 5.4 | 69.31% | Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-13:37 to 14:05 WO# & Today Module Cleaning Not done Because Grass cutting Swichyard side | 26744972 26760377
2017-02-17 | 989 | 1216 | 983 | 1220 | 38.84 | 4446.84 | 4249.5 | 197.34 | 4420 | 6.41 | 67.21% | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-13:06 to 13:15 & Today Grid Failure After Inverter No-3 ABB 250 KW not started Err code-Net Loss, Reset The Err 3 Time After Inverter started-14:37 WO# | 26744972 26760615 | 702
2017-02-18 | 1023 | 1260 | 1222 | 1240 | 37.51 | 4782.51 | 4575 | 207.51 | 4660 | 6.54 | 69.45% | Module cleaning done inverter -4 Row-H,I,J,K,L, & Total module cleaning -864 & Inverter no-4 ABB One AJB Down due to cable Lenth short | 26744972 | 864
2017-02-19 | 961 | 1182 | 1142 | 1134 | 35.31 | 4454.31 | 4276.5 | 177.81 | 4465 | 6.16 | 70.65% | Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From- 18:00 to 18:45 WO# | 26744972 26764967
2017-02-20 | 1080 | 1283 | 1215 | 1270 | 37.6 | 4885.6 | 4684.5 | 201.1 | 4910 |  | #DIV/0! | Module cleaning done inverter -3 & Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Yesterday Grid Failure After Inverter No-3 ABB 250 KW not started(Morning time not wake up) Due to D.C.contactor Failure, Inverter started Manually-08:38 WO# | 26744972 26764962 | 690
2017-02-21 | 1102 | 1272 | 1232 | 1260 | 36.94 | 4902.94 | 4697.25 | 205.69 | 4925 | 6.69 | 71.75% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today Inverter No-3 ABB 250 KW not started(Morning time not wake up) Due to D.C.contactor Failure, Inverter started Manually-07:45 WO# | 26744972 26766495 | 714
2017-02-22 | 1080 | 1255 | 1227 | 1310 | 36.45 | 4908.45 | 4722 | 186.45 | 4930 | 6.88 | 69.84% | Module cleaning done inverter -3&2 Row-,I,J,K, & Total module cleaning -840 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-16:58 to 17:52 WO# | 26744972 26766495 26771308 | 840
2017-02-23 | 1001 | 1272 | 1233 | 1321 | 43.04 | 4870.04 | 4659.75 | 210.29 | 4900 | 6.99 | 68.32% | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-08:46 to 09:05 & Grid Failure After Inverter No-1 ABB 250 KW not started Err code-8188 D.C.Breaker trip Reset Err code inverter started-9:56 WO# | 26744972 26766495 26771351 26771352 | 777
2017-02-24 | 1091 | 1266 | 1266 | 1325 | 44.24 | 4992.24 | 4785.75 | 206.49 | 5020 |  | #DIV/0! | Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-08:00 & Grid Failure From-17:28 to 17:52 WO# | 26744972 26766495 26772800
2017-02-25 | 1114 | 1301 | 1149 | 1351 | 45.16 | 4960.16 | 4721.25 | 238.91 | 4970 | 7.16 | 67.65% | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-10:02 WO# | 26744972 26766495 26776945 | 690
2017-02-26 | 1080 | 1278 | 1295 | 1331 | 44.34 | 5028.34 | 4824.75 | 203.59 | 5060 |  | #DIV/0! | Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-05:45 to 06:53 & 07:12 to 07:25 WO# | 26744972 26766495 26776955 26776956
2017-02-27 | 1051 | 1272 | 1255 | 1295 | 43.27 | 4916.27 | 4719 | 197.27 | 4945 |  | #DIV/0! | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-07:47 to 07:55 to 18:08 to 18:18 WO# | 26744972 26766495 26777140 26778337 | 702
2017-02-28 | 950 | 1209 | 1142 | 1165 | 40.78 | 4506.78 | 4332 | 174.78 | 4535 |  | #DIV/0! | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-09:07 to 09:15 & 14:10 to 14:16 & Grid Failure After Inverter No-1 ABB 250 KW not started Err code-8188 D.C.Breaker trip Reset Err code inverter started-9:47 WO# | 26744972 26766495 26778360 26778359 26778809 | 864
2017-03-01 | 1074 | 1255 | 1215 | 1234 | 41.39 | 4819.39 | 4604.25 | 215.14 | 4840 | 6.65 | 70.94% | Module cleaning done inverter -3 & Trackers, Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter no-4 ABB 250 KW Replaced New Cable & AJB, started-18:40, & short out The Issue & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26744972 26766495 | 690
2017-03-02 | 1086 | 1267 | 1233 | 1276 | 41.66 | 4903.66 | 4690.5 | 213.16 | 4935 | 6.71 | 71.68% | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26766495 26781762 | 714
2017-03-03 | 994 | 1159 | 978 | 1108 | 40.24 | 4279.24 | 4125.75 | 153.49 | 4335 | 6.17 | 68.48% | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-09:40 & Today inverter no-4 ABB 250 KW Shut Down,16:07. Due to MJB'S One Lug sparking, Resolved The Issue Inverter started-16:55 & Grid Failure From-15:08 to 16:07 WO# | 26781838 26783992 26783988 | 840
2017-03-04 | 1024 | 1204 | 972 | 1250 | 40.89 | 4490.89 | 4325.25 | 165.64 | 4571 | 6.51 | 68.44% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-10:50 & Today I Replaced The D.C.12Amp Fuse Link of The String-09++tive in AJB-116 of The Inverter-3 during The Period of 12:40 To 12:50 & Grid Failure From-08:56 to 09:08 & 09:10 to 09:23 & 11:28 to 11:36 WO# | 26788033 26788032 26785405 26786933 | 777
2017-03-05 | 1068 | 1243 | 1204 | 1296 | 41.55 | 4852.55 | 4641.75 | 210.8 | 4880 | 6.55 | 72.62% | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:50 WO# | 26788033
2017-03-06 | 1103 | 1284 | 1250 | 1356 | 43.31 | 5036.31 | 4818 | 218.31 | 5065 | 6.8 | 72.6% | Module cleaning done inverter -1&4 & Row-,A,B,C,D,& ,A,B,C, & Total module cleaning -624 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:50 WO# | 26788033 | 624
2017-03-07 | 1046 | 1221 | 1227 | 1290 | 42.1 | 4826.1 | 4623.75 | 202.35 | 4865 | 6.54 | 72.5% | Module cleaning done inverter -4, Row-,D,E,F,G, & Total module cleaning -704 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-08:00 & Grid Failure From-17:07 to 17:18 WO# | 26788033 26790307 | 704
2017-03-08 | 1113 | 1323 | 1333 | 1401 | 44.12 | 5214.12 | 4971 | 243.12 | 5215 | 6.79 | 74.86% | Module cleaning done inverter -4, Row-,H,I,J,K,L, & Total module cleaning -864 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:50 WO# | 26788033 | 864
2017-03-09 | 1069 | 1272 | 1256 | 1311 | 42.34 | 4950.34 | 4760.25 | 190.09 | 4980 | 6.6 | 73.54% | Module cleaning done inverter -3, Row-O,P,Q,R,S,T & Total module cleaning -690 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-08:00 & Grid Failure From-12:17 to 12:22 WO# | 26788033 26793174 | 690
2017-03-10 | 899 | 1034 | 1000 | 1073 | 35.35 | 4041.35 | 3861 | 180.35 | 4082 | 5.42 | 73.41% | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30 & Grid Failure From-16:17 to 16:30 WO# | 26788033 26794775 | 714
2017-03-11 | 1193 | 1397 | 1374 | 1401 | 46.12 | 5411.12 | 5159.25 | 251.87 | 5425 | 7.4 | 71.45% | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30WO# | 26788033 | 840
2017-03-12 | 1170 | 1368 | 1351 | 1396 | 42.58 | 5327.58 | 5089.5 | 238.08 | 5235 | 7.33 | 69.61% | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30WO# | 26788033
2017-03-13 | 1001 | 1340 | 1301 | 1351 | 40.81 | 5033.81 | 4833 | 200.81 | 5060 | 7.28 | 67.74% | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30 & Today morning time Inverter No-1 ABB 250 KW not wake up Due to error Net loss reset error code Inverter started at 9:30 & Grid Failure From-16:32 to 16:50 WO# | 26788033 26799068 26799266
2017-03-14 | 1192 | 1390 | 1362 | 1427 | 43.22 | 5414.22 | 5188.5 | 225.72 | 5440 | 7.43 | 71.36% | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:40 & Grid Failure From-18:24 to 18:31 WO# | 26788033 26800001
2017-03-15 | 1137 | 1329 | 1306 | 1386 | 38.5 | 5196.5 | 4993.5 | 203 | 5065 | 7.18 | 68.76% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26788033 | 777
2017-03-16 | 1063 | 1238 | 1227 | 1310 | 34.27 | 4872.27 | 4674 | 198.27 | 4895 | 6.77 | 70.47% | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26788033 | 624
2017-03-17 | 1023 | 1184 | 1215 | 1285 | 34.02 | 4741.02 | 4554 | 187.02 | 4770 | 6.64 | 70.02% | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Today Inverter No-3 ABB 250 KW Replaced The New D.C. Breaker Resolved The Issue, & Grid Failure From-10:54 to 11:08 WO# | 26788033 26810242 | 704
2017-03-18 | 1080 | 1244 | 1306 | 1376 | 34.52 | 5040.52 | 4831.5 | 209.02 | 5070 | 6.77 | 72.99% | Module cleaning done inverter -3 & Trackers & Row-,O,P,Q,R,S,T, & Total module cleaning -690 WO# |  | 690
2017-03-19 | 1051 | 1232 | 1266 | 1321 | 35.02 | 4905.02 | 4702 | 203.02 | 4930 | 6.63 | 72.47% | Grid Failure From-09:53 to 10:00 WO# | 26814767
2017-03-20 | 1035 | 1232 | 1256 | 1310 | 35.23 | 4868.23 | 4687.5 | 180.73 | 4900 | 6.88 | 69.42% | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714 & Grid Failure From-07:00 to 08:07 & 11:22 to 11:37 WO# | 26814794 26814841 | 714
2017-03-21 | 1079 | 1278 | 1272 | 1316 | 35.94 | 4980.94 | 4776 | 204.94 | 5010 | 6.91 | 70.67% | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 WO# |  | 840
2017-03-22 | 1046 | 1193 | 1192 | 1199 | 33.81 | 4663.81 | 4469.25 | 194.56 | 4690 | 6.6 | 69.26% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 |  | 777
2017-03-23 | 1108 | 1266 | 1261 | 1311 | 34.97 | 4980.97 | 4776.75 | 204.22 | 4910 | 6.89 | 69.46% | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 |  | 690
2017-03-24 | 1114 | 1284 | 1278 | 1361 | 35.46 | 5072.46 | 4874.25 | 198.21 | 5100 | 7.15 | 69.52% | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Grid Failure From-14:58 to 15:08 WO# | 26817262 | 704
2017-03-25 | 1097 | 1249 | 1249 | 1366 | 35.68 | 4996.68 | 4806.75 | 189.93 |  |  | #DIV/0! | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 & Grid Failure From-12:32 to 12:42 WO# | 26823758 | 864
2017-03-26 | 1074 | 1233 | 1244 | 1340 | 40.61 | 4931.61 | 4752 | 179.61 |  |  | #DIV/0! | Grid Failure From-06:55 to 07:05 & 17:40 TO 17:45 WO# | 26823836 26823848
2017-03-27 | 1029 | 1192 | 1210 | 1306 | 35 | 4772 | 4560.75 | 211.25 |  |  | #DIV/0! | Grid Failure From-09:33 to 09:40 WO# | 26824083
2017-03-28 | 1074 | 1233 | 1283 | 1346 | 35.82 | 4971.82 | 4784.25 | 187.57 |  |  | #DIV/0! | Module cleaning done inverter -3, Row-O,P,Q,R,S,T & Total module cleaning -690 & Grid Failure From-07:53 to 08:00 WO# | 26824084 | 690
2017-03-29 | 1052 | 1232 | 1266 | 1320 | 35 | 4905 | 4728 | 177 |  |  | #DIV/0! | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714 & Grid Failure From-08:21 to 08:30 & 18:07 to 18:15 WO# | 26825064 26825065 | 714
2017-03-30 | 1068 | 1278 | 1278 | 1321 | 35.23 | 4980.23 | 4776.75 | 203.48 |  |  | #DIV/0! | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 WO# |  | 840
2017-03-31 | 1103 | 1289 | 1278 | 1325 | 35 | 5030 | 4823.25 | 206.75 |  |  | #DIV/0! | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 |  | 777
2017-04-01 | 1113 | 1277 | 1283 | 1321 | 34.96 | 5028.96 | 4830 | 198.96 |  |  | #DIV/0! | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 |  | 690
2017-04-02 | 1108 | 1278 | 1278 | 1320 | 34.72 | 5018.72 | 4830 | 188.72 |  |  | #DIV/0! | Grid Failure From-09:57 to 10:07 & 17:07 to 17:27 WO# | 26833887 26833931
2017-04-03 | 1012 | 1159 | 1153 | 1205 | 34.14 | 4563.14 | 4404.75 | 158.39 |  |  | #DIV/0! | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Grid Failure From-15:05 to 15:15 & 15:17 to 15:50 & 17:09 to 17:18 WO# | 26834042 26834045 26834049 | 704
2017-04-04 | 1097 | 1278 | 1250 | 1346 | 41.2 | 5012.2 | 4803.75 | 208.45 |  |  | #DIV/0! | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 & Today I Replaced The 3, D.C.12Amp Fuse Link of The String-05--tive in AJB-109 of The Inverter-2 during The Period of 10:30 to 10:40 & string No2++tive & 3--tive line AJB No-113 Inverter No-3 During The period of 10:45 to 10:55, WO# |  | 864
2017-04-05 | 1035 | 1204 | 1187 | 1280 | 39.54 | 4745.54 | 4549.5 | 196.04 |  |  | #DIV/0! | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, |  | 690
2017-04-06 | 1080 | 1255 | 1255 | 1346 | 42.35 | 4978.35 | 4764.75 | 213.6 | 4990 | 6.71 | 72.48% | Module cleaning done inverter -3&2, Row-L,M,N & Total module cleaning -714, |  | 714
2017-04-07 | 1124 | 1323 | 1357 | 1376 | 44.79 | 5224.79 | 5024.25 | 200.54 | 5230 | 7.13 | 71.49% | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 WO# |  | 840
2017-04-08 | 1091 | 1295 | 1339 | 1320 | 43.81 | 5088.81 | 4902 | 186.81 | 5090 | 7.03 | 70.57% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 |  | 777
2017-04-09 | 1103 | 1339 | 1346 | 1341 | 43.71 | 5172.71 | 4962 | 210.71 | 5190 | 7.04 | 71.85% | Sunday No module cleaning
2017-04-10 | 1119 | 1374 | 1368 | 1235 | 43.84 | 5139.84 | 4938 | 201.84 | 5160 | 7.2 | 69.85% | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 & Grid Failure From-10:27 to 10:32 WO# | 26844032 | 624
2017-04-11 | 1097 | 1351 | 1317 | 1285 | 42.09 | 5092.09 | 4867.5 | 224.59 | 5120 | 6.96 | 71.7% | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 WO# |  | 704
2017-04-12 | 1120 | 1346 | 1323 | 1321 | 42.26 | 5152.26 | 4935 | 217.26 | 5170 | 7.01 | 71.88% | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 WO# |  | 864
2017-04-13 | 1147 | 1340 | 1312 | 1325 | 42 | 5166 | 4957.5 | 208.5 |  |  | #DIV/0! | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, & Grid Failure From-18:30 to 18:36 WO# |  | 690
2017-04-14 | 1114 | 1306 | 1272 | 1306 | 40.97 | 5038.97 | 4833 | 205.97 |  |  | #DIV/0! | Module cleaning done inverter -3&2, Row-L,M,N & Total module cleaning -714, & Today Inverter No-3 ABB 250 KW Morning time not wake up Due to Err code Net Loss (A32) Reset The Err code Inverter started 07:32 WO# | 26846721 | 714
2017-04-15 | 1119 | 1305 | 1278 | 1355 | 40.98 | 5097.98 | 4894.5 | 203.48 |  |  | #DIV/0! | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 & L.T, PANAL P.M, WO# |  | 840
2017-04-16 | 1103 | 1284 | 1260 | 1341 | 41.57 | 5029.57 | 4814.25 | 215.32 |  |  | #DIV/0! | Sunday No Module Cleaning
2017-04-17 | 1085 | 1266 | 1261 | 1366 | 41.08 | 5019.08 | 4809 | 210.08 |  |  | #DIV/0! | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 & Today I Replaced The 2, D.C.12Amp Fuse Link of The String-07--tive in AJB-100 of The Inverter-4 during The Period of 10:25 to 10:35 & string No3++tive line AJB No-103 Inverter No-4 During The period of 10:40 to 10:50, WO# | 26858207 | 777
2017-04-18 | 113 | 1296 | 1323 | 1406 | 38.89 | 4176.89 | 4015.5 | 161.39 |  |  | #DIV/0! | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 & Grid Failure From-07:45 to 07:50 & 10:13 to 10:23 & Today Morning time Grid Failure After Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal sutdown & Inverter No-1,2 P.M WO# | 26858589 26858656 26858771 | 624
2017-04-19 |  | 1277 | 1289 | 1381 | 40.63 | 3987.63 | 3814.5 | 173.13 |  |  | #DIV/0! | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Inverter No-1,2 P.M WO# | 26858771 | 704
2017-04-20 |  | 1266 | 1255 | 1331 | 40.02 | 3892.02 | 3717 | 175.02 |  |  | #DIV/0! | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Grid Failure From-15:17 to 15:29 WO# | 26859776 2688771
2017-04-21 |  | 1289 | 1278 | 1346 | 40.13 | 3953.13 | 3790.5 | 162.63 | 3980 | 6.65 | 58.33% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown WO# | 26858771
2017-04-22 |  | 1250 | 1238 | 1320 | 39.33 | 3847.33 | 3667.5 | 179.83 | 3860 | 6.52 | 57.7% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown WO# | 26858771
2017-04-23 |  | 1147 | 1142 | 1190 | 36.97 | 3515.97 | 3360.75 | 155.22 | 3530 | 6.01 | 57.25% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown &Grid Failure From-11:05 to 11:20 WO# | 26858771 26869751
2017-04-24 |  | 1238 | 1221 | 1305 | 38.99 | 3802.99 | 3639 | 163.99 | 3840 | 6.39 | 58.57% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 WO# | 26858771 | 864
2017-04-25 |  | 1233 | 1221 | 1326 | 38.75 | 3818.75 | 3654.75 | 164 | 3840 | 6.5 | 57.58% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, WO# | 26858771 | 690
2017-04-26 |  | 1266 | 1227 | 1391 | 39.3 | 3923.3 | 3740.25 | 183.05 | 3935 | 6.74 | 56.9% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -3&2, Row-L,M,N, & Total module cleaning -714, WO# | 26858771 | 714
2017-04-27 |  | 1215 | 1209 | 1351 | 39.63 | 3814.63 | 3661.5 | 153.13 | 3840 | 6.86 | 54.56% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -2, Row-I,J,K, & Total module cleaning -840, & Grid Failure From-11:45 to 11:55 & Today I Replaced The D.C.12Amp Fuse Link of The String-08--tive in AJB-115 of The Inverter-4 during The Period of 09:25 to 09:35 WO# | 26858771 26875944 26876163 | 840
2017-04-28 |  | 1182 | 1216 | 1330 | 38.96 | 3766.96 | 3609.75 | 157.21 | 3780 | 6.54 | 56.33% | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -1, Row-,E,F,G,H, & Total module cleaning -777, & Grid Failure From-09:55 to 10:11 WO# | 26858771 26876993 | 777
2017-04-29 | 28 | 1142 | 1187 | 1260 | 33.23 | 3650.23 | 3500.25 | 149.98 | 3670 | 6.25 | 57.23% | Today Replased New AFPS-11C Card Resoled The Issue Inverter started 17:05 & Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, & Inverter No-3,4,& Transformer P.M, WO# | 26858771 | 624
2017-04-30 | 945 | 1152 | 1182 | 1240 | 40.4 | 4559.4 | 4371.75 | 187.65 | 4600 | 6.38 | 70.27% | Sunday No Module Cleaning
2017-05-01 | 961 | 1210 | 1193 | 1245 | 35.53 | 4644.53 | 4446.75 | 197.78 | 4680 | 6.5 | 70.18% | Module cleaning done inverter -4, Row-,D,E,F,G, & Total module cleaning -704, WO# |  | 704
2017-05-02 | 949 | 1159 | 1125 | 1179 | 36.73 | 4448.73 | 4284 | 164.73 | 4500 | 6.47 | 67.79% | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 & Grid Failure From-07:07 to 08:08 WO# | 26886953 | 864
2017-05-03 | 1018 | 1198 | 1164 | 1245 | 38.2 | 4663.2 | 4476.75 | 186.45 | 4710 | 6.42 | 71.51% | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, WO# |  | 690
2017-05-04 | 1074 | 1261 | 1233 | 1326 | 38.47 | 4932.47 | 4757.25 | 175.22 | 4950 | 6.77 | 71.26% | Module cleaning done inverter -3&2, Row-L,M,N, & Total module cleaning -714, WO# |  | 714
2017-05-05 | 1023 | 1199 | 1170 | 1255 | 37.28 | 4684.28 | 4489.5 | 194.78 | 4710 | 6.43 | 71.39% | Module cleaning done inverter -2, Row-I,J,K, & Total module cleaning -840,WO# |  | 840
2017-05-06 | 1063 | 1249 | 1221 | 1356 | 38.06 | 4927.06 | 4732.5 | 194.56 | 4970 | 6.8 | 71.24% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, WO# |  | 777
2017-05-07 | 1063 | 1255 | 1227 | 1341 | 39.7 | 4925.7 | 4722.75 | 202.95 | 4960 | 6.87 | 70.37% | Sunday No Module Cleaning
2017-05-08 | 1046 | 1227 | 1232 | 1315 | 38.7 | 4858.7 | 4656.75 | 201.95 | 4890 | 6.75 | 70.61% | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, WO# |  | 624
2017-05-09 | 1029 | 1210 | 1242 | 1285 | 38.72 | 4804.72 | 4617.75 | 186.97 | 4850 | 6.68 | 70.76% | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704, WO# |  | 704
2017-05-10 | 1023 | 1215 | 1249 | 1281 | 38.24 | 4806.24 | 4612.5 | 193.74 | 4840 | 6.64 | 71.04% | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 WO# |  | 864
2017-05-11 | 1001 | 1227 | 1221 | 1250 | 37.29 | 4736.29 | 4543.5 | 192.79 | 4780 | 6.5 | 71.67% | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, WO# |  | 690
2017-05-12 | 1000 | 1204 | 1177 | 1194 | 35.97 | 4610.97 | 4414.5 | 196.47 | 4650 | 6.31 | 71.83% | Module cleaning done inverter -3&2, Row-L,M,N, & Total module cleaning -714, WO# |  | 714
2017-05-13 | 300 | 385 | 378 | 378 | 10.15 | 1451.15 | 1367.25 | 83.9 | 1511 |  | #DIV/0! | Grid Failure From-06:54 to 13:50 WO# | 26901003
2017-05-14 | 1001 | 1181 | 1165 | 1190 | 36.85 | 4573.85 | 4464 | 109.85 | 4620 | 6.25 | 72.05% | Sunday No Module Cleaning
2017-05-15 | 1046 | 1238 | 1215 | 1245 | 36.7 | 4780.7 | 4510.5 | 270.2 | 4830 | 6.67 | 70.58% | Module cleaning done inverter -2, Row-I,J,K, & Total module cleaning -840, Grid Failure From-10:49 to 10:57 WO# | 26905688 | 840
2017-05-16 | 1012 | 1199 | 1182 | 1249 | 36.6 | 4678.6 | 4498.5 | 180.1 | 4730 | 6.45 | 71.47% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, WO# |  | 777
2017-05-17 |  | 1057 | 1187 | 1281 | 36.08 | 3561.08 | 3428.25 | 132.83 | 3605 | 6.59 | 53.32% | Today morning time Grid Failure after Inverter No-2 ABB 250 KW not started Due to Emergency stop inverter started Manually-09:15 & Today morning time Grid Failure after Inverter No-1 ABB 250 KW not started Due to D.C. Breaker Failure Inverter steal shut Down at the site & Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, & Grid Failure From-06:34 to 06:40 & 16:04 to 16:10 & 16:29 to 16:38 WO# | 26911932 26911933 26911934 26912030 26912031 | 624
2017-05-18 |  | 1187 | 1193 | 1275 | 37.5 | 3692.5 | 3538.5 | 154 | 3735 |  | #DIV/0! | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,WO# | 26911934 | 704
2017-05-19 |  | 1216 | 1255 | 1305 | 37.96 | 3813.96 | 3644.25 | 169.71 | 3855 |  | #DIV/0! | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,WO# | 26911934 | 864
2017-05-20 |  | 1244 | 1249 | 1301 | 37.64 | 3831.64 | 3658.5 | 173.14 | 3850 | 6.83 | 54.94% | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26911934 | 690
2017-05-21 |  | 1079 | 1063 | 1098 | 32.91 | 3272.91 | 3162 | 110.91 | 3320 | 5.82 | 55.6% | Sunday No Module Cleaning & Grid Failure From-17:00 to 17:10 & Cloudy Day & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427
2017-05-22 |  | 1188 | 1165 | 1185 | 35.64 | 3573.64 | 3399 | 174.64 | 3600 | 6.39 | 54.91% | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,WO# | 26917427 | 714
2017-05-23 |  | 1192 | 1170 | 1189 | 35.51 | 3586.51 | 3438.75 | 147.76 | 3620 | 6.54 | 53.95% | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,& Grid Failure From-14:20 to 14:26 & 15:20 to 15:30 WO# | 26917427 26919845 26919847 | 840
2017-05-24 |  | 1182 | 1153 | 1175 | 35.09 | 3545.09 | 3383.25 | 161.84 | 3581 | 6.58 | 53.04% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, & Grid Failure From-08:30 to 08:41 WO# | 26917427 26919888 | 777
2017-05-25 |  | 1159 | 1120 | 1184 | 34.26 | 3497.26 | 3348 | 149.26 | 3535 |  | #DIV/0! | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624,& Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 | 624
2017-05-26 |  | 1165 | 1125 | 1235 | 34.44 | 3559.44 | 3401.25 | 158.19 | 3600 |  | #DIV/0! | Module cleaning done inverter -4, Row-,D,E,F,G, & Total module cleaning -704,& Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 | 704
2017-05-27 |  | 1096 | 1125 | 1240 | 36.17 | 3497.17 | 3375 | 122.17 | 3511 | 6.48 | 52.81% | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,& Yesterday Night time Grid Failure after morning time Inverter No-2&3 not wake up Due to Emergency Stop Reset The Err code Inverter started 08:17, WO# | 26917427 26929597 | 864
2017-05-28 |  | 1052 | 1091 | 1134 | 33.73 | 3310.73 | 3165.75 | 144.98 | 3340 | 5.93 | 54.9% | Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427
2017-05-29 |  | 921 | 955 | 968 | 27.66 | 2871.66 | 2724.75 | 146.91 | 2900 | 5.18 | 54.57% | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 | 690
2017-05-30 | 853 | 1035 | 1035 | 1053 | 32.11 | 4008.11 | 3850.5 | 157.61 | 4075 | 5.82 | 68.24% | Grid Failure From-11:25 to 11:47 & 13:41 to 13:46 WO# & No Module cleaning Bor Failure, | 26935692 26935694
2017-05-31 | 928 | 1119 | 1119 | 1190 | 35.05 | 4391.05 | 4209 | 182.05 | 4440 | 6.35 | 68.15% | No Module cleaning Bor Failure, & Grid Failure From-07:06 to 07:15 WO# | 26935734
2017-06-01 | 864 | 1057 | 1029 | 1078 | 39.16 | 4067.16 | 3897.5 | 169.66 | 4100 | 5.89 | 67.85% | No Module cleaning Bor Failure,
2017-06-02 | 752 | 1075 | 1029 | 1090 | 27.15 | 3973.15 | 3806.25 | 166.9 | 4010 | 5.98 | 65.36% | No Module cleaning Bor Failure, & Grid Failure From-09:28 to 09:42 & Today 11:39 Inverter No-1 ABB 250 KW Auto Trip Due to Emergency stop Reset The Err code Five time after Inverter started 12:38 WO# | 26940315 26942421
2017-06-03 | 860 | 1074 | 1012 | 1093 | 32.37 | 4071.37 | 3893.25 | 178.12 | 4115 | 5.85 | 68.56% | Today I Replaced The 2, D.C.12Amp Fuse Link of The String-03--tive in AJB-100 of The Inverter-4 during The Period of 09:25 to 09:35 & string No8--tive line AJB No-103 Inverter No-4 During The period of 09:40 to 10:45,& No Module cleaning, Bor Failure,WO#
2017-06-04 | 904 | 1108 | 1035 | 1124 | 33.77 | 4204.77 | 4005.75 | 199.02 | 4250 | 5.96 | 69.5% | cloudy day & Sunday No Module cleaning
2017-06-05 | 820 | 983 | 938 | 1013 | 28.92 | 3782.92 | 3642 | 140.92 | 3840 | 5.8 | 64.53% | Today shut Down the plant 14:53 for New UPS Installation Successfully Installation UPS After plant started-15:26 WO# & Cloudy Day | 26947491
2017-06-06 | 916 | 1018 | 950 | 1099 | 32.17 | 4015.17 | 3831.75 | 183.42 | 4060 | 5.74 | 68.94% | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714, & Grid Failure From-07:20 to 07:26 & Grid Failure After Inverter No-2&3 not wake up Due to Emergency stop Reset the Err code Inverter started-08:23 WO# | 26948606 26948608 | 714
2017-06-07 | 961 | 1103 | 1040 | 1144 | 32.58 | 4280.58 | 4087.5 | 193.08 | 4325 | 6.01 | 70.14% | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840, & Cloudy Day |  | 840
2017-06-08 | 899 | 1034 | 973 | 1139 | 30 | 4075 | 3904.5 | 170.5 | 4110 | 5.6 | 71.53% | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, & Cloudy Day |  | 777
2017-06-09 | 820 | 944 | 910 | 1049 | 29.89 | 3752.89 | 3614.25 | 138.64 | 3802 | 5.15 | 71.95% | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, & Cloudy Day |  | 624
2017-06-10 | 825 | 967 | 933 | 1038 | 29.04 | 3792.04 | 3597 | 195.04 | 3835 | 4.88 | 76.59% | Cloudy & Rainy Day & Module Clean by Rain & Grid Failure From-07:27 to 07:37 WO# | 26954215
2017-06-11 | 995 | 1165 | 1113 | 1230 | 35.31 | 4538.31 | 4355.25 | 183.06 | 4575 | 6.3 | 70.78% | Cloudy & Rainy Day & Module Clean by Rain & Grid Failure From-07:22 to 07:32 WO# | 26954295
2017-06-12 | 995 | 1176 | 1137 | 1245 | 36.28 | 4589.28 | 4374 | 215.28 | 4620 | 6.33 | 71.14% | Cloudy & Rainy Day & Module Clean by Rain
2017-06-13 | 1006 | 1175 | 1136 | 1144 | 36.86 | 4497.86 | 4353.75 | 144.11 | 4525 | 6.42 | 68.7% | Module cleaning done inverter -4 & Row-,A,B,C,D,E,F,G, & Total module cleaning -992, & Cloudy Day |  | 992
2017-06-14 | 990 | 1165 | 1119 | 1255 | 36.58 | 4565.58 | 4382.25 | 183.33 | 4595 | 6.42 | 69.76% | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864, & Cloudy Day |  | 864
2017-06-15 | 932 | 1091 | 1052 | 1164 | 33.12 | 4272.12 | 4087.5 | 184.62 | 4310 | 5.97 | 70.36% | Today I Replaced The D.C.12Amp Fuse Link of The String-03++tive in AJB-112 of The Inverter-3 during The Period of 09:10 to 09:20 & string no-3++tive line AJB-117 Inverter no-3 During the period of 9:25 to 9:35 & Cloudy Day WO#
2017-06-16 | 905 | 1063 | 1063 | 1190 | 33.21 | 4254.21 | 4084.5 | 169.71 | 4290 | 5.91 | 70.75% | Today I Replaced The D.C.12Amp Fuse Link of The String-04++tive in AJB-104 of The Inverter-4 during The Period of 09:00 to 09:10 & string no-2--tive line AJB-105 Inverter no-4 During the period of 9:15 to 9:25 & Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690 & Cloudy Day WO# |  | 690
2017-06-17 | 876 | 1040 | 1051 | 1149 | 31.97 | 4147.97 | 3967.5 | 180.47 | 4175 | 5.72 | 71.14% | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714,& cloudy Day |  | 714
2017-06-18 | 860 | 1029 | 1041 | 1119 | 31.9 | 4080.9 | 3896.25 | 184.65 | 4115 | 5.68 | 70.61% | cloudy day & Sunday No Module cleaning
2017-06-19 | 836 | 995 | 994 | 1074 | 28.91 | 3927.91 | 3786.75 | 141.16 | 3970 | 5.43 | 71.26% | Module cleaning done inverter -3 & Row-,M,N,O,P,Q,R,S,T, & Total module cleaning -992, & Cloudy Day |  | 992
2017-06-20 | 803 | 950 | 962 | 1013 | 29.76 | 3757.76 | 3588 | 169.76 | 3800 | 5.21 | 71.09% | Module cleaning done inverter -2 & Row-,I,J,K,L, & Total module cleaning -1092, & Cloudy Day |  | 992
2017-06-21 | 820 | 961 | 961 | 1043 | 30.63 | 3815.63 | 3732.75 | 82.88 | 3860 | 5.29 | 71.12% | Module cleaning done inverter -1 & Row-,A,B,C,D,E,F,G,H, & Total module cleaning -1113, & Grid Failure From-08:26 to 08:36 & Fully Cloudy Day | 26989259 | 1113
2017-06-22 | 557 | 850 | 870 | 937 | 26.62 | 3240.62 | 3214.5 | 26.12 | 3500 | 4.67 | 73.05% | Rainy & cloudy day, No Module clean by Rain
2017-06-23 | 905 | 1063 | 1066 | 1140 | 33.77 | 4207.77 | 4045.5 | 162.27 | 4251 | 5.72 | 72.43% | Rainy & cloudy day, No Module clean by Rain & Grid Failure From-08:to 08:50 & 10:15 TO 10:20 WO#
2017-06-24 | 910 | 1052 | 1052 | 1149 | 34.01 | 4197.01 | 3964.5 | 232.51 | 4240 | 5.63 | 73.4% | Rainy & cloudy day
2017-06-25 | 842 | 972 | 978 | 1018 | 29.84 | 3839.84 | 3745.5 | 94.34 | 3884 | 5.21 | 72.66% | Rainy & cloudy day
2017-06-26 | 781 | 882 | 893 | 932 | 28.95 | 3516.95 | 3300.75 | 216.2 | 3563 | 4.75 | 73.11% | Rainy & cloudy day
2017-06-27 | 384 | 430 | 430 | 409 | 13.49 | 1666.49 | 1613.25 | 53.24 | 1734 | 2.34 | 72.22% | Rainy & cloudy day & Grid Failure From-11:01 to 11:11 & 13:18 to 13:47 & 13:53 to 14:33 & 14:42 to 16:01 & 16:57 to 17:54 WO# | 26997787 26997809 26997810 26997811 26997888
2017-06-28 | 673 | 769 | 774 | 816 | 22.68 | 3054.68 | 2889 | 165.68 | 3101 | 4.11 | 73.54% | Rainy & cloudy day & Grid Failure From-11:08 to 11:26 WO# | 27002161
2017-06-29 | 565 | 639 | 645 | 670 | 19.1 | 2538.1 | 2412.75 | 125.35 | 2580 | 3.35 | 75.06% | Rainy & cloudy day
2017-06-30 | 605 | 644 | 655 | 726 | 21.39 | 2651.39 | 2506.5 | 144.89 | 2722 | 3.61 | 73.49% | Rainy & cloudy day
2017-07-01 | 277 | 305 | 300 | 313 | 8.31 | 1203.31 | 1090 | 113.31 | 1242 | 1.52 | 79.64% | Rainy & cloudy day
2017-07-02 | 204 | 232 | 237 | 250 | 5.77 | 928.77 | 738 | 190.77 | 960 | 1.23 | 76.07% | Rainy & cloudy day
2017-07-03 | 192 | 221 | 181 | 203 | 6.09 | 803.09 | 790.5 | 12.59 | 882 | 1.18 | 72.85% | Rainy & cloudy day
2017-07-04 | 718 | 836 | 831 | 882 | 23.85 | 3290.85 | 3091.5 | 199.35 | 3332 | 4.33 | 75% | Rainy & cloudy day
2017-07-05 | 848 | 1001 | 984 | 1064 | 32.41 | 3929.41 | 3746.25 | 183.16 | 3952 | 5.32 | 72.4% | Rainy & cloudy day
2017-07-06 | 870 | 1029 | 1017 | 1089 | 31.92 | 4036.92 | 3867 | 169.92 | 4100 | 5.58 | 71.61% | Rainy & cloudy day
2017-07-07 | 865 | 1023 | 1007 | 1088 | 33.01 | 4016.01 | 3863.25 | 152.76 | 4042 | 5.53 | 71.24% | Rainy & cloudy day
2017-07-08 | 939 | 1114 | 1085 | 1195 | 35.47 | 4368.47 | 4224.75 | 143.72 | 4412 | 5.9 | 72.88% | Rainy & cloudy day & Grid Failure From-09:52 to 09:56
2017-07-09 | 893 | 1063 | 1046 | 1134 | 38.83 | 4174.83 | 3957 | 217.83 | 4204 | 5.73 | 71.51% | Rainy & cloudy day
2017-07-10 | 910 | 1068 | 1057 | 1149 | 36.46 | 4220.46 | 4077.75 | 142.71 | 4252 | 5.77 | 71.82% | Rainy & cloudy day
2017-07-11 | 498 | 571 | 560 | 590 | 16.62 | 2235.62 | 2109.75 | 125.87 | 2294 | 2.8 | 79.85% | Rainy & cloudy day
2017-07-12 | 435 | 503 | 486 | 519 | 14.08 | 1957.08 | 1851.75 | 105.33 | 1994 | 2.47 | 78.68% | Rainy & cloudy day
2017-07-13 | 628 | 730 | 724 | 771 | 25.46 | 2878.46 | 2727 | 151.46 | 2932 | 3.82 | 74.81% | Rainy & cloudy day
2017-07-14 | 378 | 441 | 424 | 459 | 13.28 | 1715.28 | 1611 | 104.28 | 1772 | 2.17 | 79.59% | Rainy & cloudy day
2017-07-15 | 328 | 429 | 418 | 448 | 13.27 | 1636.27 | 1557 | 79.27 | 1742 | 2.21 | 76.83% | Rainy & cloudy day
2017-07-16 | 368 | 379 | 368 | 368 | 10.02 | 1493.02 | 1332 | 161.02 | 1482 | 1.83 | 78.93% | Rainy & cloudy day & Grid Failure From-16:50 to 17:18 & 17:26 to 17:33
2017-07-17 | 712 | 837 | 825 | 882 | 24.94 | 3280.94 | 3123 | 157.94 | 3322 | 4.52 | 71.63% | Rainy & cloudy day
2017-07-18 | 871 | 1029 | 989 | 1099 | 35.06 | 4023.06 | 3848.25 | 174.81 | 4062 | 5.56 | 71.21% | Rainy & cloudy day & Grid Failure From-15:00 to 15:03
2017-07-19 | 848 | 989 | 956 | 1058 | 30.44 | 3881.44 | 3720.75 | 160.69 | 3922 | 5.35 | 71.45% | Rainy & cloudy day & Grid Failure From-09:44 to 09:47
2017-07-20 | 480 | 560 | 537 | 585 | 15.73 | 2177.73 | 2083.5 | 94.23 | 2242 | 2.92 | 74.84% | Rainy & cloudy day
2017-07-21 | 848 | 995 | 955 | 1079 | 29.25 | 3906.25 | 3735 | 171.25 | 3942 | 5.34 | 71.95% | Rainy & cloudy day
2017-07-22 | 74 | 96 | 91 | 80 | 1.42 | 342.42 | 243.75 | 98.67 | 398 | 0.61 | 63.59% | Rainy & cloudy day & Grid Failure From-09:02 to 09:19 & 15:24 to 15:27 & 15:43 to 15:48
2017-07-23 | 231 | 277 | 265 | 278 | 4.95 | 1055.95 | 941 | 114.95 | 1112 | 1.38 | 78.54% | Rainy & cloudy day
2017-07-24 | 102 | 124 | 125 | 121 | 1.54 | 473.54 | 375 | 98.54 | 523 | 0.716 | 71.19% | Rainy & cloudy day
2017-07-25 | 142 | 170 | 164 | 166 | 2.64 | 644.64 | 543 | 101.64 | 693 | 0.907 | 74.47% | Rainy & cloudy day
2017-07-26 | 73 | 90 | 85 | 86 | 1 | 335 | 231.75 | 103.25 | 386 | 0.59 | 63.77% | Rainy & cloudy day
2017-07-27 | 136 | 176 | 169 | 166 | 2.57 | 649.57 | 537.75 | 111.82 | 703 | 0.981 | 69.85% | Rainy & cloudy day
2017-07-28 | 543 | 650 | 628 | 680 | 14.4 | 2515.4 | 2379.75 | 135.65 | 2560 | 3.26 | 76.54% | Rainy & cloudy day
2017-07-29 | 774 | 932 | 893 | 988 | 29.06 | 3616.06 | 3416.25 | 199.81 |  |  | #DIV/0! | Rainy & cloudy day & 11 KV Switch yard Site GOD Switch Repleced 'R' Phase cable & Luges,
2017-07-30 | 577 | 690 | 690 | 731 | 20.53 | 2708.53 | 2618.25 | 90.28 |  |  | #DIV/0! | Today I Replaced The 2 D.C.12Amp Fuse Link of The String-04--tive in AJB-113 of The Inverter-3 during The Period of 09:40 to 09:50 & string no-2++tive line AJB-101 Inverter no-4 During the period of 10:50 to 11:00 &Today Replaced 1 MC4 Connecter string No-8 AJB No-117 Inverter No-3 Durring The period 9:30 to 9:40 & Grid Failure From-14:23 to 14:36 & Rainy & cloudy day
2017-07-31 | 497 | 594 | 593 | 620 | 17.94 | 2321.94 | 2181 | 140.94 |  |  | #DIV/0! | Grid Failure From-16:49 to 17:02 & Rainy & cloudy day
2017-08-01 | 769 | 910 | 910 | 988 | 24.13 | 3601.13 | 3447.75 | 153.38 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-02 | 560 | 661 | 667 | 685 | 19.08 | 2592.08 | 2469.75 | 122.33 |  |  | #DIV/0! | Grid Failure From-11:20 to 17:24,16:41 to 16:44 & 16:47 to 16:57 & Rainy & cloudy day
2017-08-03 | 842 | 990 | 996 | 1069 | 31.45 | 3928.45 | 3745.5 | 182.95 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-04 | 775 | 916 | 910 | 978 | 29.92 | 3608.92 | 3451.5 | 157.42 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-05 | 531 | 616 | 616 | 635 | 19.24 | 2417.24 | 2292 | 125.24 |  |  | #DIV/0! | Grid Failure From-8:53 to 9:33 & Rainy & cloudy day
2017-08-06 | 871 | 1023 | 1023 | 1073 | 31.91 | 4021.91 | 3849 | 172.91 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-07 | 537 | 633 | 639 | 323 | 19.19 | 2151.19 | 2013 | 138.19 |  |  | #DIV/0! | Today Morning time Inverter No:-4 not wake up due to error code (Run Disable:-8194).five time reset the Err code After Inverter started 14:50 & Rainy & cloudy day
2017-08-08 | 718 | 843 | 842 | 897 | 25.89 | 3325.89 | 3187.5 | 138.39 |  |  | #DIV/0! | Rainy & cloudy day & Morning time plant checking time 1 module crack found . Inverter-4 Row-D Up Line module No-5 Sr No :-BPC10BU1109685(By mistack Module Crack by garden boy)
2017-08-09 | 808 | 944 | 945 | 1023 | 30.01 | 3750.01 | 3581.25 | 168.76 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-10 | 797 | 950 | 949 | 1039 | 30.76 | 3765.76 | 3603.75 | 162.01 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-11 | 611 | 780 | 781 | 851 | 25.85 | 3048.85 | 2908.5 | 140.35 |  |  | #DIV/0! | Today Inverter No :-1 ABB 250kw morning time not wake up due to emergency stop reset the Errore code Inverter started at:-09:14
2017-08-12 | 576 | 678 | 683 | 721 | 20.57 | 2678.57 | 2542.5 | 136.07 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-13 | 611 | 712 | 719 | 751 | 21.35 | 2814.35 | 2669.25 | 145.1 |  |  | #DIV/0! | Grid Failure From-09:23 to 09:33 & Rainy & cloudy day
2017-08-14 | 690 | 815 | 813 | 857 | 26.64 | 3201.64 | 3047.25 | 154.39 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-15 | 791 | 921 | 922 | 968 | 28.76 | 3630.76 | 3444.75 | 186.01 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-16 | 910 | 1074 | 1080 | 1157 | 33.53 | 4254.53 | 4101.75 | 152.78 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-17 | 843 | 995 | 995 | 1058 | 32.07 | 3923.07 | 3759 | 164.07 |  |  | #DIV/0! | cloudy day
2017-08-18 | 904 | 1069 | 1063 | 1144 | 34.3 | 4214.3 | 4039.5 | 174.8 |  |  | #DIV/0! | Module cleaning has Been done In Row-A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -792 |  | 792
2017-08-19 | 588 | 690 | 689 | 731 | 21.17 | 2719.17 | 2600.25 | 118.92 |  |  | #DIV/0! | Module cleaning has Been done In Row-G,H,I,J,K,L Inverter N0-4 & Total module cleaning -1122 |  | 1122
2017-08-20 | 249 | 293 | 300 | 308 | 5.67 | 1155.67 | 1033.5 | 122.17 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-21 | 876 | 1046 | 1040 | 1129 | 31.99 | 4122.99 | 3929.25 | 193.74 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-22 | 809 | 944 | 939 | 1043 | 30 | 3765 | 3600 | 165 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-23 | 356 | 413 | 418 | 428 | 12.3 | 1627.3 | 1509.75 | 117.55 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-24 | 885 | 1018 | 1012 | 1109 | 33.27 | 4057.27 | 3861.75 | 195.52 |  |  | #DIV/0! | Rainy & cloudy day
2017-08-25 | 955 | 1125 | 1120 | 1225 | 35.7 | 4460.7 | 4288.5 | 172.2 | 4512 | 6.13 | 71.74% | Fully cloudy day
2017-08-26 | 820 | 949 | 961 | 1013 | 30.23 | 3773.23 | 3609 | 164.23 | 3800 | 4.95 | 74.82% | Fully cloudy day
2017-08-27 | 616 | 730 | 723 | 771 | 23.09 | 2863.09 | 2723.25 | 139.84 | 2900 |  | #DIV/0! | Rainy & cloudy day
2017-08-28 | 639 | 752 | 752 | 812 | 26.44 | 2981.44 | 2808.75 | 172.69 | 3032 | 4.12 | 71.73% | Rainy & cloudy day
2017-08-29 | 565 | 661 | 667 | 705 | 21.72 | 2619.72 | 2478 | 141.72 | 2674 | 3.48 | 74.89% | Rainy & cloudy day
2017-08-30 | 560 | 650 | 656 | 711 | 20.61 | 2597.61 | 2433 | 164.61 | 2642 | 3.54 | 72.74% | Grid Failure From 11:14 to 11:24 , Rainy & Cloudy day
2017-08-31 | 430 | 498 | 497 | 509 | 15.37 | 1949.37 | 1849 | 100.37 | 2000 | 2.55 | 76.44% | Grid Failure From 10:02 to 10:07 & 11:15 to 11:18 ,Rainy & Cloudy day
2017-09-01 | 836 | 983 | 978 | 1074 | 32.97 | 3903.97 | 3729.75 | 174.22 | 3942 | 5.43 | 70.76% | Rainy & cloudy day
2017-09-02 | 402 | 470 | 475 | 489 | 14.53 | 1850.53 | 1736 | 114.53 | 1910 | 2.44 | 76.3% | Grid Failure From 07:36 to 07:39, Rainy & Cloudy day
2017-09-03 | 594 | 689 | 696 | 725 | 21.33 | 2725.33 | 2566 | 159.33 | 2772 | 3.64 | 74.22% | Rainy & cloudy day
2017-09-04 | 678 | 798 | 797 | 847 | 25.36 | 3145.36 | 2998 | 147.36 | 3190 | 4.21 | 73.85% | Rainy & cloudy day
2017-09-05 | 899 | 1062 | 1057 | 1129 | 35.63 | 4182.63 | 4013.25 | 169.38 | 4230 | 5.78 | 71.33% | Rainy & cloudy day
2017-09-06 | 910 | 1069 | 1074 | 1129 | 35.61 | 4217.61 | 4013.25 | 204.36 | 4242 | 5.83 | 70.92% | Rainy & cloudy day
2017-09-07 | 1001 | 1187 | 1182 | 1240 | 39.49 | 4649.49 | 4482 | 167.49 | 4690 | 6.6 | 69.26% | Rainy & cloudy day
2017-09-08 | 916 | 1080 | 1091 | 1109 | 36.1 | 4232.1 | 4046 | 186.1 | 4255 | 5.89 | 70.41% | Module cleaning has Been done In Row-A,B,C Inverter N0-4 & Total module cleaning -288
2017-09-09 | 994 | 1142 | 1136 | 1230 | 38.96 | 4540.96 | 4362 | 178.96 | 4581 | 6.89 | 64.8% | Module cleaning has Been done In Row-D,E,F Inverter N0-4 & Total module cleaning -504
2017-09-10 | 792 | 933 | 933 | 963 | 31.61 | 3652.61 | 3489 | 163.61 | 3685 | 5.05 | 71.12% | cloudy day
2017-09-11 | 826 | 972 | 967 | 1028 | 33.28 | 3826.28 | 3656.25 | 170.03 | 3860 | 5.38 | 69.93% | Rainy & cloudy day
2017-09-12 | 842 | 1001 | 1001 | 1063 | 34.7 | 3941.7 | 3779 | 162.7 | 3965 | 5.6 | 69.01% | Rainy & cloudy day
2017-09-13 | 667 | 780 | 780 | 807 | 28.03 | 3062.03 | 2924 | 138.03 | 3120 | 4.41 | 68.96% | Grid Failure From 14:31 to 14:35 & 14:42 to 14:49 ,Rainy & Cloudy day
2017-09-14 | 893 | 1052 | 1045 | 1093 | 34.21 | 4117.21 | 3937 | 180.21 | 4153 | 5.71 | 70.89% | Rainy & cloudy day
2017-09-15 | 922 | 1085 | 1080 | 1139 | 36.73 | 4262.73 | 4089 | 173.73 | 4290 | 5.98 | 69.92% | Rainy & cloudy day
2017-09-16 | 565 | 656 | 662 | 701 | 22.62 | 2606.62 | 2460.75 | 145.87 |  |  | #DIV/0! | Grid Failure From 10:38 to 10:43 ,Rainy & Cloudy day & Today Night Many Time Grid Failure After High Voltage, 2 Power supply Failure, 1 SEEDS, & 2. SCADA
2017-09-17 | 775 | 899 | 893 | 922 | 29.03 | 3518.03 | 3362.25 | 155.78 |  |  | #DIV/0! | Grid Failure From 14:08 to 14:14 ,Rainy & Cloudy day
2017-09-18 | 904 | 1051 | 1046 | 1109 | 36.52 | 4146.52 | 3972 | 174.52 |  |  | #DIV/0! | cloudy day
2017-09-19 | 669 | 780 | 774 | 776 | 25.19 | 3024.19 | 2889 | 135.19 |  |  | #DIV/0! | Grid Failure From 10:35 to 10:40 , 11:33 to 12:44 , 14:20 to 15:14, Cloudy day & Grid Failure After High voltage MOXA SEEDA Unit power supply Failure,
2017-09-20 | 990 | 1182 | 1176 | 1215 | 39.44 | 4602.44 | 4429.5 | 172.94 | 4643 |  | #DIV/0! | Grid Failure From 08:43 to 08:49 & 10:17 to 10:22 ,Cloudy day
2017-09-21 | 707 | 690 | 690 | 822 | 27.14 | 2936.14 | 2793.75 | 142.39 | 2994 |  | #DIV/0! | Grid Failure From 17:25 to 17:27, Fully Cloudy day
2017-09-22 | 587 | 638 | 667 | 736 | 24.22 | 2652.22 | 2526 | 126.22 | 2710 |  | #DIV/0! | Today AMC MaintanCe for ABB Inverter no-1,2,3,
2017-09-23 | 1001 | 1188 | 1182 | 1240 | 40.33 | 4651.33 | 4463.25 | 188.08 | 4700 |  | #DIV/0! | GrId Failure From-17:13 to 17:18
2017-09-24 | 808 | 944 | 944 | 967 | 32.16 | 3695.16 | 3526.5 | 168.66 | 3734 |  | #DIV/0! | cloudy day
2017-09-25 | 962 | 1063 | 1062 | 1144 | 38.4 | 4269.4 | 4098 | 171.4 | 4321 |  | #DIV/0! | Module cleaning has Been done In Row-A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -792 |  | 792
2017-09-26 | 921 | 1091 | 1086 | 1165 | 36.28 | 4299.28 | 4119 | 180.28 | 4332 |  | #DIV/0! | Module cleaning has Been done In Row-,G,H,I,J,K,L, Inverter N0-4 & Total module cleaning -1062 & Grid Failure From-10:42 to 10:50 & 12:01 to 12:06 |  | 1062
2017-09-27 | 995 | 1181 | 1187 | 1255 | 40.28 | 4658.28 | 4471.5 | 186.78 | 4681 |  | #DIV/0! | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, |  | 690
2017-09-28 | 1018 | 1154 | 1170 | 1290 | 41.02 | 4673.02 | 4491 | 182.02 | 4704 |  | #DIV/0! | Module cleaning done inverter -3, Row-M,N & Total module cleaning -462, Grid Failure from 8:25 to 8:45,12:00 to 12:04, 16:33 to 16:36 |  | 462
2017-09-29 | 1051 | 1249 | 1267 | 1326 | 42.18 | 4935.18 | 4725.75 | 209.43 | 4980 |  | #DIV/0! | Module cleaning done inverter -2, Row-K,L & Total module cleaning -525, Grid Failure from 7:20 to 7:30 |  | 525
2017-09-30 | 1040 | 1215 | 1210 | 1290 | 41.82 | 4796.82 | 4598.25 | 198.57 | 4840 |  | #DIV/0! | Module cleaning done inverter -2, Row-J,I & Total module cleaning -567, |  | 567
2017-10-01 | 1041 | 1267 | 1249 | 1290 | 41.64 | 4888.64 | 4690.5 | 198.14 | 4934 |  | #DIV/0! | Sunday No Module Cleaning
2017-10-02 | 1034 | 1249 | 1227 | 1240 | 41.01 | 4791.01 | 4596 | 195.01 | 4830 |  | #DIV/0! | Today I Replaced The 3 D.C.12Amp Fuse, Link of The String-02++tive in AJB-101 of The Inverter-4 during The Period of 17:45 to 17:50 & string no-6--tive line AJB-104 Inverter no-4 During the period of 18:00 to 18:05 & string 02--tive line AJB-105 Inverter No-4 Durring The period 18:10 to 18:15 & Module cleaning done inverter -1, Row-A,B,C,D,E,F,G,H, & Total module cleaning -1113, |  | 1113
2017-10-03 | 1012 | 1187 | 1170 | 1230 | 39.47 | 4638.47 | 4429.5 | 208.97 | 4771 |  | #DIV/0! | Module cleaning has Been done In Row-A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -792 |  | 792
2017-10-04 | 1035 | 1210 | 1193 | 1300 | 40.13 | 4778.13 | 4596 | 182.13 | 4814 |  | #DIV/0! | Module cleaning has Been done In Row-G,H,I,J, Inverter N0-4 & Total module cleaning -774 & Grid Failure from 17:10 to 17:19 |  | 774
2017-10-05 | 1012 | 1193 | 1170 | 1296 | 40.13 | 4711.13 | 4516.5 | 194.63 | 4744 |  | #DIV/0! | Module cleaning has Been done In Row-K,L, & R,S,T, & trackers ,Inverter N0-4,3, & Total module cleaning -516 & Grid Failure from 10:45 to 10:47 |  | 516
2017-10-06 | 859 | 989 | 990 | 1063 | 34.67 | 3935.67 | 3773.25 | 162.42 | 3985 |  | #DIV/0! | Module cleaning has Been done In Row-,M,N,O,P,Q, Inverter N0-3 & Total module cleaning -924 & Grid Failure from 13:08 to 13:35 |  | 924
2017-10-07 | 972 | 1160 | 1159 | 1235 | 39.25 | 4565.25 | 4379.25 | 186 | 4610 |  | #DIV/0! | Module cleaning has Been done In Row-J,K,L, Inverter N0-2 & Total module cleaning -819 & Grid Failure from 10:46 to 10:50 |  | 819
2017-10-08 | 1007 | 1209 | 1193 | 1260 | 40.65 | 4709.65 | 4513.5 | 196.15 | 4750 |  | #DIV/0! | Sunday No Module Cleaning
2017-10-09 | 887 | 1063 | 1040 | 1089 | 35.85 | 4114.85 | 3950.25 | 164.6 | 4170 |  | #DIV/0! | Module cleaning has Been done In Row-F,G,H,I, Inverter N0-1,2 & Total module cleaning -903 & Grid Failure from 13:08 to 13:11 |  | 903
2017-10-10 | 860 | 1006 | 983 | 1043 | 35.41 | 3927.41 | 3753.75 | 173.66 | 3970 |  | #DIV/0! | Module cleaning has Been done In (Row-A,B,C,D,E Inverter N0-1), (Row-A,B Inverter N0-4) & Total module cleaning -642 & Grid Failure from-11:13 to 11:18 & 13:46 to 14:26 |  | 642
2017-10-11 | 429 | 486 | 481 | 494 | 15.43 | 1905.43 | 1788 | 117.43 | 1960 |  | #DIV/0! | Fully cloudy day & Borwall Failure No Module cleaning
2017-10-12 | 402 | 453 | 447 | 459 | 13.96 | 1774.96 | 1650 | 124.96 | 1830 |  | #DIV/0! | Fully cloudy day & Borwall Failure No Module cleaning
2017-10-13 | 667 | 769 | 752 | 801 | 26 | 3015 | 2880 | 135 | 3082 |  | #DIV/0! | Fully cloudy day & Borwall Failure No Module cleaning
2017-10-14 | 949 | 1119 | 1096 | 1164 | 37.57 | 4365.57 | 4182.25 | 183.32 | 4411 |  | #DIV/0! | Fully cloudy day & Borwall Failure No Module cleaning
2017-10-15 | 933 | 1097 | 1069 | 1134 | 36.94 | 4269.94 | 4091.25 | 178.69 | 4320 |  | #DIV/0! | Sunday No module cleaning
2017-10-16 | 990 | 1165 | 1136 | 1220 | 39.46 | 4550.46 | 4369.5 | 180.96 | 4600 |  | #DIV/0! | Module cleaning has Been done In Row-G,H,I, Inverter N0-4& Total module cleaning -594 |  | 594
2017-10-17 | 1017 | 1198 | 1164 | 1275 | 40.26 | 4694.26 | 4498.5 | 195.76 | 4740 |  |  | No module cleaning
2017-10-18 | 1029 | 1221 | 1188 | 1306 | 41.25 | 4785.25 | 4588.5 | 196.75 | 4830 |  | #DIV/0! | No module cleaning
2017-10-19 | 973 | 1142 | 1114 | 1209 | 39.84 | 4477.84 | 4285.5 | 192.34 | 4523 |  | #DIV/0! | Holiday No module cleaning
2017-10-20 | 842 | 984 | 961 | 1008 | 35.17 | 3830.17 | 3669.75 | 160.42 | 3890 |  | #DIV/0! | Grid Failure from :- 9:07 to 9:10, 9:33 to 9:36, 11:20 to 11:32, 12:44 to 12:48, 13:30 to 13:37, 14:11 to 14:17
2017-10-21 | 848 | 989 | 961 | 998 | 35.91 | 3831.91 | 3660.75 | 171.16 | 3880 |  | #DIV/0! | Grid Failure from:-8:13 to 8:29, 9:23 to 9:34, 13:45 to 13:54
2017-10-22 | 984 | 1153 | 1125 | 1245 | 40.7 | 4547.7 | 4356.75 | 190.95 | 4590 |  | #DIV/0! | cloudy day
2017-10-23 | 966 | 1148 | 1125 | 1240 | 40.78 | 4519.78 | 4334.25 | 185.53 | 4565 |  | #DIV/0! | Module cleaning has Been done In Row-O,P,Q,R,S,T, Inverter N0-3 & Total module cleaning -630 |  | 630
2017-10-24 | 950 | 1119 | 1136 | 1210 | 39.82 | 4454.82 | 4266 | 188.82 | 4492 |  | #DIV/0! | Module cleaning has Been done In Row-L,M,N, Inverter N0-3,2 & Total module cleaning -714 |  | 714
2017-10-25 | 973 | 1176 | 1199 | 1240 | 40.74 | 4628.74 | 4442.25 | 186.49 | 4670 |  | #DIV/0! | No module cleaning
2017-10-26 | 938 | 1125 | 1147 | 1169 | 39.59 | 4418.59 | 4230 | 188.59 | 4460 |  | #DIV/0! | Module cleaning has Been done In Row-,I,J,K, Inverter N0-2 & Total module cleaning -840 |  | 840
2017-10-27 | 871 | 1069 | 1057 | 1069 | 37.1 | 4103.1 | 3926.25 | 176.85 | 4150 |  | #DIV/0!
2017-10-28 | 876 | 1091 | 1069 | 1073 | 37.37 | 4146.37 | 3976.5 | 169.87 | 4200 |  | #DIV/0!
2017-10-29 | 848 | 1057 | 1024 | 1028 | 36.24 | 3993.24 | 3825.75 | 167.49 | 4042 |  | #DIV/0! | GrId Failure From-08:14 to 08:18
2017-10-30 | 888 | 1103 | 1074 | 1084 | 38.01 | 4187.01 | 4006.5 | 180.51 | 4230 |  | #DIV/0!
2017-10-31 | 898 | 1108 | 1074 | 1089 | 37.84 | 4206.84 | 4022.25 | 184.59 | 4243 |  | #DIV/0! | Module cleaning has Been done In Row-E,F,G,H, Inverter N0-1 & Total module cleaning -777 |  | 777
2017-11-01 | 888 | 1040 | 1001 | 993 | 36.39 | 3958.39 | 3790.5 | 167.89 | 4020 |  | #DIV/0! | Module cleaning has Been done In Row-A,B,C,D, Inverter N0-1 & Total module cleaning -336 & Grid Failure From :-16:33 to 16:36 & Replaced New Earthnet Moxa switch |  | 336
2017-11-02 | 882 | 1029 | 995 | 993 | 36.01 | 3935.01 | 3756 | 179.01 | 3980 |  | #DIV/0! | Module cleaning has Been done In Row-A,B,C,D, Inverter N0-4 & Total module cleaning -432 |  | 432
2017-11-03 | 921 | 1080 | 1040 | 1071 | 37.2 | 4149.2 | 3971.25 | 177.95 | 4202 |  | #DIV/0! | Module cleaning has Been done In Row-,E,F,G,H, Inverter N0-4 & Total module cleaning -756 |  | 756
2017-11-04 | 865 | 921 | 888 | 1025 | 35.3 | 3734.3 | 3559.5 | 174.8 | 3790 |  | #DIV/0! | Module cleaning has Been done In Row-I,J, Inverter N0-4 & Total module cleaning -378 |  | 378
2017-11-05 | 815 | 938 | 910 | 968 | 33.2 | 3664.2 | 3498 | 166.2 | 3710 |  | #DIV/0! | Sunday No Module Cleaning
2017-11-06 | 915 | 1075 | 1029 | 1144 | 37.53 | 4200.53 | 4012.5 | 188.03 | 4240 |  | #DIV/0! | Inverter 1 &2 & Main transformer replaced new silica gel ,Today install new cable for ups to scada.
2017-11-07 | 888 | 1017 | 978 | 1104 | 36.57 | 4023.57 | 3853.5 | 170.07 | 4080 |  | #DIV/0!
2017-11-08 | 876 | 1029 | 983 | 1099 | 37.36 | 4024.36 | 3837.75 | 186.61 | 4060 |  | #DIV/0! | Module cleaning has Been done In Row-K,L, & Trackers Inverter N0-4 & Total module cleaning -348 |  | 348
2017-11-09 | 814 | 944 | 922 | 993 | 35.58 | 3708.58 | 3540 | 168.58 | 3750 |  | #DIV/0! | Today Replaced New Plus Din Rail power supply For AJB & SCADA,& Module cleaning has Been done In Row-,O,P,Q,R,S,T, & Trackers Inverter N0-3 & Total module cleaning -630 |  | 630
2017-11-10 | 797 | 922 | 944 | 962 | 35.34 | 3660.34 | 3496.5 | 163.84 | 3710 |  | #DIV/0! | Module cleaning has Been done In Row-K,L,M, & Trackers Inverter N0-2&3 & Total module cleaning -777 & Grid Failure From-16:46 to 16:52 |  | 777
2017-11-11 | 798 | 955 | 955 | 963 | 35.28 | 3706.28 | 3533.25 | 173.03 | 3740 |  | #DIV/0! | Module cleaning has Been done In Row-I,J,K, & Inverter N0-2 & Total module cleaning -840 & Grid Failure From-17:04 to 17:12 |  | 840
2017-11-12 | 785 | 967 | 939 | 933 | 35.13 | 3659.13 | 3498.75 | 160.38 | 3710 |  | #DIV/0! | Sunday No Module cleaning
2017-11-13 | 792 | 961 | 933 | 927 | 34.95 | 3647.95 | 3486 | 161.95 | 3700 |  | #DIV/0! | Module cleaning has Been done In Row-E,F,G,H, & Inverter N0-1 & Total module cleaning -777 & Grid Failure From-13:57 to 14:01 |  | 777
2017-11-14 | 729 | 848 | 825 | 796 | 31.14 | 3229.14 | 3076 | 153.14 | 3260 |  | #DIV/0! | Module cleaning has Been done In Row-A,B,C,D, Inverter N0-1 & Row A,B, Inverter no -4 & Total module cleaning -498 |  | 498
2017-11-15 | 831 | 967 | 939 | 948 | 34.49 | 3719.49 | 3546 | 173.49 | 3780 |  | #DIV/0! | Module cleaning has Been done In Row-C,D,E, Inverter N0-4 & Total module cleaning -432 |  | 432
2017-11-16 | 871 | 1023 | 989 | 1043 | 36.57 | 3962.57 | 3791.25 | 171.32 | 4010 |  | #DIV/0! | Module cleaning has Been done In Row-F,G,H, Inverter N0-4 & Total module cleaning -574 |  | 574
2017-11-17 | 803 | 933 | 905 | 953 | 34.02 | 3628.02 | 3465 | 163.02 | 3680 |  | #DIV/0! | Module cleaning has Been done In Row-I,J,K, Inverter N0-4 & Total module cleaning -540 |  | 540
2017-11-18 | 780 | 910 | 882 | 932 | 33.62 | 3537.62 | 3372 | 165.62 | 3580 |  | #DIV/0! | Module cleaning has Been done In Row-L, Inverter N0-4 & Solar Trakers & Row-Q,R,S,T, Inverter no-3 , Total module cleaning -480 & Grid Failur From 8:30 to 8:35 |  | 480
2017-11-19 | 763 | 888 | 876 | 918 | 33.28 | 3478.28 | 3315 | 163.28 | 3530 |  | #DIV/0! | Sunday No Module Cleaning & Grid failure from 10:20 to 10:38
2017-11-20 | 735 | 848 | 853 | 846 | 32.24 | 3314.24 | 3157.5 | 156.74 | 3370 |  | #DIV/0! | Module cleaning has Been done In Row-M,N,O,P, Inverter N0-3 & Total module cleaning -798 |  | 798
2017-11-21 | 746 | 887 | 882 | 898 | 32.71 | 3445.71 | 3283.5 | 162.21 | 3500 |  | #DIV/0! | Module cleaning has Been done In Row - J,K,L, Inverter N0-2 & Total module cleaning -819 & Grid Failure from 11:00 to 11:25 |  | 819
2017-11-22 | 842 | 1024 | 995 | 1003 | 36.98 | 3900.98 | 3726.75 | 174.23 | 3950 |  | #DIV/0! | Module cleaning has Been done In Row - ,G,H,I, Inverter N0-2&1 & Total module cleaning -714 & Grid Failure from 11:10 to 11:14 & 11:54 to 11:58 |  | 714
2017-11-23 | 899 | 1085 | 1040 | 1068 | 38.59 | 4130.59 | 3945.75 | 184.84 | 4170 |  | #DIV/0! | Module cleaning has Been done In Row - ,A,B,C,D,E,F, Inverter N0-1 & Total module cleaning -672 |  | 672
2017-11-24 | 922 | 1086 | 1052 | 1059 | 38.94 | 4157.94 | 4032 | 125.94 | 4200 |  | #DIV/0!
2017-11-25 | 950 | 1125 | 1085 | 1124 | 39.86 | 4323.86 | 4070.25 | 253.61 | 4370 |  | #DIV/0! | Module cleaning has Been done In Row - ,A,B,C,D,E, Inverter N0-4 & Total module cleaning -592 |  | 592
2017-11-26 | 910 | 1079 | 1035 | 1108 | 38.57 | 4170.57 | 3988.5 | 182.07 | 4220 |  | #DIV/0! | Sunday No Module Cleaning
2017-11-27 | 899 | 1063 | 1023 | 1104 | 38.46 | 4127.46 | 3951 | 176.46 | 4160 |  | #DIV/0! | Module cleaning has Been done In Row - F,G,H, Inverter N0-4 & Total module cleaning -594 |  | 594
2017-11-28 | 887 | 1046 | 1018 | 1081 | 38.53 | 4070.53 | 3879 | 191.53 | 4110 |  | #DIV/0! | Module cleaning has Been done In Row - ,I,J,K,L, & Trackers, Inverter N0-4 & Total module cleaning -726 |  | 726
2017-11-29 | 848 | 1000 | 1001 | 1026 | 37.26 | 3912.26 | 3738 | 174.26 | 3970 |  | #DIV/0! | Module cleaning has Been done In Row - ,O,P,Q,R,S,T, Inverter N0-3 & Total module cleaning -630 |  | 630
2017-11-30 | 831 | 990 | 983 | 1003 | 36.53 | 3843.53 | 3666.75 | 176.78 | 3890 |  | #DIV/0! | Module cleaning has Been done In Row - J,K,L, Inverter N0-2 & Total module cleaning -819 & Grid Failure From :-8:58 to 9:08 |  | 819
2017-12-01 | 860 | 1046 | 1012 | 1038 | 37.9 | 3993.9 | 3816.75 | 177.15 | 4050 |  | #DIV/0! | Module cleaning has Been done In Row - G,H,I, Inverter N0-1 & Inverter-2 & Total module cleaning -714 |  | 714
2017-12-02 | 763 | 904 | 877 | 882 | 32.34 | 3458.34 | 3309 | 149.34 | 3520 |  | #DIV/0! | Module cleaning has Been done In Row - A,B,C,D,E,F, Inverter N0-1 & Total module cleaning -672 |  | 672
2017-12-03 | 548 | 622 | 610 | 595 | 23.1 | 2398.1 | 2263.5 | 134.6 | 2450 |  | #DIV/0! | Sunday No Module Cleaning & Day was fully cloudy
2017-12-04 | 340 | 390 | 379 | 373 | 13.35 | 1495.35 | 1380.75 | 114.6 | 1550 |  | #DIV/0! | Module cleaning has Been done In Row - A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -772 & Fully Cloudy Day |  | 772
2017-12-05 | 39 | 46 | 45 | 45 | 1.16 | 176.16 | 86.25 | 89.91 | 239 |  | #DIV/0! | Module clean by Rain & Grid Failure From :-10:25 to 11:46, 13:15 to 13:23, 14:24 to 14:28, 15:25 to 16:49, 17:26 to 17:29 & Rainy & Fully Cloudy Day
2017-12-06 | 79 | 84 | 85 | 81 | 2.41 | 331.41 | 174 | 157.41 | 379 |  | #DIV/0! | Module clean by Rain & Grid Failure From :-09:37 to 12:40, & Rainy & Fully Cloudy Day
2017-12-07 | 605 | 696 | 695 | 691 | 25.27 | 2712.27 | 2640 | 72.27 | 2761 |  | #DIV/0! | Module clean by Rain & Rainy and cloudy day
2017-12-08 | 662 | 774 | 764 | 766 | 28.45 | 2994.45 | 2848.5 | 145.95 | 3040 |  | #DIV/0! | Cloudy day
2017-12-09 | 684 | 797 | 785 | 786 | 29.81 | 3081.81 | 2934 | 147.81 | 3123 |  | #DIV/0! | Module cleaning has been done in Row-A,B,C,D,E, Inverter no-4 & Total module cleaning-594 & Fully Cloudy Day |  | 594
2017-12-10 | 695 | 809 | 797 | 801 | 30.78 | 3132.78 | 2994 | 138.78 | 3190 |  | #DIV/0! | Sunday No Module Cleaning
2017-12-11 | 526 | 616 | 605 | 625 | 23.11 | 2395.11 | 2262 | 133.11 | 2450 |  | #DIV/0! | Fully cloudy weather & Grid failure from-15:48 to 15:53 & Module cleaning by rain
2017-12-12 | 871 | 1040 | 1012 | 1069 | 38.1 | 4030.1 | 3846.75 | 183.35 | 4063 |  | #DIV/0! | Module cleaning has been done in Row-A,B,C,D,E,F, Inverter no-4 & Total module cleaning-772 & Grid failure from 16:53 to 16:57 |  | 772
2017-12-13 | 927 | 1108 | 1091 | 1149 | 40.26 | 4315.26 | 4122.75 | 192.51 | 4350 |  | #DIV/0! | Module cleaning has been done in Row-,G,H,I, Inverter no-4 & Total module cleaning-594 |  | 594
2017-12-14 | 814 | 962 | 939 | 978 | 36.15 | 3729.15 | 3559.5 | 169.65 | 3770 |  | #DIV/0! | Module cleaning has been done in Row-,J,K,L, & Trackers Inverter no-4 & Total module cleaning-528 |  | 528
2017-12-15 | 673 | 774 | 775 | 771 | 28.78 | 3021.78 | 2868.75 | 153.03 | 3063 |  | #DIV/0! | Module cleaning has been done in Row-P,Q,R,S,T, &Inverter no-3 & Total module cleaning-441 |  | 441
2017-12-16 | 774 | 922 | 915 | 927 | 34.92 | 3572.92 | 3411 | 161.92 | 3614 |  | #DIV/0! | Module cleaning has been done in Row-M,N,O, &Inverter no-3 & Total module cleaning-651 & Grid failure from-9:31 to 9:48 |  | 651
2017-12-17 | 741 | 859 | 865 | 852 | 33.07 | 3350.07 | 3189.75 | 160.32 | 3394 |  | #DIV/0! | Sunday no module cleaning & Grid failure from-9:22 to 9:27
2017-12-18 | 831 | 1006 | 996 | 1033 | 37.28 | 3903.28 | 3723.75 | 179.53 | 3942 |  | #DIV/0! | Module cleaning has been done in Row-J,K,L, & Inverter no-2 & Total module cleaning-819 |  | 819
2017-12-19 | 480 | 526 | 508 | 540 | 20.08 | 2074.08 | 1956.75 | 117.33 | 2133 |  | #DIV/0! | Module cleaning has been done in Row-F,G,H,I, & Inverter no-1,2 & Total module cleaning-903 |  | 930
2017-12-20 | 464 | 531 | 509 | 519 | 18.74 | 2041.74 | 1916.25 | 125.49 | 2091 |  | #DIV/0! | Module cleaning has been done in Row-A,B,C,D,E & A,B & Inverter no-1,4 & Total module cleaning-645 |  | 645
2017-12-21 | 593 | 684 | 656 | 675 | 24.33 | 2632.33 | 2502 | 130.33 | 2690 |  | #DIV/0! | Today I Replaced The 1 D.C.12 Amp Fuse, Link of The String-09++tive in AJB-113 of The Inverter-3 during The Period of 15:10 to 15:15 & Module cleaning done inverter -4 Row-,C,D,E,F,G, & Total module cleaning -808 |  | 808
2017-12-22 | 515 | 583 | 571 | 590 | 21.25 | 2280.25 | 2149.5 | 130.75 | 2331 |  | #DIV/0! | Module cleaning has been done in Row-H,I,J,K,L, & Inverter no-4 & Total module cleaning-864 |  | 864
2017-12-23 | 842 | 994 | 967 | 1043 | 37.47 | 3883.47 | 3702.75 | 180.72 | 3930 |  | #DIV/0! | Module cleaning has been done in Row-Q,R,S,T, & Inverter no-3 & Total module cleaning-294 & Grid failure from-14:55 to 15:02 & Color working to AJB structure box-100 to 111 |  | 294
2017-12-24 | 894 | 1075 | 1051 | 1079 | 39.46 | 4138.46 | 3952.5 | 185.96 | 4180 |  | #DIV/0! | Sunday no module cleaning
2017-12-25 | 921 | 1096 | 1068 | 1104 | 40.75 | 4229.75 | 4039.5 | 190.25 | 4270 |  | #DIV/0! | Color working to AJB box & structure -112 to 118
2017-12-26 | 955 | 1149 | 1125 | 1164 | 42.17 | 4435.17 | 4240.5 | 194.67 | 4471 |  | #DIV/0! | Module cleaning has been done in Row-M,N,O,P &Inverter no-3 & Total module cleaning-798 & Grid failure from-9:03 to 9:10 |  | 798
2017-12-27 | 945 | 1135 | 1131 | 1159 | 41.45 | 4411.45 | 4215 | 196.45 | 4450 |  | #DIV/0! | PDPU BOR Failure No Module cleaning
2017-12-28 | 915 | 1092 | 1092 | 1099 | 39.93 | 4237.93 | 4034.25 | 203.68 | 4265 |  | #DIV/0! | Plant shut down for switchgear testing at 17:29 to 11:00
2017-12-29 | 849 | 1023 | 1005 | 993 | 37.61 | 3907.61 | 3773.25 | 134.36 | 3960 |  | #DIV/0! | Module cleaning has been done in Row-K,L, & Inverter no-2 & Total module cleaning-525 |  | 525
2017-12-30 | 836 | 1018 | 990 | 968 | 36.88 | 3848.88 | 3677.25 | 171.63 | 3890 |  | #DIV/0! | Today I Replaced The 1 D.C.12 Amp Fuse, Link of The String-08--tive in AJB-101 of The Inverter-4 during The Period of 10:50 to 10:55 & Module cleaning done inverter -1,2 Row-H,I,J, & Total module cleaning -798 & Grid failure from:-9:49 to 9:53 |  | 798
2017-12-31 | 786 | 949 | 916 | 892 | 34.68 | 3577.68 | 3414.75 | 162.93 | 3630 |  | #DIV/0! | Sunday No Module Cleaning
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!

## 2018
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2018
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | Total NO- Of Clean Modules
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 9175000042 | 9170301408 | 2100570073/ 2100567820/ 2100567898
2018-01-01 | 740 | 888 | 859 | 821 | 32.39 | 3340.39 | 3174 | 166.39 | 3424 |  | #DIV/0! | Module cleaning has been done in Row-A,B,C,D,E,F,G, & Inverter no-1 & Total module cleaning-882 & Grid failure from-13:22 to 13:51 |  | 882
1900-01-01 | 871 | 1023 | 984 | 953 | 37.57 | 3868.57 | 3697.5 | 171.07 | 3900 |  | #DIV/0! | Module cleaning has been done in Row-A,B,C,D,E, & Inverter no-4 & Total module cleaning-594 |  | 594
2018-01-03 | 893 | 1063 | 598 | 1033 | 38.39 | 3625.39 | 3467.25 | 158.14 | 3643 |  | #DIV/0! | Inverter-3 cut off at-13:10 due to installing a new inverter & Grid failure from-17:05 to 19:00
2018-01-04 | 831 | 1023 | 0 | 1008 | 36.96 | 2898.96 | 2772 | 126.96 | 2940 |  | #DIV/0! | Module cleaning has been done in Row-F,G,H,I, & Inverter no-4 & Total module cleaning-772 & Grid Failure from-16:14 to 16:18 |  | 772
2018-01-05 | 328 | 385 | 0 | 388 | 11.4 | 1112.4 | 1024.5 | 87.9 | 1151 |  | #DIV/0! | Grid Failure From-9:35 to 14:10
2018-01-06 | 718 | 848 | 1 | 847 | 32.59 | 2446.59 | 2331 | 115.59 | 2500 |  | #DIV/0! | Today inverter no-3 new ABB 250KW inverter commissioning by ABB Mr. Slimbhai Dadu , Inverter started-5:00PM & Grid Failure from-14:05 to 15:35
2018-01-07 | 843 | 1006 | 849 | 993 | 36.67 | 3727.67 | 3563.25 | 164.42 | 3775 |  | #DIV/0! | Sunday no module cleaning & Grid Failure From-10:8 to 10:23 , 10:32 to 10:38
2018-01-08 | 853 | 1006 | 184 | 948 | 36.5 | 3027.5 | 2856.75 | 170.75 | 3062 |  | #DIV/0! | Inverter No-3 Morning time not wakeup due to Error CH2 COM LOSS (7052) Inverter started at 14:40,
2018-01-09 | 786 | 927 | 907 | 902 | 35.11 | 3557.11 | 3393.75 | 163.36 | 3600 |  | #DIV/0! | Module cleaning has been done in Row-K,L, & Row-Q,R,S,T, & Solar traker Inverter no-4,3 & Total module cleaning-642 |  | 642
2018-01-10 | 780 | 917 | 916 | 907 | 35.04 | 3555.04 | 3378 | 177.04 | 3590 |  | #DIV/0! | Module cleaning has been done in Row-M,N,O,P, Inverter no-3 & Total module cleaning-798 & Grid Failure From-15:19 to 15:27 |  | 798
2018-01-11 | 786 | 938 | 943 | 912 | 35.98 | 3614.98 | 3459 | 155.98 | 3670 |  | #DIV/0! | Module cleaning has been done in Row-K,L, Inverter no-2 & Total module cleaning-525 |  | 525
2018-01-12 | 662 | 802 | 795 | 772 | 29.73 | 3060.73 | 2901 | 159.73 | 3100 |  | #DIV/0! | Module cleaning has been done in Row-H,I,J, Inverter no-2&1 & Total module cleaning-798 & Day was cloudy |  | 798
2018-01-13 | 633 | 763 | 749 | 720 | 28.22 | 2893.22 | 2723.25 | 169.97 | 2940 |  | #DIV/0! | Day was cloudy
2018-01-14 | 797 | 865 | 939 | 918 | 35.61 | 3554.61 | 3409.5 | 145.11 | 3610 |  | #DIV/0! | Today morning time Inverter -2 not wakeup due to grid failure night time Reset the Err code Than Inverter started 10:05 & Sunday No Module Cleaning
2018-01-15 | 859 | 1046 | 1024 | 1003 | 37.44 | 3969.44 | 3787.5 | 181.94 |  |  | #DIV/0! | Grid Failure From-16:47 to 16:55 & No Module cleaning
2018-01-16 | 899 | 1091 | 576 | 978 | 39.04 | 3583.04 | 3412.5 | 170.54 |  |  | #DIV/0! | Today visited Abb Engineer Mr.salimbhai Inverter -3 perameter setting & Grid Failure From-11:30 to 11:35 & Module cleaning has been done in Row-D,E,F,G, Inverter No-1 & Total module cleaning-672 |  | 672
2018-01-17 | 950 | 1130 | 1099 | 1073 | 39.76 | 4291.76 | 4098.75 | 193.01 |  |  | #DIV/0! | Module cleaning has been done in Row-A,B,C,&A,B,C,D,E, Inverter No-1&4 & Total module cleaning-804 |  | 804
2018-01-18 | 1001 | 1205 | 1173 | 1240 | 42.17 | 4661.17 | 4470.75 | 190.42 |  |  | #DIV/0! | Module cleaning has been done in Row-,F,G,H,I, Inverter No-4 & Total module cleaning-792 |  | 792
2018-01-19 | 951 | 1153 | 1116 | 1149 | 40.76 | 4409.76 | 4218.75 | 191.01 |  |  | #DIV/0! | Module cleaning has been done in Row-,J,K,L,& Trackers Inverter No-4 & Total module cleaning-528 |  | 528
2018-01-20 | 915 | 1091 | 1072 | 1104 | 39.88 | 4221.88 | 4038.75 | 183.13 |  |  | #DIV/0! | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630
2018-01-21 | 877 | 1040 | 1008 | 1043 | 38.23 | 4006.23 | 3861.75 | 144.48 |  |  | #DIV/0! | Sunday No Module cleaning
2018-01-22 | 831 | 989 | 967 | 968 | 36.32 | 3791.32 | 3645.75 | 145.57 |  |  | #DIV/0! | Module cleaning has been done in Row-,L,M,N, & Inverter No-2&3 & Total module cleaning-714 |  | 714
2018-01-23 | 938 | 1148 | 1114 | 1154 | 41.04 | 4395.04 | 4237.5 | 157.54 |  |  | #DIV/0! | Module cleaning has been done in Row-,I,J,K, & Inverter No-2 & Total module cleaning-840 |  | 840
2018-01-24 | 950 | 1171 | 1109 | 1124 | 41.3 | 4395.3 | 4241.25 | 154.05 |  |  | #DIV/0! | Module cleaning has been done in Row-,F,G,H, & Inverter No-1 & Total module cleaning-630 |  | 630
2018-01-25 | 950 | 1154 | 1084 | 1094 | 40.57 | 4322.57 | 4161.75 | 160.82 |  |  | #DIV/0! | Module cleaning has been done in Row-,A,B,C,D,&A,B,C, & Inverter No-1&4 & Total module cleaning-642 & Grid Failure From-16:22 to 16:26 |  | 642
2018-01-26 | 978 | 1175 | 1104 | 1119 | 41.41 | 4417.41 | 4264.5 | 152.91 |  |  | #DIV/0! | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702
2018-01-27 | 927 | 1113 | 1053 | 1079 | 39.22 | 4211.22 | 4062.75 | 148.47 |  |  | #DIV/0! | Module cleaning has been done in Row-,H,I,J, & Inverter No-4 & Total module cleaning-576 & Grid Failure From-16:44 to 16:55 |  | 576
2018-01-28 | 927 | 1114 | 1048 | 1069 | 39.28 | 4197.28 | 4045.5 | 151.78 |  |  | #DIV/0! | Sunday No Module cleaning
2018-01-29 | 933 | 1114 | 1054 | 1104 | 39.27 | 4244.27 | 4092.75 | 151.52 |  |  | #DIV/0! | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630
2018-01-30 | 938 | 1125 | 1073 | 1129 | 40.15 | 4305.15 | 4154.25 | 150.9 |  |  | #DIV/0! | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 |  | 714
2018-01-31 | 882 | 1063 | 1039 | 1068 | 38.92 | 4090.92 | 3947.25 | 143.67 |  |  | #DIV/0! | Module cleaning has been done in Row-,I,J,K, & Inverter No-4 & Total module cleaning-840 & Grid Failure From-14:13 to 14:17 & 14:46 to 14:50 & 15:10 to 15:20 |  | 840
2018-02-01 | 877 | 1074 | 1028 | 1034 | 37.71 | 4050.71 | 3898.5 | 152.21 |  |  | #DIV/0! | Module cleaning has been done in Row-,E,F,G,H,& Inverter No-1 & Total module cleaning-777 |  | 777
2018-02-02 | 910 | 1097 | 1038 | 1048 | 38.1 | 4131.1 | 3988.5 | 142.6 |  |  | #DIV/0! | Module cleaning has been done in Row-,A,B,C,D,& A,B,C, & Inverter No-1&4 & Total module cleaning-624 |  | 624
2018-02-03 | 961 | 1153 | 1099 | 1119 | 40.11 | 4372.11 | 4218 | 154.11 |  |  | #DIV/0! | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702
2018-02-04 | 955 | 1153 | 1089 | 1154 | 40.26 | 4391.26 | 4281.75 | 109.51 |  |  | #DIV/0! | Today I Replaced The D.C.12Amp Fuse Link of The String-08++tive in AJB-105 of The Inverter-4 During The Period of 10:00 To 10:10
2018-02-05 | 566 | 645 | 620 | 650 | 23.03 | 2504.03 | 2350.5 | 153.53 |  |  | #DIV/0! | Module cleaning has been done in Row-,H,I,J,K,L,& Trackers & Inverter No-4 & Total module cleaning-924 & cloudy Day |  | 924
2018-02-06 | 326 | 373 | 352 | 368 | 11.94 | 1430.94 | 1320 | 110.94 |  |  | #DIV/0! | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 & Fully cloudy Day |  | 630
2018-02-07 | 870 | 1040 | 1003 | 1064 | 37.16 | 4014.16 | 3873.75 | 140.41 |  |  | #DIV/0! | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 |  | 714
2018-02-08 | 984 | 1188 | 1160 | 1219 | 42.02 | 4593.02 | 4434 | 159.02 |  |  | #DIV/0! | Module cleaning has been done in Row-,I,J,K, & Inverter No-2&3 & Total module cleaning-840, |  | 840
2018-02-09 | 984 | 1192 | 1179 | 1220 | 42.17 | 4617.17 | 4467 | 150.17 |  |  | #DIV/0! | Module cleaning has been done in Row-,E,F,G,H,& Inverter No-1 & Total module cleaning-777 |  | 777
2018-02-10 | 774 | 950 | 922 | 892 | 34.59 | 3572.59 | 3452.25 | 120.34 |  |  | #DIV/0! | Module cleaning has been done in Row-,A,B,C,D,& A,B,C, & Inverter No-1&4 & Total module cleaning-624 & Grid Failure From-14:05 to 14:35 |  | 624
2018-02-11 | 831 | 1029 | 973 | 1003 | 36.34 | 3872.34 | 3738.75 | 133.59 |  |  | #DIV/0! | Sunday No Module cleaning & Today started SCADA Work.
2018-02-12 | 944 | 1142 | 1094 | 1119 | 38.91 | 4337.91 | 4183.5 | 154.41 |  |  | #DIV/0! | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702
2018-02-13 | 990 | 1187 | 1129 | 1165 | 40.63 | 4511.63 | 4365.75 | 145.88 |  |  | #DIV/0! | Grid Failure From-9:32 to 09:41
2018-02-14 | 582 | 679 | 650 | 650 | 24.97 | 2585.97 | 2470.5 | 115.47 |  |  | #DIV/0! | Grid Failure From-8:30 to 09:20 & 13:10 TO 15:15
2018-02-15 | 1063 | 1288 | 1220 | 1295 | 44 | 4910 | 4745.25 | 164.75 |  |  | #DIV/0! | Module cleaning has been done in Row-,H,I,J, & Inverter No-4 & Total module cleaning-576 |  | 576
2018-02-16 | 983 | 1187 | 1129 | 1220 | 40.35 | 4559.35 |  | 4559.35 |  |  | #DIV/0! | Grid Failure From-17:20 to 18:20
2018-02-17 | 978 | 1182 | 1124 | 1230 | 40.39 | 4554.39 | 4385.25 | 169.14 |  |  | #DIV/0! | Module cleaning has been done in Row-,K,L, & Trackers & Inverter No-4 & Total module cleaning-528 |  | 528
2018-02-18 | 935 | 1080 | 1056 | 1090 | 37.26 | 4198.26 | 4026 | 172.26 |  |  | #DIV/0! | Grid Failure From-17:10 to 17:25
2018-02-19 | 945 | 1090 | 1055 | 1100 | 40.88 | 4230.88 | 4068 | 162.88 |  |  | #DIV/0!
2018-02-20 | 933 | 1114 | 1074 | 1164 | 40.24 | 4325.24 | 4173 | 152.24 |  |  | #DIV/0! | Grid Failure From-10:05 to 10:10
2018-02-21 | 939 | 1125 | 1144 | 1185 | 40.03 | 4433.03 | 4275 | 158.03 |  |  | #DIV/0!
2018-02-22 | 938 | 1136 | 1104 | 1179 | 39.82 | 4396.82 | 4242.75 | 154.07 | 4424 | 4.926 | 87.53% | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630
2018-02-23 | 893 | 1120 | 1079 | 1109 | 38.55 | 4239.55 | 4092.75 | 146.8 | 4280 | 4.977 | 83.82% | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 & Grid Failure From-09:12 to 09:20 |  | 714
2018-02-24 | 956 | 1215 | 1159 | 1199 | 40.65 | 4569.65 | 4412.25 | 157.4 | 4580 | 5.019 | 88.94% | Today Inverter no-4 AJB-100, string no-9 Down, Due to cable Falt Replaced 30 meter cable string started 18:00.
2018-02-25 | 989 | 1261 | 1194 | 1291 | 41.9 | 4776.9 | 4611.75 | 165.15 | 4780 | 5.926 | 78.62%
2018-02-26 | 950 | 1210 | 1149 | 1224 | 40.97 | 4573.97 | 4422 | 151.97 | 4580 | 5.331 | 83.74% | Module cleaning has been done in Row-,I,J,K, & Inverter No-2&3 & Total module cleaning-840, |  | 840
2018-02-27 | 888 | 1113 | 1054 | 1094 | 37.8 | 4186.8 | 4041 | 145.8 | 4190 | 5.08 | 80.39% | Module cleaning has been done in Row-,E,F,G,H,& Inverter No-1 & Total module cleaning-777 |  | 777
2018-02-28 | 786 | 961 | 912 | 938 | 34.06 | 3631.06 | 3489 | 142.06 | 3640 | 4.679 | 75.82% | Today I Replaced The D.C.12Amp Fuse Link of The String-08++tive in AJB-101 of The Inverter-1 during The Period of 17:00 To 17:05 & Module cleaning has been done in Row-,A,B,C,D,& A,B,C, Inverter No-1&4 & Total module cleaning-624 |  | 624
2018-03-01 | 859 | 1012 | 958 | 972 | 34.7 | 3835.7 | 3698.25 | 137.45 | 3840 | 4.882 | 76.66% | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702
2018-03-02 | 972 | 1159 | 1094 | 1140 | 38.87 | 4403.87 | 4254.75 | 149.12 | 4410 | 5.646 | 76.13%
2018-03-03 | 1006 | 1193 | 1134 | 1189 | 40.05 | 4562.05 | 4395 | 167.05 | 4570 | 5.313 | 83.84% | Module cleaning has been done in Row-,H,I,J, & Inverter No-4 & Total module cleaning-576 |  | 576
2018-03-04 | 961 | 1148 | 1088 | 1205 | 38.65 | 4440.65 | 4290.75 | 149.9 | 4450 | 5.551 | 78.13% | Sunday No Module cleaning
2018-03-05 | 1007 | 1210 | 1144 | 1310 | 40.43 | 4711.43 | 4551.75 | 159.68 | 4720 | 5.79 | 79.45%
2018-03-06 | 1012 | 1136 | 1175 | 1331 | 41.96 | 4695.96 | 4524 | 171.96 | 4705 | 6.232 | 73.58% | Module cleaning has been done in Row-K,L,& Trackers, & ,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-978 & Grid Failure From-12:00 to 12:05 & 13:00 to 13:08 |  | 978
2018-03-07 | 921 | 647 | 1083 | 1144 | 39.06 | 3834.06 | 3703.5 | 130.56 | 3840 | 5.357 | 69.87% | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 &Today Inverter no-2 ABB Auto Trip Due to Err code Auto Reset (056) 13:30 to 18:00 |  | 714
2018-03-08 | 899 | 1117 | 1074 | 1124 | 38.1 | 4252.1 | 4118.25 | 133.85 | 4250 | 5.301 | 78.14% | Today I Replaced The D.C.12Amp Fuse Link of The String-03++tive in AJB-103 of The Inverter-4 during The Period of 12:40 To 12:45 & Module cleaning has been done in Row-,H,I,J, & Inverter No-1&2 & Total module cleaning-798 |  | 798
2018-03-09 | 933 | 1165 | 1119 | 1184 | 39.38 | 4440.38 | 4286.25 | 154.13 | 4450 | 5.516 | 78.63% | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-1 & Total module cleaning-672 & Grid Failure From-15:28 to 15:32 |  | 672
2018-03-10 | 995 | 1226 | 1164 | 1260 | 41.39 | 4686.39 | 4533 | 153.39 | 4695 | 6.127 | 74.69% | Module cleaning has been done in Row-,A,B,C,& A,B,C, Inverter No-1&4 & Total module cleaning-498 & Grid Failure From-10:18 to 10:32 |  | 498
2018-03-11 | 1018 | 1267 | 1200 | 1316 | 41.73 | 4842.73 | 4683 | 159.73 | 4850 | 6.018 | 78.55% | Today I Replaced The D.C.12Amp Fuse Link of The String-03++tive in AJB-103 of The Inverter-4 during The Period of 18:10 To 18:15 & Grid Failure From-08:10 to 08:16 & 08:38 to 08:52 & Sunday No Module Cleaning
2018-03-12 | 514 | 605 | 1245 | 1351 | 43.1 | 3758.1 | 3633 | 125.1 |  |  | #DIV/0! | Today start Tranformer 1&2 overalling work 12:30 & Transformer-3,4& MainTransformer start-18:00 & Total Module Cleaning - 682 |  | 682
2018-03-13 | 0 | 0 | 0 | 0 | 39 | 39 | 0 | 39 | 0 |  | #DIV/0! | Module Cleaning Done - 198 |  | 198
2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #DIV/0! | As per P.O. Of pdpu solar plant All 5 Nos Transformer overalling work done from-12-3-18 12:30 to 14-3-18, 18:00,
2018-03-15 | 1040 | 1272 | 1209 | 1386 | 41 | 4948 | 4759.5 | 188.5 | 4960 | 6.243 | 77.44%
2018-03-16 | 1018 | 1221 | 1185 | 1371 | 41.29 | 4836.29 | 4678.5 | 157.79 | 4845 | 6.186 | 76.34% | Today morning time inverter no - 2 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:15 am & Total Module has been done in Row I,J,K,L, Inverter no-4 & Trackers, Total Module Cleaning-726 |  | 726
2018-03-17 | 989 | 1198 | 1154 | 1330 | 41.92 | 4712.92 | 4558.5 | 154.42 | 4769 | 6.078 | 76.47% | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630
2018-03-18 | 860 | 1007 | 1013 | 1114 | 37.62 | 4031.62 | 3898.5 | 133.12 | 4089 | 4.775 | 83.46% | Today morning time inverter no - 2 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:21
2018-03-19 | 712 | 842 | 862 | 907 | 30.38 | 3353.38 | 3214.5 | 138.88 | 3380 | 3.885 | 84.8% | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 & Grid Failure From-09:15 to 09:21 & Day was cloudy |  | 714
2018-03-20 | 1034 | 1283 | 1290 | 1407 | 43.91 | 5057.91 | 4893.75 | 164.16 | 5070 | 6.13 | 80.61% | Module cleaning has been done in Row-,I,J,K, & Inverter No-2 & Total module cleaning-840, |  | 840
2018-03-21 | 1001 | 1300 | 1255 | 1371 | 44.85 | 4971.85 | 4815.75 | 156.1 | 5090 | 5.551 | 89.37% | Module cleaning has been done in Row-,G,H, & Inverter No-1&2 & Total module cleaning-441 & Replaced New Door Handle of Inverter No - 1 ABB |  | 441
2018-03-22 | 1046 | 1295 | 1245 | 1350 | 42.71 | 4978.71 | 4803.75 | 174.96 | 5025 | 5.75 | 85.18% | Module cleaning has been done in Row-A,B,C,D,E,F & Inverter No-1 & Total module cleaning-672 |  | 672
2018-03-23 | 1057 | 1295 | 1245 | 1341 | 42.58 | 4980.58 | 4825.5 | 155.08 | 5040 | 6.205 | 79.17% | Today I Replaced The D.C.12Amp Fuse Link of The String-08--tive in AJB-101 of The Inverter-1 during The Period of 18:05 To 18:10 & Module cleaning has been done in Row-A,B,C,D,E,F & Inverter No-4 & Total module cleaning-792 & Today replaced New SPD & Blower Fan & Ac side Auxiliary Fan Inverter No-1 ABB |  | 792
2018-03-24 | 1018 | 1209 | 1170 | 1346 | 40.83 | 4783.83 | 4629.75 | 154.08 | 4840 | 6.01 | 78.49% | Grid Failure From-15:22 to 15:38 & Module cleaning has been done in Row-G,H,I,J & Inverter No-4 & Total module cleaning-808 |  | 808
2018-03-25 | 1040 | 1250 | 1209 | 1396 | 41.51 | 4936.51 | 4783.5 | 153.01 | 4999 | 6.369 | 76.5% | Today Painting Work of all 5 Nos of Transformers Started & Inverter N0-4 Tripped at 18:00 due to AP Message 1
2018-03-26 | 1035 | 1238 | 1205 | 1401 | 42.72 | 4921.72 | 4779 | 142.72 | 4967 | 6.103 | 79.32% | Module cleaning has been done in Row-,K,L, & Inverter No-4 & Trackers, Total module cleaning-314 |  | 314
2018-03-27 | 1034 | 1244 | 1220 | 1406 | 42.9 | 4946.9 | 4797 | 149.9 | 4997 | 5.372 | 90.66% | Module cleaning has been done in Row-,P,Q,R,S,T, & Inverter No-3, Total module cleaning-465 |  | 465
2018-03-28 | 1012 | 1210 | 1229 | 1356 | 42.15 | 4849.15 | 4691.25 | 157.9 | 4903 | 5.548 | 86.13% | Module cleaning has been done in Row-,L,M,N,O, & Inverter No-2&3, Total module cleaning-903 |  | 903
2018-03-29 | 1001 | 1237 | 1240 | 1336 | 41.77 | 4855.77 | 4701.75 | 154.02 | 4903 | 6.217 | 76.87% | Module cleaning has been done in Row-,I,J,K, & Inverter No-1&2, Total module cleaning-840 |  | 840
2018-03-30 | 1012 | 1272 | 1230 | 1325 | 41.74 | 4880.74 | 4728.75 | 151.99 | 4943 | 6.177 | 77.99% | Inverter No-4 PM & Module cleaning has been done in Row-E,F,G,H, & Inverter No-1, Total module cleaning-777 |  | 777
2018-03-31 | 723 | 1154 | 1084 | 1240 | 38.02 | 4239.02 | 4110 | 129.02 | 4286 | 6.526 | 64.01% | Grid Failure From-9:37 to 9:42 & 11:37 to 12:08, After Grid Failure at 9:37, inverter no - 1 ABB 250 kw not wake up due to Err Grid MOMFLT (8189) & Reset the Err 6 Times, inverter started at 11:30 & Module cleaning has been done in Row-,A,B,C,D,A,B,C, & Inverter No-1&4, Total module cleaning-624 |  | 624
2018-04-01 | 1041 | 1249 | 1209 | 1336 | 41.5 | 4876.5 | 4714.5 | 162 | 4922 | 6.644 | 72.2% | Grid Failure From-10:44 to 10:48
2018-04-02 | 955 | 1125 | 1099 | 1179 | 38.97 | 4396.97 | 4254 | 142.97 | 4444 | 5.919 | 73.18% | Today morning time inverter no - 4 ABB 250 kw Tripped at 9:05 due to Err Auto Reset F (8185) & Reset Manually inverter started at 9:25 & Grid Failure From-9:25 to 9:30 & Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4, Total module cleaning-666 |  | 666
2018-04-03 | 1001 | 1194 | 1159 | 1351 | 39.85 | 4744.85 | 4592 | 152.85 | 4802 | 6.186 | 75.66% | Module cleaning has been done in Row-H,I,J & Inverter No-4, Total module cleaning-576 & Inverter No-1 PM |  | 576
2018-04-04 | 899 | 1074 | 1044 | 1255 | 36.67 | 4308.67 | 4157 | 151.67 | 4343 | 6.2 | 68.27% | Inverter No-1,2,3,4 ABB 250 kw not wake up due to Grid MONFLT (8189) & ISU fault (8185)(Tripping of ACB & VCB),Started by Switching on, LT outgoing ACB & HT Outdoor VCB at 9:23 & Module cleaning has been done in Row-K,L,P,Q,R,S,T & Inverter No-3&4 & Trackers, Total module cleaning-717 |  | 717
2018-04-05 | 791 | 938 | 942 | 1089 | 34.58 | 3794.58 | 3673.5 | 121.08 | 3836 | 5.472 | 68.33% | Night time Grid Failure due to high Frequency VCB trip,(Plant Started) Started at 9:33 & Module cleaning has been done in Row-M,N,O & Inverter No-3, Total module cleaning-723 |  | 723
2018-04-06 | 967 | 1187 | 1185 | 1346 | 39.95 | 4724.95 | 4576 | 148.95 | 4780 | 6.07 | 76.75% | Module cleaning has been done in Row-J,K,L & Inverter No-2, Total module cleaning-900 & Inverter No-2 PM |  | 900
2018-04-07 | 1001 | 1227 | 1189 | 1355 | 40.62 | 4812.62 | 4658 | 154.62 | 4869 | 6.261 | 75.8% | Module cleaning has been done in Row-E,F,G,H,I & Inverter No-1&2, Total module cleaning-900 |  | 900
2018-04-08 | 949 | 1142 | 1104 | 1235 | 38 | 4468 | 4317 | 151 | 4516 | 5.841 | 75.36%
2018-04-09 | 990 | 1170 | 1134 | 1165 | 38.96 | 4497.96 | 4349 | 148.96 | 4545 | 5.969 | 74.21% | Module cleaning has been done in Row-A,B,C,D,A,B,C & Inverter No-1&4, Total module cleaning-700 & Inverter No-4 ABB 250 kw not Wake up Due to Err Auto Reset F (8185),Reset Manually, Inverter Started at 9:19 |  | 700
2018-04-10 | 966 | 1142 | 1104 | 1240 | 35.15 | 4487.15 | 4352 | 135.15 | 4547 | 5.944 | 74.56% | Module cleaning has been done in Row-D,E,F & Inverter No-4, Total module cleaning-544 & Grid Failure From-9:39 to 9:44 |  | 544
2018-04-11 | 905 | 1057 | 1033 | 1224 | 36.5 | 4255.5 | 4109 | 146.5 | 4303 | 5.222 | 80.31% | Module cleaning has been done in Row-G,H,I,J & Inverter No-4, Total module cleaning-814 & LT Panel Conzerv EM6400 Energy meter of Incomer-3 fail |  | 814
2018-04-12 | 967 | 1148 | 1119 | 1331 | 38.98 | 4603.98 | 4435 | 168.98 | 4651 | 6.031 | 75.16% | Grid Failure From 8:23 to 8:36 & From 10:34 to 10:38 & Module cleaning has been done in Row-K,L,Q,R,S,T & Inverter No-3&4 & Total module cleaning-582 |  | 582
2018-04-13 | 916 | 1080 | 1079 | 1220 | 37.34 | 4332.34 | 4217 | 115.34 | 4379 | 5.643 | 75.63% | Module cleaning has been done in Row-M,N,O,P & Inverter No-3, Total module cleaning-800 & Today Replaced The D.C.12 Amp Fuse Link of The String-09--tive in AJB-107 of The Inverter-2 during The Period of 18:00 To 18:05 |  | 800
2018-04-14 | 983 | 1181 | 1189 | 1340 | 39.51 | 4732.51 | 4589 | 143.51 | 4780 | 6.322 | 73.69% | Today morning time inverter no - 2 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:10 & Module cleaning has been done in Row-J,K,L & Inverter No-2, Total module cleaning-819 |  | 819
2018-04-15 | 922 | 1142 | 1099 | 1250 | 37.74 | 4450.74 | 4304 | 146.74 | 4496 | 5.825 | 75.23%
2018-04-16 | 995 | 1255 | 1210 | 1391 | 39.93 | 4890.93 | 4729 | 161.93 | 4938 | 6.436 | 74.78% | Module cleaning has been done in Row-I,A,B,C,D & Inverter No-2&4, Total module cleaning-562 & Grid Failure From-7:54 to 08:00 AM |  | 562
2018-04-17 | 1029 | 1289 | 1240 | 1417 | 40.95 | 5015.95 | 4855 | 160.95 | 5060 | 6.519 | 75.65% | Module cleaning has been done in Row-E,F,G,H & Inverter No-4, Total module cleaning-800 |  | 800
2018-04-18 | 1000 | 1256 | 1199 | 1401 | 40.21 | 4896.21 | 4733 | 163.21 | 4942 | 6.427 | 74.95% | Module cleaning has been done in Row-I,J,K,L, Inverter No-4 & Trackers, Total module cleaning-726 & Grid Failure From-18:10 to 18:15 |  | 726
2018-04-19 | 950 | 1187 | 1149 | 1361 | 38.73 | 4685.73 | 4541 | 144.73 | 4730 | 6.362 | 72.46% | Module cleaning has been done in Row-Q,R,S,T, Inverter No-3, Total module cleaning-294 & Grid Failure From 10:34 to 10:38 & 11:15 to 11:35 & 15:08 to 15:12 & 16:49 to 16:52 |  | 294
2018-04-20 | 1001 | 1249 | 1230 | 1431 | 40.54 | 4951.54 | 4794 | 157.54 | 4996 | 6.312 | 77.15% | Module cleaning has been done in Row-M,N,O,P, Inverter No-3, Total module cleaning-800 |  | 800
2018-04-21 | 1040 | 1323 | 1296 | 1467 | 41.84 | 5167.84 | 5003 | 164.84 | 5214 | 6.565 | 77.41% | Module cleaning has been done in Row-J,K,L, Inverter No-2, Total module cleaning-819 |  | 819
2018-04-22 | 984 | 1261 | 1219 | 1366 | 40.04 | 4870.04 | 4724 | 146.04 | 4915 | 6.579 | 72.81% | Grid Failure From 8:36 to 8:56
2018-04-23 | 932 | 1175 | 1134 | 1255 | 37.49 | 4533.49 | 4382 | 151.49 | 4580 | 6.682 | 66.81% | Module cleaning has been done in Row-F,G,H,I, Inverter No-1&2, Total module cleaning-903 & Grid Failure From 10:30 to 10:34 & from 10:50 to 11:33 |  | 903
2018-04-24 | 1063 | 1295 | 1240 | 1381 | 40.58 | 5019.58 | 4861 | 158.58 | 5065 | 6.794 | 72.66% | Module cleaning has been done in Row-A,B,C,D,E,A,B,C,D, Inverter No-1&4, Total module cleaning-915 & Grid Failure From 16:20 to 16:24 |  | 915
2018-04-25 | 1086 | 1312 | 1250 | 1381 | 40.69 | 5069.69 | 4904 | 165.69 | 5115 | 6.829 | 73% | Module cleaning has been done in Row-E,F,G,H,I, Inverter No-4, Total module cleaning-954 |  | 954
2018-04-26 | 1040 | 1249 | 1200 | 1431 | 39.12 | 4959.12 | 4807 | 152.12 | 5004 | 6.575 | 74.18% | Module cleaning has been done in Row-J,K,L,& Trackers Inverter No-4, Total module cleaning-528 |  | 528
2018-04-27 | 978 | 1182 | 1144 | 1356 | 38 | 4698 | 4544 | 154 | 4744 | 6.28 | 73.63% | Module cleaning has been done in Row-P,Q,R,S,T, Inverter No-3, Total module cleaning-450 |  | 450
2018-04-28 | 1006 | 1209 | 1210 | 1391 | 39.02 | 4855.02 | 4700 | 155.02 | 4900 | 6.338 | 75.35% | Module cleaning has been done in Row-M,N,O, Inverter No-3, Total module cleaning-651 |  | 651
2018-04-29 | 1006 | 1211 | 1214 | 1371 | 39.51 | 4841.51 | 4691 | 150.51 | 4886 | 6.499 | 73.28% | Grid Failure From-10:05 to 10:09
2018-04-30 | 979 | 1130 | 1170 | 1341 | 38.5 | 4658.5 | 4514 | 144.5 | 4703 | 6.116 | 74.95% | Today morning time inverter no - 2 ABB 250 kw not Wake up due to Err Auto Reset F (8185), Reset Manually, inerter started at 8:10 AM & Module cleaning has been done in Row-L,A,B,C,D, & Inverter No-2&4, Total module cleaning-684 |  | 684
2018-05-01 | 995 | 1249 | 1199 | 1376 | 38.59 | 4857.59 | 4701 | 156.59 | 4904 | 6.392 | 74.78% | Module cleaning has been done in Row-I,J,K, Inverter No-2, Total module cleaning-901 |  | 901
2018-05-02 | 1017 | 1261 | 1195 | 1376 | 38.47 | 4887.47 | 4736 | 151.47 | 4930 | 6.285 | 76.45% | Module cleaning has been done in Row-C,D,E,F,G,H, Inverter No-1, Total module cleaning-902 |  | 902
2018-05-03 | 1018 | 1221 | 1159 | 1320 | 37.75 | 4755.75 | 4595 | 160.75 | 4800 | 6.456 | 72.47% | Module cleaning has been done in Row-A,B,A,B,C,D,E, Inverter No-1&4, Total module cleaning-774 & Grid Failure From 16:53 PM to 17:00 PM |  | 774
2018-05-04 | 961 | 1154 | 1094 | 1195 | 35.78 | 4439.78 | 4301 | 138.78 | 4459 | 6.055 | 71.78% | Inverter No - 4 ABB 250 kw not Wake up due to Err DC GND fault (108), Reset Manually, Inverter started at 8:44 AM & The same Inverter tripped due to Err DC GND fault (108) at 16:00, Started Manually at 16:12, Grid Failure from 13:56 to 14:00, Module cleaning has been done in Row-F,G,H, Inverter No-4, Total module cleaning-604 |  | 604
2018-05-05 | 724 | 876 | 836 | 892 | 23.65 | 3351.65 | 3232 | 119.65 | 3371 | 6.285 | 52.28% | Inverter No - 4 ABB 250 kw Tripped due to Error DC GND fault (108) at 9:30 AM, Started Manually at 10:10 AM, Grid Failure from 11:30 to 13:30, Module cleaning done in Row-I,J, Inverter No-4, Total module cleaning-368 |  | 368
2018-05-06 | 989 | 1204 | 1139 | 1366 | 37.25 | 4735.25 | 4585 | 150.25 | 4760 | 6.394 | 72.56%
2018-05-07 | 984 | 1210 | 1155 | 1396 | 39 | 4784 | 4625 | 159 | 4804 | 6.333 | 73.93% | Module cleaning has been done in Row-Q,R,S,T,K,L, Inverter No-3&4 & Trackers, Total module cleaning-642 & Grid Failure from 14:45 to 14:49, from 16:59 to 17:05 & from 17:59 to 18:06 |  | 642
2018-05-08 | 944 | 1159 | 1149 | 1341 | 38.3 | 4631.3 | 4488 | 143.3 | 4655 | 6.149 | 73.78% | Module cleaning has been done in Row-M,N,O,P, Inverter No-3, Total module cleaning-798 |  | 798
2018-05-09 | 961 | 1210 | 1204 | 1366 | 38.28 | 4779.28 | 4627 | 152.28 | 4800 | 6.262 | 74.71% | Module cleaning has been done in Row-J,K,L, Inverter No-2, Total module cleaning-819 |  | 819
2018-05-10 | 955 | 1238 | 1185 | 1335 | 37.89 | 4750.89 | 4596 | 154.89 | 4773 | 6.259 | 74.33% | Module cleaning has been done in Row-G,H,I, Inverter No-1&2, Total module cleaning-714 |  | 714
2018-05-11 | 905 | 1153 | 1104 | 1250 | 35.74 | 4447.74 | 4312 | 135.74 | 4470 | 6.292 | 69.24% | Grid Failure from 9:40 to 9:44 & from 15:55 to 16:35, No Module Cleaning done due to Absence of Manpower |  | 0
2018-05-12 | 1000 | 1250 | 1194 | 1346 | 38.21 | 4828.21 | 4664 | 164.21 | 4850 | 6.492 | 72.81% | Module cleaning done in Row-A,B,C,D,E,F, Inverter No-1, Total module cleaning-672 & Grid Failure from 14:10 to 14:13 & from 16:16 to 16:18 |  | 672
2018-05-13 | 995 | 1226 | 1175 | 1296 | 37.64 | 4729.64 | 4581 | 148.64 | 4748 | 6.395 | 72.36% | Inverter No-4 ABB 250 KW not wake up due to Err Auto Reset F (8185), Reset Manually, Inverter Started at 8:00, Sunday No Module Cleaning
2018-05-14 | 809 | 978 | 962 | 1083 | 32.41 | 3864.41 | 3740 | 124.41 | 3885 | 5.747 | 65.89% | Today I Replaced The D.C.12 Amp Fuse Link of The String-03, +ve in AJB-101 of The Inverter-1 during The Period of 18:10 To 18:15 & Module cleaning done in Row-A,B,C, Inverter No-4 & Total module cleaning-288 & Grid Failure from 11:05 to 11:25 & from 14:23 to 14:46 & Inverter No-1&2 ABB 250 KW Not Wake up due to Err Auto Reset F (8185), Reset Manually, Inverters started at 7:40 |  | 288
2018-05-15 | 232 | 272 | 262 | 287 | 7.529 | 1060.529 | 1026 | 34.529 | 1081.35 | 5.645 | 18.67% | Grid Failure from 6:50 AM to 2:20 PM,Module Cleaning has been done in Row-D,E,Inverter No-4 & Total Module Cleaning-306 |  | 306
2018-05-16 | 921 | 1091 | 1049 | 1204 | 34.8 | 4299.8 | 4181.25 | 118.55 | 4308.6 | 5.744 | 73.11% | Grid Failure from 2:19 to 2:24 PM,Module Cleaning has been done in Row-F,G Inverter No-4 & Total Module Cleaning-396 |  | 396
2018-05-17 | 899 | 1074 | 1033 | 1159 | 34.36 | 4199.36 | 4090.5 | 108.86 | 4213.8 | 5.773 | 71.14% | Inverter No. 4 has stopped around 30 minutes(9:50 to 10:20) due to ground fault,Grid failure from 1:40 to 1:45, Module Cleaning has been done in Row-H,I,J,K & tracker's 60 PV Modules, Inverter No-4 & total module cleaning-924 |  | 924
2018-05-18 | 842 | 984 | 943 | 1150 | 33.73 | 3952.73 | 3879.75 | 72.98 | 3955.65 | 5.364 | 71.88% | Grid failure from 4:50 to 4:55 PM, Module cleaning has not done because of water tank cleaning. |  | 0
2018-05-19 | 922 | 1092 | 1048 | 1280 | 35.74 | 4377.74 | 4251 | 126.74 | 4391.65 | 5.886 | 72.72% | Grid failure from 5:47 to 5:52, Module cleaning has not done due to absence of manpower |  | 0
2018-05-20 | 868 | 1023 | 978 | 1129 | 33.61 | 4031.61 | 3921 | 110.61 | 4044.22 | 5.546 | 71.07% | Today morning time inverter no - 4 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:12. |  | 0
2018-05-21 | 885 | 1057 | 1028 | 1125 | 34.65 | 4129.65 | 4122.75 | 6.9 | 4147.3 | 5.816 | 69.5% | Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No-3 & total module cleaning-441, No Grid failure,Replace 400 W halogen lamp & fix new LED light(150 W-5 peace). |  | 441
2018-05-22 | 859 | 1017 | 1068 | 1159 | 34.02 | 4137.02 | 4025.55 | 111.47 | 4152.6 | 5.7 | 71.01% | Module Cleaning has been done in Row-N,O Inverter No-3 & total module cleaning-399, No Grid failure. |  | 399
2018-05-23 | 842 | 1046 | 1094 | 1044 | 33.225 | 4059.225 | 3935.25 | 123.975 | 4080 | 5.575 | 71.33% | Today morning time inverter no - 4 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:55, Module Cleaning has been done in Row-J,K,L,M Inverter No-2,3 & total module cleaning-1071, No Grid failure. |  | 1071
2018-05-24 | 882 | 1182 | 1134 | 1179 | 34.203 | 4411.203 | 4296.75 | 114.453 | 4429 | 5.495 | 78.56% | Module Cleaning has been done in Row-J,K,L Inverter No-1,2 & total module cleaning-721,Today morning time inverter no - 4 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:10 |  | 721
2018-05-25 | 990 | 1210 | 1149 | 1250 | 33.946 | 4632.946 | 4476 | 156.946 | 4652 | 5.844 | 77.59% | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1,2 & total module cleaning-483,No Grid failure. |  | 483
2018-05-26 | 1005 | 1188 | 1129 | 1225 | 33.196 | 4580.196 | 4429.5 | 150.696 | 4600 | 5.882 | 76.22% | Module Cleaning has been done in Row-C,D,E Inverter No-4 & total module cleaning-483,No Grid failure. |  | 483
2018-05-27 | 950 | 1147 | 1089 | 1184 | 32.21 | 4402.21 | 4266.75 | 135.46 | 4422 | 5.791 | 74.42% | Sunday No Module Cleaning
2018-05-28 | 939 | 1114 | 1058 | 1185 | 31.45 | 4327.45 | 4216.5 | 110.95 | 4347 | 5.529 | 76.63% | Inverter No. 4 has stopped around 30 minutes(09:42 to 09:53 & 11:06 to 11:17) due to ground fault, Module Cleaning has been done in Row-F,G,H,I Inverter No-4 & total module cleaning-792,No Grid failure. |  | 792
2018-05-29 | 931 | 1097 | 1049 | 1250 | 30.76 | 4357.76 | 4246.5 | 111.26 | 4370 | 5.46 | 78.01% | Module Cleaning has been done in Row-J,K,L & tracker's 60 PV Modules, Inverter No-4 & total module cleaning-528,No Grid failure. |  | 528
2018-05-30 | 866 | 1018 | 1003 | 1189 | 33.048 | 4109.048 | 4001.25 | 107.798 | 4129 | 5.141 | 78.28% | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3 & total module cleaning-630,No Grid failure. |  | 630
2018-05-31 | 857 | 1007 | 1043 | 1175 | 32.964 | 4114.964 | 3981 | 133.964 | 4134 | 5.246 | 76.81% | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2,3 & total module cleaning-987,No Grid failure. |  | 987
2018-06-01 | 805 | 1012 | 978 | 1083 | 30.894 | 3908.894 | 3792 | 116.894 | 3928 | 4.897 | 78.18% | Module Cleaning has been done in Row-G,H,I,J, Inverter No-1,2 & total module cleaning-1008,No Grid failure. |  | 1008
2018-06-02 | 899 | 1091 | 1043 | 1164 | 32.653 | 4229.653 | 4112.25 | 117.403 | 4249 | 5.468 | 75.74% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & total module cleaning-672,No Grid failure. |  | 672
2018-06-03 | 924 | 1097 | 1054 | 1169 | 32.185 | 4276.185 | 4156.5 | 119.685 | 4296 | 5.41 | 77.4% | Sunday No Module Cleaning,No Grid failure.
2018-06-04 | 478 | 572 | 549 | 610 | 20.54 | 2229.54 | 2148.75 | 80.79 | 2250 | 5.617 | 39.04% | Inverter has stopped due to Grid failure from 8.30 AM to 12.40 PM & 5.22 to 6.10 PM Module Cleaning has been done in Row-A,B,C Inverter No-1,2 & total module cleaning-288 |  | 288
2018-06-05 | 945 | 1141 | 1094 | 1230 | 33.329 | 4443.329 | 4301.25 | 142.079 | 4465 | 5.655 | 76.96% | Module Cleaning has been done in Row-D,E,F,G,H Inverter No-4 & total module cleaning-900 ,No Grid failure. |  | 900
2018-06-06 | 407 | 464 | 464 | 539 | 13.57 | 1887.57 | 1808.25 | 79.32 | 1207 | 5.389 | 21.83% | Inverter has stopped due to Grid failure from 8.58 AM to 1.30 PM,Module Cleaning has been done in Row-I,J Inverter No-4 & total module cleaning-378 |  | 378
2018-06-07 | 927 | 1114 | 1089 | 1306 | 34.412 | 4470.412 | 4336.5 | 133.912 | 4490 | 5.583 | 78.38% | Module Cleaning has been done in Row-K,L & tracker's Inverter No-4(Thin Film Area) Row-O,P,Q,R,S,T Inverter No. 3 & total module cleaning-978 ,No Grid failure. |  | 978
2018-06-08 | 865 | 1034 | 1038 | 1204 | 33.065 | 4174.065 | 4055.25 | 118.815 | 4194 | 5.287 | 77.32% | Module Cleaning has been done in Row-L,M,N Inverter No. 2,3 & total module cleaning-714 ,No Grid failure. |  | 714
2018-06-09 | 752 | 916 | 912 | 1024 | 30.25 | 3634.25 | 3510.75 | 123.5 | 3655 | 4.7 | 75.8% | Module Cleaning has been done in Row-J,K Inverter No. ,2 & total module cleaning-820 ,No Grid failure & cloudy day |  | 567
2018-06-10 | 774 | 933 | 933 | 1053 | 30.96 | 3723.96 | 3615 | 108.96 | 3745 | 4.735 | 77.09% | No module cleaning due to holiday & cloudy day
2018-06-11 | 758 | 933 | 912 | 1033 | 28.56 | 3664.56 | 3540.75 | 123.81 | 3675 | 4.547 | 78.77% | Module Cleaning has been done in Row-H,I, Inverter No. 1,2 & total module cleaning-399,No Grid failure. & cloudy day |  | 504
2018-06-12 | 825 | 1017 | 993 | 1119 | 31.05 | 3985.05 | 3848.25 | 136.8 | 4000 | 4.993 | 78.08% | No Module cleaning (No Man power) & cloudy day
2018-06-13 | 729 | 899 | 882 | 993 | 26.3 | 3529.3 | 3392.25 | 137.05 | 3545 | 5.209 | 66.33% | Grid Failure From-12:44 to 13:50. No Module Cleaning (No Man Power) & cloudy day
2018-06-14 | 696 | 847 | 837 | 943 | 26.3 | 3349.3 | 3252 | 97.3 | 3365 | 4.994 | 65.67% | Grid Failure From-15:18 to 17:25. No Module Cleaning (No Man Power) & cloudy day
2018-06-15 | 786 | 950 | 937 | 1063 | 29.12 | 3765.12 | 3626.25 | 138.87 | 3780 | 4.733 | 77.84% | No Module Cleaning (No Man Power) & cloudy day
2018-06-16 | 893 | 1096 | 1079 | 1260 | 33.1 | 4361.1 | 4221.75 | 139.35 | 4370 | 5.549 | 76.76% | No Module Cleaning (No Man Power) & Grid Failure From-18:24 to 18:28 & Today replaced New MFM Meter for LT panel Incomer Feeder No.3 (conzerve 6400NG) & cloudy day
2018-06-17 | 774 | 928 | 917 | 1074 | 29.65 | 3722.65 | 3612 | 110.65 | 3740 | 4.895 | 74.47% | Grid Failure From-10:50 to 10:56. No Module Cleaning (No Man Power) & cloudy day
2018-06-18 | 826 | 994 | 983 | 1124 | 31.18 | 3958.18 | 3807.75 | 150.43 | 3970 | 5.202 | 74.38% | No Module Cleaning (No Man Power) & cloudy day
2018-06-19 | 825 | 1004 | 968 | 1114 | 31.71 | 3942.71 | 3792.75 | 149.96 | 3955 | 5.166 | 74.62% | No Module Cleaning (No Man Power) & cloudy day
2018-06-20 | 905 | 1080 | 1053 | 1209 | 33.49 | 4280.49 | 4137.75 | 142.74 | 4290 | 5.826 | 71.77% | No Module Cleaning (No Man Power) & cloudy day
2018-06-21 | 899 | 1074 | 1053 | 1210 | 33.1 | 4269.1 | 4129.5 | 139.6 | 4280 | 5.793 | 72.01% | No Module Cleaning (No Man Power) & cloudy day
2018-06-22 | 859 | 1001 | 978 | 1144 | 31.75 | 4013.75 | 3901.5 | 112.25 | 4015 | 5.472 | 71.51% | No Module Cleaning (No Man Power) & cloudy day
2018-06-23 | 701 | 803 | 786 | 887 | 22.71 | 3199.71 | 3111 | 88.71 | 3110 | 4.326 | 70.07% | Module Cleaning has been done in Row-,A,B,C,D,E,F, Inverter No-4 & total module cleaning-792, & Cloudy Day,No Grid failure. |  | 792
2018-06-24 | 515 | 588 | 580 | 600 | 16.67 | 2299.67 | 2160 | 139.67 | 2310 | 2.894 | 77.8% | Today Morning Time Inverter No-4 Thinfilm Note wake up, Due to Ground Fault by Modules crack, Reset the Err Then Inverter started- 11:05. Rainy & cloudy day
2018-06-25 | 616 | 718 | 711 | 816 | 24.02 | 2885.02 | 2794.5 | 90.52 | 2900 | 3.985 | 70.93% | Module clean By Rain & Grid Failure From-11:07 to 11:17, 14:47 to 14:46, 15:17 to 16:52, 17:24 to 17:31,& Module clean by Rain, Rainy & cloudy day
2018-06-26 | 656 | 752 | 746 | 792 | 24.47 | 2970.47 | 2818.5 | 151.97 | 2980 | 3.798 | 76.47% | Today Morning Time Inverter No-4 Thinfilm Note wake up, Due to Ground Fault by Modules crack, Reset the Err (GND CLOSE ER 8196)Then Inverter started- 09:40. Module clean by Rain & Rainy & cloudy day
2018-06-27 | 730 | 826 | 821 | 922 | 26.25 | 3325.25 | 3173.25 | 152 | 3336 | 4.184 | 77.71% | Module clean by Rain & Rainy & cloudy day
2018-06-28 | 774 | 894 | 887 | 1023 | 28.48 | 3606.48 | 3497.25 | 109.23 | 3595 | 4.539 | 77.2% | Module clean by Rain & Rainy & cloudy day
2018-06-29 | 588 | 678 | 681 | 766 | 23.01 | 2736.01 | 2625 | 111.01 | 2745 | 3.65 | 73.3% | Grid Failure From-11:55 to 12:07 & Module clean by Rain & Rainy & cloudy day
2018-06-30 | 712 | 820 | 846 | 983 | 28.56 | 3389.56 | 3243 | 146.56 | 3400 | 4.406 | 75.21% | Today replaced The New MC4 Connector String No-6,AJB-106,Inverter-No-2, During The Period of 17:30 & Module clean by Rain & Rainy & cloudy day
2018-07-01 | 848 | 989 | 978 | 1154 | 33.55 | 4002.55 | 3843 | 159.55 | 4010 | 5.242 | 74.56% | Module clean by Rain & Rainy & cloudy day
2018-07-02 | 622 | 775 | 776 | 903 | 24.76 | 3100.76 | 3023.25 | 77.51 | 3110 | 4.02 | 75.4% | Today Morning time inverter No-1 ABB 250KW not wake up Due to Auto reset 'F' Reset The Err Then Inverter started-08:48. & Module clean by Rain & Rainy & cloudy day
2018-07-03 | 407 | 452 | 454 | 509 | 13.15 | 1835.15 | 1761.75 | 73.4 | 1840 | 2.18 | 82.26% | Today Monkey Broke a one Module Thin film site AJB-101, Inverter No-4, & Module clean by Rain. Cloudy & Rainy Day
2018-07-04 | 243 | 271 | 277 | 247 | 7.8 | 1045.8 | 951 | 94.8 | 1050 | 1.465 | 69.86% | Fully cloudy & Heavy Rainy Day
2018-07-05 | 865 | 996 | 983 | 1139 | 32.92 | 4015.92 | 3810 | 205.92 | 4015 | 5.104 | 76.67% | Fully cloudy & Rainy Day
2018-07-06 | 774 | 892 | 887 | 1018 | 29.71 | 3600.71 | 3521.25 | 79.46 | 3610 | 4.671 | 75.33% | Grid Failure From-10:20 to 10:28 & Module clean by Rain & cloudy day
2018-07-07 | 860 | 1001 | 998 | 1159 | 32.52 | 4050.52 | 3902.25 | 148.27 | 4060 | 5.267 | 75.13% | Module clean by Rain & cloudy day
2018-07-08 | 689 | 775 | 786 | 897 | 27.82 | 3174.82 | 3080.25 | 94.57 | 3180 | 4.111 | 75.39% | Module clean by Rain & cloudy day
2018-07-09 | 713 | 803 | 817 | 923 | 27.69 | 3283.69 | 3168.75 | 114.94 | 3290 | 4.292 | 74.71% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 & total module cleaning-792, & Fully cloudy day |  | 792
2018-07-10 | 571 | 627 | 640 | 705 | 20.69 | 2563.69 | 2460.75 | 102.94 | 2575 | 3.195 | 78.55% | Module clean by Rain & cloudy day
2018-07-11 | 441 | 486 | 494 | 550 | 15.72 | 1986.72 | 1913.25 | 73.47 | 1995 | 2.357 | 82.5% | Module clean by Rain & Fully Rainy & cloudy day
2018-07-12 | 367 | 396 | 408 | 453 | 12.44 | 1636.44 | 1547.25 | 89.19 | 1644 | 1.96 | 81.75% | Module clean by Rain & Rainy & cloudy day
2018-07-13 | 633 | 712 | 721 | 827 | 24.24 | 2917.24 | 2784 | 133.24 | 2925 | 3.779 | 75.44% | Grid Faiure From-08:50 to 09:27 & Module clean by Rain & Rainy & cloudy day
2018-07-14 | 317 | 345 | 363 | 383 | 11.31 | 1419.31 | 1329.75 | 89.56 | 1425 | 2.244 | 61.89% | Grid Faiure From-11:15 to 13:07 & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for Inport-xport meter, (Replaced total cable 80 meter)
2018-07-15 | 328 | 357 | 363 | 358 | 10.72 | 1416.72 | 1314 | 102.72 | 1425 | 1.802 | 77.07% | Grid Faiure From-14:52 to 15:05 & 15:48 to 15:57, 16:52 to 17:25 & Module clean by Rain & Rainy & Fully cloudy day
2018-07-16 | 486 | 537 | 554 | 625 | 18.31 | 2220.31 | 2127 | 93.31 | 2230 | 2.554 | 85.1% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 101 to SMB No-1, (Replaced total cable 70 meter)
2018-07-17 | 430 | 475 | 484 | 544 | 15.57 | 1948.57 | 1818.75 | 129.82 | 1960 | 2.406 | 79.4% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 100 to AJB-101, (Replaced total cable 25 meter)
2018-07-18 | 384 | 423 | 433 | 474 | 13.17 | 1727.17 | 1655.25 | 71.92 | 1740 | 2.114 | 80.22% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 101 to AJB-102, (Replaced total cable 25 meter)
2018-07-19 | 294 | 317 | 328 | 358 | 10.21 | 1307.21 | 1247.25 | 59.96 | 1315 | 1.762 | 72.74% | Grid Failure From-15:43 to 17:17, & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 102 to AJB-103, (Replaced total cable 25 meter)
2018-07-20 | 277 | 317 | 323 | 358 | 9.69 | 1284.69 | 1175.25 | 109.44 | 1295 | 1.544 | 81.75% | Grid Failure From-15:43 to 17:17, & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 103 to AJB-104, (Replaced total cable 25 meter) & Today I Replaced The D.C.12Amp Fuse Link of The String-07++tive in AJB-109 of The Inverter-2 during The Period of 17:30 To 17:40
2018-07-21 | 334 | 373 | 378 | 403 | 11.77 | 1499.77 | 1398 | 101.77 | 1510 | 1.817 | 81% | Grid Failure From-15:43 to 17:17, & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 104 to AJB-105, (Replaced total cable 25 meter)
2018-07-22 | 520 | 604 | 604 | 675 | 19.52 | 2422.52 | 2302.5 | 120.02 | 2430 | 2.965 | 79.88% | Module clean by Rain & Rainy & Fully cloudy day
2018-07-23 | 333 | 384 | 383 | 418 | 11.67 | 1529.67 | 1433.25 | 96.42 | 1540 | 1.837 | 81.71% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 105 to AJB-106, (Replaced total cable 25 meter)
2018-07-24 | 210 | 243 | 247 | 162 | 7.16 | 869.16 | 788.25 | 80.91 | 880 | 1.296 | 66.18% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 106 to AJB-107, (Replaced total cable 25 meter) & Grid Failure From-09:05 to 09:25, 10:27 to 10:36, 14:47 to 15:02, 15:56 to 16:31
2018-07-25 | 350 | 396 | 404 | 368 | 12.19 | 1530.19 | 1373.25 | 156.94 | 1540 | 1.935 | 77.57% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 107 to AJB-108, (Replaced total cable 25 meter)
2018-07-26 | 469 | 543 | 544 | 584 | 18.12 | 2158.12 | 2117.25 | 40.87 | 2160 | 2.665 | 79% | Module clean by Rain & Rainy & Fully cloudy day
2018-07-27 | 396 | 452 | 454 | 479 | 14.22 | 1795.22 | 1683.75 | 111.47 | 1800 | 2.239 | 78.36% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 108 to AJB-109, (Replaced total cable 50 meter)
2018-07-28 | 650 | 763 | 761 | 852 | 25.97 | 3051.97 | 2922 | 129.97 | 3060 | 3.976 | 75.01% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 109 to AJB-110, (Replaced total cable 25 meter)
2018-07-29 | 413 | 487 | 484 | 494 | 15.84 | 1893.84 | 1814.25 | 79.59 | 1905 | 2.491 | 74.54% | Module clean by Rain & Rainy & cloudy day
2018-07-30 | 656 | 768 | 725 | 857 | 25.18 | 3031.18 | 2904 | 127.18 | 3040 | 3.948 | 75.05% | Module clean by Rain & Rainy & cloudy day
2018-07-31 | 695 | 820 | 817 | 922 | 28.52 | 3282.52 | 3161.25 | 121.27 | 3170 | 4.252 | 72.66% | Grid Failure From-11:41 to 11:48 & Module clean by Rain & cloudy day
2018-08-01 | 656 | 774 | 766 | 857 | 25.86 | 3078.86 | 2979.75 | 99.11 | 2990 | 4.036 | 72.21% | Grid Failure From-15:04 to 15:10 & Module clean by Rain & cloudy day & Today Replaced 2 MC4 Connecter for string No-2 positive & Negative line, AJB No-102, Inverter-1
2018-08-02 | 627 | 719 | 721 | 791 | 24.27 | 2882.27 | 2787 | 95.27 | 2890 | 3.677 | 76.6% | Grid Failure From-15:04 to 15:10 & Module clean by Rain & cloudy day & Grid Failure From-08:30 to 08:43
2018-08-03 | 696 | 813 | 801 | 908 | 28.78 | 3246.78 | 3153.75 | 93.03 | 3250 | 4.232 | 74.85% | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 110 to AJB-111, (Replaced total cable 40 meter)
2018-08-04 | 684 | 787 | 781 | 856 | 26.65 | 3134.65 | 3003.75 | 130.9 | 3140 | 4.107 | 74.52% | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 111 to AJB-112, (Replaced total cable 40 meter)
2018-08-05 | 605 | 695 | 691 | 772 | 23.84 | 2786.84 | 2675.25 | 111.59 | 2790 | 3.612 | 75.29% | Module clean by Rain & Fully cloudy day
2018-08-06 | 497 | 577 | 569 | 640 | 19.64 | 2302.64 | 2220 | 82.64 | 2310 | 2.968 | 75.86% | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 112 to AJB-113, (Replaced total cable 40 meter)
2018-08-07 | 537 | 610 | 610 | 675 | 20.08 | 2452.08 | 2339.25 | 112.83 | 2460 | 3.144 | 76.26% | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 113 to AJB-114, (Replaced total cable 40 meter)
2018-08-08 | 300 | 339 | 338 | 272 | 10.06 | 1259.06 | 1187.25 | 71.81 | 1300 | 1.695 | 74.75% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 114 to AJB-115, (Replaced total cable 40 meter)
2018-08-09 | 610 | 702 | 701 | 791 | 23.32 | 2827.32 | 2700 | 127.32 | 2835 | 3.52 | 78.5% | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 115 to AJB-116, (Replaced total cable 40 meter) & Grid Failure From-11:36 to 11:42, 12:00 to 12:05
2018-08-10 | 933 | 1102 | 1098 | 1266 | 37.24 | 4436.24 | 4258.5 | 177.74 | 4440 | 5.728 | 75.55% | Module clean by Rain & Rainy & cloudy day & Today Replaced New cat 6 communication cable for AJB 116 to AJB-117, (Replaced total cable 40 meter) & Grid Failure From-14:55 to 15:05,
2018-08-11 | 724 | 848 | 837 | 957 | 27.23 | 3393.23 | 3275.25 | 117.98 | 3400 | 4.168 | 79.51% | Module clean by Rain & Rainy & cloudy day,
2018-08-12 | 543 | 627 | 630 | 706 | 22.48 | 2528.48 | 2440.5 | 87.98 | 2530 | 3.239 | 76.13% | Module clean by Rain & Rainy & cloudy day,
2018-08-13 | 576 | 662 | 660 | 721 | 22.27 | 2641.27 | 2517 | 124.27 | 2650 | 3.239 | 79.74% | Module clean by Rain & Rainy & cloudy day,
2018-08-14 | 532 | 610 | 605 | 650 | 20.79 | 2417.79 | 2304 | 113.79 | 2420 | 3.034 | 77.74% | Module clean by Rain & Rainy & cloudy day,
2018-08-15 | 554 | 634 | 635 | 680 | 20.72 | 2523.72 | 2418.75 | 104.97 | 2530 | 3.244 | 76.01% | Module clean by Rain & cloudy day & Grid Failure From-14:02 to 14:10,
2018-08-16 | 706 | 825 | 817 | 928 | 28.75 | 3304.75 | 3180.75 | 124 | 3310 | 4.219 | 76.47% | Module clean by Rain & Rainy & cloudy day,
2018-08-17 | 68 | 79 | 85 | 80 | 2 | 314 | 241.5 | 72.5 | 320 | 0.451 | 69.16% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-09:44 to 09:55,
2018-08-18 | 475 | 548 | 545 | 620 | 17.28 | 2205.28 | 2078.25 | 127.03 | 2210 | 2.741 | 78.58% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-13:51 to 13:56,
2018-08-19 | 300 | 334 | 343 | 363 | 9.74 | 1349.74 | 1231.5 | 118.24 | 1350 | 1.651 | 79.7% | Module clean by Rain & Fully Rain & cloudy day
2018-08-20 | 610 | 723 | 715 | 822 | 24.62 | 2894.62 | 2797.5 | 97.12 | 2900 | 3.694 | 76.52% | Module clean by Rain & Fully Rain & cloudy day
2018-08-21 | 306 | 345 | 348 | 257 | 10.63 | 1266.63 | 1191.75 | 74.88 | 1270 | 1.621 | 76.36% | Module clean by Rain & Fully Rain & cloudy day
2018-08-22 | 378 | 430 | 433 | 474 | 13.65 | 1728.65 | 1599.75 | 128.9 | 1730 | 2.108 | 79.99% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-09:45 to 09:50 & 14:50 to 14:55
2018-08-23 | 696 | 814 | 812 | 942 | 28.93 | 3292.93 | 3170.25 | 122.68 | 3300 | 4.234 | 75.97% | Module clean by Rain & Fully Rain & cloudy day
2018-08-24 | 593 | 696 | 696 | 791 | 24.72 | 2800.72 | 2676 | 124.72 | 2810 | 3.581 | 76.48% | Module clean by Rain & Fully Rain & cloudy day
2018-08-25 | 515 | 599 | 599 | 661 | 20.22 | 2394.22 | 2306.25 | 87.97 | 2400 | 3.042 | 76.9% | Module clean by Rain & Fully Rain & cloudy day
2018-08-26 | 616 | 734 | 731 | 816 | 26.13 | 2923.13 | 2781.75 | 141.38 | 2930 | 3.811 | 74.93% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-12:23 to 12:28
2018-08-27 | 543 | 640 | 635 | 711 | 20.38 | 2549.38 | 2438.25 | 111.13 | 2550 | 3.214 | 77.33% | Module clean by Rain & Fully Rain & cloudy day
2018-08-28 | 757 | 899 | 897 | 1028 | 32.57 | 3613.57 | 3501.75 | 111.82 | 3620 | 4.566 | 77.27% | Module clean by Rain & Fully Rain & cloudy day
2018-08-29 | 385 | 446 | 444 | 494 | 14.93 | 1783.93 | 1686 | 97.93 | 1790 | 2.141 | 81.49% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-17:30 to 17:43
2018-08-30 | 379 | 430 | 433 | 479 | 13.69 | 1734.69 | 1627 | 107.69 | 1740 | 2.001 | 84.75% | Module clean by Rain & Fully Rain & cloudy day
2018-08-31 | 407 | 469 | 469 | 514 | 16.31 | 1875.31 | 1793.25 | 82.06 | 1880 | 2.852 | 64.25% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-10:57 to 12:30
2018-09-01 | 576 | 678 | 670 | 771 | 24.58 | 2719.58 | 2597.25 | 122.33 | 2720 | 3.68 | 72.04% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-08:47 to 09:33
2018-09-02 | 747 | 882 | 872 | 1008 | 28.83 | 3537.83 | 3420 | 117.83 | 3540 | 4.479 | 77.03% | Module clean by Rain & Fully Rain & cloudy day
2018-09-03 | 344 | 396 | 404 | 439 | 12.61 | 1595.61 | 1482 | 113.61 | 1600 | 1.952 | 79.89% | Module clean by Rain & Fully Rain & cloudy day
2018-09-04 | 735 | 865 | 857 | 952 | 27.51 | 3436.51 | 3303 | 133.51 | 3440 | 4.311 | 77.77% | Module clean by Rain & Fully Rain & cloudy day
2018-09-05 | 848 | 1018 | 1003 | 1134 | 35.29 | 4038.29 | 3900 | 138.29 | 4040 | 5.039 | 78.14% | Module clean by Rain & Fully Rain & cloudy day
2018-09-06 | 916 | 1102 | 1088 | 1240 | 38.12 | 4384.12 | 4236 | 148.12 | 4390 | 5.721 | 74.79% | Module clean by Rain
2018-09-07 | 735 | 871 | 872 | 973 | 32.1 | 3483.1 | 3354 | 129.1 | 3490 | 4.514 | 75.36% | Module clean by Rain & Fully Rain & cloudy day
2018-09-08 | 243 | 282 | 282 | 287 | 8.41 | 1102.41 | 1027.5 | 74.91 | 1110 | 1.395 | 77.55% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-15:45 to 15:55
2018-09-09 | 243 | 277 | 278 | 298 | 8.19 | 1104.19 | 1014.75 | 89.44 | 1110 | 1.352 | 80.02% | Module clean by Rain & Fully Rain & cloudy day
2018-09-10 | 294 | 328 | 337 | 358 | 21.74 | 1338.74 | 1233.75 | 104.99 | 1340 | 1.692 | 77.19% | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-14:15 to 15:30
2018-09-11 | 780 | 933 | 928 | 1058 | 32.65 | 3731.65 | 3597 | 134.65 | 3735 | 4.812 | 75.65% | Module clean by Rain & Fully cloudy day
2018-09-12 | 679 | 797 | 796 | 882 | 26.6 | 3180.6 | 3048 | 132.6 | 3185 | 4.119 | 75.37% | Module clean by Rain & Fully cloudy day & Grid Failure From-09:00 to 09:03
2018-09-13 | 803 | 967 | 958 | 1074 | 34.4 | 3836.4 | 3708 | 128.4 | 3840 | 5.366 | 69.75% | Module clean by Rain & Fully cloudy day & Grid Failure From-12:12 to 12:20
2018-09-14 | 774 | 910 | 897 | 998 | 30.7 | 3609.7 | 3483.75 | 125.95 | 3612 | 4.839 | 72.75% | Module clean by Rain & Fully cloudy day & Grid Failure From-07:22 to 7:44
2018-09-15 | 797 | 950 | 942 | 1073 | 33 | 3795 | 3675 | 120 | 3800 | 4.96 | 74.67% | Module clean by Rain & Fully cloudy day & Grid Failure From-15:32 to 15:35 and 17:58 to 18:08
2018-09-16 | 814 | 978 | 963 | 1099 | 34.8 | 3888.8 | 3747.75 | 141.05 | 3895 | 5.321 | 71.35% | Module clean by Rain & cloudy day
2018-09-17 | 826 | 995 | 982 | 1068 | 33.46 | 3904.46 | 3767.25 | 137.21 | 3910 | 5.308 | 71.8% | Module clean by Rain & cloudy day
2018-09-18 | 893 | 1068 | 1053 | 1220 | 38.84 | 4272.84 | 4095.75 | 177.09 | 4280 | 5.9 | 70.7% | Module clean by Rain & cloudy day
2018-09-19 | 944 | 1142 | 1124 | 1301 | 39.95 | 4550.95 | 4430.25 | 120.7 | 4555 | 6.211 | 71.48% | Module clean by Rain & cloudy day
2018-09-20 | 967 | 1176 | 1154 | 1370 | 40.3 | 4707.3 | 4560 | 147.3 | 4711 | 6.409 | 71.64% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 & total module cleaning-792, |  | 792
2018-09-21 | 978 | 1188 | 1180 | 1392 | 41.53 | 4779.53 | 4604.25 | 175.28 | 4783 | 6.457 | 72.2% | Module Cleaning has been done in Row-,G,H,I,J,, Inverter No-4 & total module cleaning-774, |  | 774
2018-09-22 | 447 | 520 | 534 | 604 | 18.03 | 2123.03 | 2037.75 | 85.28 | 2127 | 2.785 | 74.44% | Module clean by Rainy & Fully cloudy day & Grid Failure From-15:01 to 15:07 and 18:01 to 18:10.
2018-09-23 | 367 | 424 | 429 | 469 | 13.35 | 1702.35 | 1613.25 | 89.1 | 1706 | 2.119 | 78.47% | Module clean by Rain & Fully cloudy day & Grid Failure From-7:44 to 7:50,7:53 to 7:59,8:02 to 8:10,9:16 to 9:24 and 11:56 to 11:59.
2018-09-24 | 492 | 570 | 579 | 630 | 18.78 | 2289.78 | 2191.5 | 98.28 | 2293 | 2.968 | 75.3% | Module clean by Rain & Fully cloudy day
2018-09-25 | 944 | 1143 | 1129 | 1285 | 39.86 | 4540.86 | 4395 | 145.86 | 4545 | 6.264 | 70.72% | Module clean by Rain & cloudy day & Grid Failure From-09:06 to 09:12,
2018-09-26 | 983 | 1198 | 1180 | 1346 | 41.08 | 4748.08 | 4595.25 | 152.83 | 4752 | 6.545 | 70.77% | Module clean by Rain
2018-09-27 | 973 | 1204 | 1194 | 1351 | 41 | 4763 | 4603.5 | 159.5 | 4767 | 6.541 | 71.03% | Module Cleaning has been done in Row-N,O,P,Q,R,S,T., Inverter No-3 & total module cleaning-840,Grid Failure From-17:32 to 17:37, |  | 840
2018-09-28 | 989 | 1210 | 1210 | 1361 | 41.3 | 4811.3 | 4650 | 161.3 | 4815 | 6.621 | 70.88% | Module Cleaning has been done in Row-M,L,K,J, Inverter No-2 and 3 & total module cleaning-1071. |  | 1071
2018-09-29 | 967 | 1210 | 1184 | 1320 | 40.64 | 4721.64 | 4576.5 | 145.14 | 4725 | 6.501 | 70.84% | Module Cleaning has been done in Row-I,H,G,F, Inverter No-1 and 2 & total module cleaning-903. |  | 903
2018-09-30 | 978 | 1210 | 1180 | 1306 | 40.53 | 4714.53 | 4552.5 | 162.03 | 4719 | 6.423 | 71.61%
2018-10-01 | 978 | 1193 | 1164 | 1280 | 40.15 | 4655.15 | 4502.25 | 152.9 | 4660 | 6.4 | 70.97% | Module Cleaning has been done in Row-A,B,C,D,E,& A,B,C,D, Inverter No-1 and 4, total module cleaning-915. |  | 915
2018-10-02 | 927 | 1119 | 1094 | 1189 | 38.46 | 4367.46 | 4220.25 | 147.21 | 4370 | 6.003 | 70.95% | Module Cleaning has been done in Row-,E,F,G,H,I, Inverter No-4, total module cleaning-954. |  | 954
2018-10-03 | 809 | 967 | 947 | 1054 | 34.32 | 3811.32 | 3687 | 124.32 | 3815 | 5.19 | 71.64% | Module Cleaning has been done in Row-,J,K,L, & Q,R,S,T and Tracker ,Inverter No-3 and 4, total module cleaning-822. |  | 822
2018-10-04 | 882 | 1063 | 1054 | 1189 | 37.72 | 4225.72 | 4078.5 | 147.22 | 4229 | 5.788 | 71.21% | Module Cleaning has been done in Row-,L,M,N,O ,Inverter No-2 and 3, total module cleaning-1050. |  | 1050
2018-10-05 | 915 | 1125 | 1119 | 1250 | 39.57 | 4448.57 | 4308 | 140.57 | 4452 | 5.197 | 83.49% | Module Cleaning has been done in Row-I,J,K, Inverter No-2 , total module cleaning-840.Grid Failure From-11:10 to 11:15, |  | 840
2018-10-06 | 950 | 1176 | 1139 | 1281 | 40.11 | 4586.11 | 4424 | 162.11 | 4590 | 6.169 | 72.52% | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-1 , total module cleaning-903. |  | 903
2018-10-07 | 927 | 1131 | 1099 | 1224 | 39.25 | 4420.25 | 4274.25 | 146 | 4424 | 6.122 | 70.43% | No Module Cleaning
2018-10-08 | 843 | 1011 | 987 | 1079 | 34.8 | 3954.8 | 3824 | 130.8 | 3958 | 5.437 | 70.95% | Module Cleaning has been done in Row-A,B,C, & A,B,C,D,E , Inverter No-1 and 4 , total module cleaning-804. |  | 804
2018-10-09 | 871 | 1052 | 1024 | 1124 | 37.73 | 4108.73 | 3956 | 152.73 | 4112 | 5.701 | 70.3% | Module Cleaning has been done in Row-F,G,H, Inverter No-4 , total module cleaning-574. |  | 574
2018-10-10 | 876 | 1063 | 1033 | 1134 | 37.34 | 4143.34 | 4004.2 | 139.14 | 4147 | 5.747 | 70.33% | Module Cleaning has been done in Row-I,J,K, Inverter No-4 , total module cleaning-438. |  | 438
2018-10-11 | 848 | 1017 | 993 | 1119 | 36.6 | 4013.6 | 3874.5 | 139.1 | 4020 | 5.446 | 71.95% | Module Cleaning has been done in Row-K,L, & Trackers,& O,P,Q,R,S,T., Inverter No-3&4, & total module cleaning-918,Grid Failure From-17:27 to 17:37, |  | 918
2018-10-12 | 825 | 995 | 998 | 1114 | 36.18 | 3968.18 | 3829.5 | 138.68 | 3972 | 5.422 | 71.4% | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2 &3 , total module cleaning-987. |  | 987
2018-10-13 | 842 | 1057 | 1028 | 1149 | 36.67 | 4112.67 | 3967.5 | 145.17 | 4116 | 5.758 | 69.67% | Module Cleaning has been done in Row-H,I,J, Inverter No-1 &2 , total module cleaning-798,Grid Failure From-16:12 to 16:49. |  | 798
2018-10-14 | 832 | 1035 | 998 | 1099 | 36.79 | 4000.79 | 3863.2 | 137.59 | 4004 | 5.417 | 72.04% | No Module Cleaning
2018-10-15 | 876 | 1103 | 1063 | 1174 | 38.38 | 4254.38 | 4098 | 156.38 | 4258 | 5.778 | 71.83% | No Module Cleaning
2018-10-16 | 803 | 977 | 953 | 1028 | 35.57 | 3796.57 | 3664.5 | 132.07 | 3800 | 5.209 | 71.1% | Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 , total module cleaning-882. |  | 882
2018-10-17 | 882 | 1058 | 1023 | 1114 | 37.68 | 4114.68 | 3974.2 | 140.48 | 4118 | 5.825 | 68.9% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 , total module cleaning-792,Grid Failure From-15:30 to 15:35. |  | 792
2018-10-18 | 876 | 1046 | 1008 | 1109 | 37.44 | 4076.44 | 3928.5 | 147.94 | 4080 | 5.627 | 70.67% | Module Cleaning has been done in Row-G,H,I, Inverter No-4 , total module cleaning-594. |  | 594
2018-10-19 | 825 | 1000 | 963 | 1074 | 36.23 | 3898.23 | 3756 | 142.23 | 3902 | 5.05 | 75.31% | Module Cleaning has been done in Row-J,K,L & Tracker, Inverter No-4 , total module cleaning-528,Grid Failure From-13:52 to 14:22. |  | 528
2018-10-20 | 860 | 1024 | 1003 | 1174 | 37.46 | 4098.46 | 3957 | 141.46 | 4102 | 5.739 | 69.66% | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3 , total module cleaning-630,Grid Failure From-17:24 to 17:30. |  | 630
2018-10-21 | 944 | 1147 | 1139 | 1305 | 41.25 | 4576.25 | 4424.25 | 152 | 4580 | 6.366 | 70.12% | No Moule Cleaning
2018-10-22 | 882 | 1057 | 1069 | 1180 | 39.78 | 4227.78 | 4079.25 | 148.53 | 4230 | 5.941 | 69.4% | Module Cleaning has been done in Row-,M,N, Inverter No-3 , total module cleaning-462, & Grid Failure From-16:30 to 16:40. |  | 462
2018-10-23 | 882 | 1092 | 1083 | 892 | 39.22 | 3988.22 | 3839.25 | 148.97 | 3992 | 5.905 | 65.89% | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 , total module cleaning-1092. |  | 1092
2018-10-24 | 904 | 1130 | 1084 | 1210 | 39.05 | 4367.05 | 4218.75 | 148.3 | 4371 | 5.993 | 71.09% | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-1 , total module cleaning-840. |  | 840
2018-10-25 | 910 | 1108 | 1058 | 1149 | 38.46 | 4263.46 | 4113.75 | 149.71 | 4268 | 5.991 | 69.43% | Module Cleaning has been done in Row-A,B,C,D, and A,B,C,D,E Inverter No-1 & 4, total module cleaning-785. |  | 785
2018-10-26 | 910 | 1103 | 1049 | 1205 | 38.46 | 4305.46 | 4158.75 | 146.71 | 4309 | 5.188 | 80.95% | Module Cleaning has been done in Row-E,F,G,H,I, Inverter No- 4, total module cleaning-772. |  | 774
2018-10-27 | 815 | 983 | 942 | 1098 | 35.62 | 3873.62 | 3736.5 | 137.12 | 3877 | 5.792 | 65.24% | Module Cleaning has been done in Row-I,J,K, Inverter No-4 , total module cleaning-440, & Grid Failure From-10:07 to 10:34. |  | 442
2018-10-28 | 864 | 1041 | 993 | 1154 | 37.31 | 4089.31 | 3945.75 | 143.56 | 4100 | 5.723 | 69.83% | No Module Cleaning
2018-10-29 | 888 | 1068 | 1028 | 1200 | 39.41 | 4223.41 | 4074 | 149.41 | 4230 | 5.884 | 70.07% | Module Cleaning has been done in Row-,L,& Trackers, O,P,Q,R,S,T, Inverter No-4&3 , total module cleaning-814, |  | 814
2018-10-30 | 888 | 1068 | 1079 | 1185 | 39.63 | 4259.63 | 4107.75 | 151.88 | 4263 | 5.832 | 71.24% | Module Cleaning has been done in Row-K,L,M,N Inverter No-2 &3, total module cleaning-987. |  | 987
2018-10-31 | 876 | 1109 | 1074 | 1174 | 39.19 | 4272.19 | 4109.25 | 162.94 | 4280 | 5.598 | 74.52% | Module Cleaning has been done in Row-,G,H,I,J, Inverter No-1&2, total module cleaning-1008. |  | 1008
2018-11-01 | 910 | 1108 | 1063 | 1174 | 39.05 | 4294.05 | 4148.25 | 145.8 | 4298 | 5.932 | 70.62% | Module Cleaning has been done in Row-A,B,C,D,E,F & A,B,C, Inverter No-1 & 4, total module cleaning-960. |  | 960
2018-11-02 | 876 | 1062 | 1023 | 1124 | 37.68 | 4122.68 | 3969.75 | 152.93 | 4126 | 5.772 | 69.67% | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-4 , total module cleaning-900,Grid Failure From-16:20 to 16:23. |  | 900
2018-11-03 | 820 | 984 | 948 | 802 | 35.79 | 3589.79 | 3454.5 | 135.29 | 3593 | 5.418 | 64.64% | Module Cleaning has been done in Row-I,J,K,L & Q,R,S,T, and Tracker, Inverter No-4 & 3, total module cleaning-1020. |  | 1020
2018-11-04 | 814 | 984 | 952 | 1078 | 35.93 | 3863.93 | 3727.5 | 136.43 | 3867 | 5.398 | 69.82% | No Module Cleaning
2018-11-05 | 837 | 1000 | 988 | 1104 | 37.29 | 3966.29 | 3817 | 149.29 | 3970 | 5.521 | 70.09% | Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 & 3 , total module cleaning-924,Grid Failure From-10:06 to 10:08 and 15:23 to 15:30. |  | 924
2018-11-06 | 870 | 1064 | 1054 | 1164 | 39.01 | 4191.01 | 4045.5 | 145.51 | 4195 | 5.785 | 70.68% | Grid Failure From - 08:52 to 08:58.
2018-11-07 | 894 | 1090 | 1073 | 1160 | 40.36 | 4257.36 | 4110.75 | 146.61 | 4261 | 5.9 | 70.39% | No Module Cleaning
2018-11-08 | 854 | 1024 | 1023 | 1063 | 38.91 | 4002.91 | 3864 | 138.91 | 4006 | 5.599 | 69.74% | No Module Cleaning
2018-11-09 | 813 | 983 | 973 | 1038 | 37.05 | 3844.05 | 3702.75 | 141.3 | 3848 | 5.415 | 69.26% | No Module Cleaning
2018-11-10 | 826 | 1001 | 988 | 1039 | 37.49 | 3891.49 | 3761.25 | 130.24 | 3895 | 5.503 | 68.99% | No Module Cleaning
2018-11-11 | 843 | 1018 | 1008 | 1109 | 38.12 | 4016.12 | 3879.75 | 136.37 | 4020 | 5.674 | 69.05% | No Module Cleaning
2018-11-12 | 814 | 983 | 973 | 1063 | 36.92 | 3869.92 | 3729 | 140.92 | 3873 | 5.036 | 74.96% | No Module Cleaning
2018-11-13 | 757 | 899 | 892 | 958 | 34.63 | 3540.63 | 3416.25 | 124.38 | 3540 | 5.031 | 68.58% | No Module Cleaning
2018-11-14 | 746 | 905 | 892 | 947 | 34.45 | 3524.45 | 3379.5 | 144.95 | 3530 | 5.034 | 68.35% | No Module Cleaning
2018-11-15 | 792 | 955 | 943 | 1049 | 36.11 | 3775.11 | 3646.5 | 128.61 | 3779 | 5.399 | 68.22% | Grid Failure From - 10:02 to 10:09.
2018-11-16 | 752 | 893 | 887 | 942 | 35.01 | 3509.01 | 3378.75 | 130.26 | 3513 | 5.043 | 67.9% | Grid Failure From - 09:55 to 09:58.
2018-11-17 | 45 | 51 | 40 | 45 | 2.32 | 183.32 | 118.5 | 64.82 | 190 | 5.458 | 3.393% | Grid Failure From - 07:29 to 16:00.
2018-11-18 | 797 | 961 | 953 | 999 | 36.83 | 3746.83 | 3608.25 | 138.58 | 3750 | 5.53 | 66.09% | No Module Cleaning
2018-11-19 | 797 | 973 | 947 | 1002 | 36.54 | 3755.54 | 3625.5 | 130.04 | 3760 | 5.56 | 65.91% | No Module Cleaning
2018-11-20 | 792 | 950 | 933 | 1059 | 36.34 | 3770.34 | 3634.5 | 135.84 | 3774 | 5.477 | 67.16% | No Module Cleaning
2018-11-21 | 740 | 882 | 872 | 978 | 33.87 | 3505.87 | 3379.5 | 126.37 | 3509 | 4.869 | 70.24% | No Module Cleaning
2018-11-22 | 712 | 859 | 841 | 902 | 32.98 | 3346.98 | 3222.75 | 124.23 | 3350 | 5.005 | 65.24% | Grid Failure From - 13:04 to 13:07.
2018-11-23 | 752 | 893 | 882 | 998 | 34.57 | 3559.57 | 3435.75 | 123.82 | 3563 | 5.163 | 67.26% | No Module Cleaning
2018-11-24 | 741 | 887 | 867 | 968 | 23.25 | 3486.25 | 3363.75 | 122.5 | 3367 | 5.105 | 64.28% | No Module Cleaning
2018-11-25 | 741 | 894 | 877 | 967 | 45.62 | 3524.62 | 3390 | 134.62 | 3530 | 5.153 | 66.77% | No Module Cleaning
2018-11-26 | 661 | 775 | 761 | 847 | 28.93 | 3072.93 | 2958 | 114.93 | 3076 | 4.428 | 67.71% | Couldy Day & Grid Failure From - 17:12 to 17:50.
2018-11-27 | 633 | 740 | 731 | 812 | 28.95 | 2944.95 | 2819.25 | 125.7 | 2949 | 4.198 | 68.47% | Couldy Day & No Module cleaning.
2018-11-28 | 532 | 616 | 605 | 655 | 24.67 | 2432.67 | 2325 | 107.67 | 2440 | 3.559 | 66.82% | Couldy Day & No Module cleaning.
2018-11-29 | 752 | 893 | 857 | 963 | 34.72 | 3499.72 | 3361.5 | 138.22 | 3503 | 4.833 | 70.64% | No Module Cleaning
2018-11-30 | 706 | 843 | 806 | 897 | 33.16 | 3285.16 | 3174 | 111.16 | 3289 | 4.548 | 70.48% | Today Replaced The D.C.12 Amp Fuse Link of The String-03--tive in AJB-114 of The Inverter-3 during The Period of 16:40 To 16:45 and Inverter No -1 ,ABB Primary Maintenance Done & No Module Cleaning.
2018-12-01 | 645 | 763 | 736 | 766 | 30.2 | 2940.2 | 2820 | 120.2 | 2944 | 4.465 | 64.26% | Module Cleaning has been done in Row-A,B,C,D,E,F. Inverter No-4 , total module cleaning-792,Grid Failure From-10:32 to 10:40. |  | 792
2018-12-02 | 593 | 695 | 676 | 761 | 27.31 | 2752.31 | 2637 | 115.31 | 2756 | 3.923 | 68.47% | Couldy Day & No Module cleaning.
2018-12-03 | 667 | 780 | 756 | 872 | 31.03 | 3106.03 | 2975.25 | 130.78 | 3110 | 4.609 | 65.77% | Module Cleaning has been done in Row-G,H,I,J,K. Inverter No-4 , total module cleaning-936 ,today Inverter No -2 , ABB Primary Maintenance Done. |  | 936
2018-12-04 | 532 | 617 | 604 | 766 | 27.21 | 2546.21 | 2436 | 110.21 | 2550 | 3.677 | 67.59% | Module Cleaning has been done in Row-L, & P,Q,R,S,T & Tracker. Inverter No-4 and 3 , total module cleaning-627,Grid Failure From-11:21 to 11:27. |  | 627
2018-12-05 | 616 | 718 | 777 | 877 | 32.54 | 3020.54 | 2900.25 | 120.29 | 3024 | 4.337 | 67.96% | Today Replaced The D.C.12 Amp Fuse Link of The String-02 ++tive in AJB-113 of The Inverter-3 during The Period of 16:55 To 17:00 and Module Cleaning has been done in Row-L,M,N,O. Inverter No-2 & 3 , total module cleaning-803, Inverter No -3 ,ABB Primary Maintanance Done. |  | 803
2018-12-06 | 639 | 819 | 882 | 892 | 34.25 | 3266.25 | 3141.75 | 124.5 | 3270 | 4.278 | 74.5% | Module Cleaning has been done in Row-J,K,L. Inverter No-2 , total module cleaning-667, Inverter No-4 , ABB Primary Maintanance Done. |  | 667
2018-12-07 | 679 | 950 | 912 | 968 | 35.77 | 3544.77 | 3408 | 136.77 | 3549 | 4.725 | 73.21% | Module Cleaning has been done in Row-G,H,I. Inverter No-1 and 2 , total module cleaning-714. |  | 714
2018-12-08 | 745 | 944 | 902 | 957 | 34.98 | 3582.98 | 3438.75 | 144.23 | 3590 | 4.684 | 74.7% | Module Cleaning has been done in Row-A,B,C,D,E,F. Inverter No-1 , total module cleaning-672. |  | 672
2018-12-09 | 809 | 972 | 928 | 993 | 36.42 | 3738.42 | 3605.25 | 133.17 | 3740 | 4.987 | 73.09% | No module cleaning
2018-12-10 | 775 | 928 | 887 | 782 | 34.75 | 3406.75 | 3264.75 | 142 | 3410 | 4.828 | 68.84% | Module Cleaning has been done in Row-A,B,C,D,E,F,G. Inverter No-4 , total module cleaning-990. |  | 990
2018-12-11 | 678 | 808 | 776 | 821 | 31.67 | 3114.67 | 2986.5 | 128.17 | 3119 | 4.213 | 72.16% | Module Cleaning has been done in Row-H,I,J,K,L and Tracker. Inverter No-4 , total module cleaning-924. |  | 924
2018-12-12 | 741 | 882 | 857 | 978 | 33.74 | 3491.74 | 3354.75 | 136.99 | 3495 | 4.584 | 74.31% | Module Cleaning has been done in Row-O,P,Q,R,S,T. Inverter No-3 , total module cleaning-630. |  | 630
2018-12-13 | 802 | 962 | 962 | 1038 | 38.3 | 3802.3 | 3654 | 148.3 | 3806 | 4.986 | 74.4% | Module Cleaning has been done in Row-K,L,M,N. Inverter No-2 and 3 , total module cleaning-987. |  | 987
2018-12-14 | 803 | 994 | 968 | 1028 | 37.79 | 3830.79 | 3682.5 | 148.29 | 3835 | 5.136 | 72.78% | Grid Failure From-13:04 to 13:16, Module Cleaning has been done in Row-G,H,I,J. Inverter No-1 and 2 , total module cleaning-1008. |  | 1008
2018-12-15 | 837 | 1012 | 978 | 1039 | 38.01 | 3904.01 | 3758 | 146.01 | 3908 | 4.959 | 76.81% | Module Cleaning has been done in Row-A,B,C,D,E,F & A,B,C. Inverter No-1 and 4 , total module cleaning-960. |  | 960
2018-12-16 | 735 | 871 | 842 | 922 | 33.61 | 3403.61 | 3261.75 | 141.86 | 3407 | 4.47 | 74.29%
2018-12-17 | 797 | 967 | 927 | 968 | 37.56 | 3696.56 | 3550.5 | 146.06 | 3700 | 4.859 | 74.22% | Module Cleaning has been done in Row-D,E,F,G,H,I. Inverter No-4 , total module cleaning-1098. |  | 1098
2018-12-18 | 865 | 1057 | 1013 | 1109 | 38.96 | 4082.96 | 3927 | 155.96 | 4090 | 5.444 | 73.22% | Module Cleaning has been done in Row-,J,K,L,&,P,Q,R,S,T,&Trackers. Inverter No-4 & 3 , total module cleaning-969. |  | 969
2018-12-19 | 853 | 1034 | 1018 | 1098 | 39.9 | 4042.9 | 3900 | 142.9 | 4046 | 5.458 | 72.25% | Module Cleaning has been done in Row-L,M,N,O. Inverter No-2 & 3 , total module cleaning-903. |  | 903
2018-12-20 | 854 | 1063 | 1033 | 1114 | 39.56 | 4103.56 | 3952.5 | 151.06 | 4107 | 5.511 | 72.64% | Module Cleaning has been done in Row-H,I,J,K. Inverter No-1 & 2 , total module cleaning-955. & Main Transformer (1250 KVA) primary maintenace Done. |  | 955
2018-12-21 | 876 | 1086 | 1039 | 1134 | 40.58 | 4175.58 | 4021.5 | 154.08 | 4179 | 5.7 | 71.46% | Grid Failure From-08:02 to 08:08, Module Cleaning has been done in Row-A,B,C,D,E,F,G,H and A, Inverter No-1 and 4 , total module cleaning-1070, Today Breakedown of VCB on 17:34 to 18:40 due to Spring charged motor remove. |  | 1070
2018-12-22 | 826 | 1006 | 968 | 973 | 36.72 | 3809.72 | 3660.75 | 148.97 | 3813 | 5.335 | 69.66% | Grid Failure From-08:44 to 08:48, Module Cleaning has been done in Row-,B,C,D,E,F, Inverter No-4 , total module cleaning-720 |  | 720
2018-12-23 | 842 | 1018 | 977 | 1069 | 36.46 | 3942.46 | 3801 | 141.46 | 3946 | 5.482 | 70.16% | Grid Failure From-14:01 to 14:06.
2018-12-24 | 808 | 977 | 256 | 846 | 36.51 | 2923.51 | 2799 | 124.51 | 2930 | 5.171 | 55.23% | Today morning time Inverter No :-3 ,ABB 250KW not wake up due to error " CH2 COM LOSS (7520)" ,Reset manually Inverter started 14:00.& Grid Failure From-17:47 to 18:07, Module Cleaning has been done in Row-,H,I,J,K,L, & Trackers, Inverter No-4 , total module cleaning-1122. |  | 1122
2018-12-25 | 837 | 1018 | 988 | 1089 | 38.89 | 3970.89 | 3831.75 | 139.14 | 3974 | 5.276 | 73.41% | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3 , total module cleaning-630. |  | 630
2018-12-26 | 849 | 1030 | 1013 | 1084 | 36.14 | 4012.14 | 3859.5 | 152.64 | 4016 | 5.219 | 75% | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2 & 3 , total module cleaning-814. |  | 814
2018-12-27 | 853 | 1073 | 1039 | 1124 | 40.29 | 4129.29 | 3979.5 | 149.79 | 4133 | 5.747 | 70.09% | Grid Failure From-12:17 to 12:22 and 15:17 to 15:24 , Module Cleaning has been done in Row-H,I,J,K, Inverter No-1 & 2 , total module cleaning-971. |  | 971
2018-12-28 | 904 | 1114 | 1063 | 1144 | 41.5 | 4266.5 | 4108.5 | 158 | 4270 | 5.689 | 73.16% | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A. Inverter No-1 and 4 , total module cleaning-954.
2018-12-29 | 809 | 978 | 938 | 973 | 34.03 | 3732.03 | 3582 | 150.03 | 3736 | 5.834 | 62.42% | Grid Failure From-11:21 to 12:17 , Module Cleaning has been done in Row-B,C,D,E,F, Inverter No-4 , total module cleaning-720. |  | 720
2018-12-30 | 814 | 1074 | 1018 | 1119 | 38.88 | 4063.88 | 3914.25 | 149.63 | 4067 | 5.584 | 70.99% | Today morning time Inverter No-1, ABB 250KW not wake up Due to error of " EXT DI1 ALM (1089)",Reset manually Inverter started-09:27.
2018-12-31 | 876 | 1063 | 1018 | 1098 | 38.9 | 4093.9 | 3936.75 | 157.15 | 4100 | 5.635 | 70.92% | Grid Failure From-12:00 to 12:05, Module Cleaning has been done in Row-,G,H,I,J,K,L, & Trackers, Inverter No-4 , total module cleaning-1122. |  | 1122
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
Note on C76: Author: In-no-2 ABB Auto Trip 13:30 to 18:00

## 2019
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2019
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
PDPU
[6 empty] | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | Total NO- Of Clean Modules
Inverter generation (KWH)
Date | 1104500527 | 1104500529 | 9175000042 | 9170301408 | 2100570073/ 2100567820/ 2100567898
2018-01-01 | 814 | 990 | 947 | 1024 | 37.94 | 3812.94 | 3658.5 | 154.44 | 3816 | 5.357 | 69.43% | Grid Failure From-15:49 to 15:56, Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-4 , total module cleaning-524. |  | 524
2019-01-02 | 809 | 1023 | 988 | 1063 | 37.74 | 3920.74 | 3779.25 | 141.49 | 3924 | 5.38 | 71.09% | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " GND CLOSER ER (8196)" ,Reset manually Inverter started 9:05.& Grid Failure From-16:03 to 16:07, Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No-3 , total module cleaning-441. |  | 441
2019-01-03 | 859 | 1046 | 1049 | 1119 | 40.45 | 4113.45 | 3995.25 | 118.2 | 4117 | 5.598 | 71.68% | Grid Failure From-17:19 to 17:20, Module Cleaning has been done in Row-L,M,N,O, Inverter No-2 & 3 , total module cleaning-903. |  | 903
2019-01-04 | 803 | 1006 | 978 | 1048 | 38.59 | 3873.59 | 3717.75 | 155.84 | 3877 | 5.136 | 73.57% | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-1 & 2 , total module cleaning-1281. |  | 1281
2019-01-05 | 775 | 944 | 907 | 943 | 34.61 | 3603.61 | 3465 | 138.61 | 3607 | 4.808 | 73.12% | Module Cleaning has been done in Row-A,B,C,D,E,F & A,B, Inverter No-1 & 4 , total module cleaning-792. |  | 792
2019-01-06 | 944 | 1153 | 1109 | 1154 | 41.37 | 4401.37 | 4240.5 | 160.87 | 4405 | 5.946 | 72.21%
2019-01-07 | 842 | 1007 | 972 | 993 | 38.56 | 3852.56 | 3697.5 | 155.06 | 3860 | 5.184 | 72.57% | Module Cleaning has been done in Row-C,D,E,F Inverter No- 4 , total module cleaning-630. |  | 630
2019-01-08 | 842 | 1017 | 978 | 1038 | 38.55 | 3913.55 | 3768 | 145.55 | 3920 | 5.26 | 72.64% | Module Cleaning has been done in Row-,G,H,I,J,K, Inverter No- 4 , total module cleaning-936. |  | 936
2019-01-09 | 798 | 955 | 928 | 1013 | 37.08 | 3731.08 | 3588.75 | 142.33 | 3735 | 5.008 | 72.69% | Grid Failure From-12:28 to 12:35, Module Cleaning has been done in Row-L, &O,P,Q,R,S,T, and Trackers, Inverter No-4 & 3 , total module cleaning-816. |  | 816
2019-01-10 | 847 | 1035 | 1033 | 1104 | 39.75 | 4058.75 | 3912 | 146.75 | 4062 | 5.336 | 74.2% | Module Cleaning has been done in Row-K,L,M,N, Inverter No- 2 & 3 , total module cleaning-987. |  | 987
2019-01-11 | 843 | 1063 | 1028 | 1104 | 39.43 | 4077.43 | 3929.25 | 148.18 | 4081 | 5.35 | 74.35% | Today Inverter No:1(17:13 to 17:55) Breakdown due to Primary Maintenance by AMC (ABB). Module Cleaning has been done in Row G,H,I,J , Inverter No-1 & 2, total module cleaning-1008 |  | 1008
2019-01-12 | 842 | 1023 | 988 | 1033 | 37.99 | 3923.99 | 3786.75 | 137.24 | 3927 | 5.08 | 75.34% | Grid Failure From-11:11 to 11:14, Module Cleaning has been done in Row-A,B,C,D,E,F, &A,B,C,D, Inverter No-1 & 4 , total module cleaning-1104. |  | 1104
2019-01-13 | 763 | 922 | 892 | 933 | 34.94 | 3544.94 | 3403.5 | 141.44 | 3549 | 5.241 | 66% | Grid Failure From-14:24 to 14:35 and 14:36 to 15:04.
2019-01-14 | 741 | 899 | 862 | 650 | 32.01 | 3184.01 | 3063 | 121.01 | 3188 | 5.096 | 60.97% | Grid Failure From-11:16 to 11:23,12:47 to 12:58,13:48 to 13:58,14:28 to 14:33 and 16:30 to 17:18.Today Inverter No:4 are wake up after grid failure from 13:58, Due to Error ">RUN DISABLE (8194)" Reset manually inverter started 16:05.
2019-01-15 | 814 | 978 | 942 | 968 | 36.13 | 3738.13 | 3584.25 | 153.88 | 3740 | 5.259 | 69.31% | Grid Failure From-12:48 to 12:58. & Module cleaning has been done in row- E,F,G,H, Inveter No-4, Total module cleaning-756. |  | 756
2019-01-16 | 871 | 1063 | 1024 | 1124 | 39.14 | 4121.14 | 3966 | 155.14 | 4125 | 5.594 | 71.87% | ꟷ
2019-01-17 | 859 | 1045 | 1008 | 1063 | 38.75 | 4013.75 | 3878.25 | 135.5 | 4017 | 5.315 | 73.66% | Module Cleaning has been done in Row-I,J,K,L, &,Q,R,S,T, and Trackers, Inverter No-4 & 3 , total module cleaning-1020. |  | 1020
2019-01-18 | 876 | 1069 | 1063 | 1159 | 40.29 | 4207.29 | 4037.25 | 170.04 | 4211 | 5.435 | 75.52% | Today Installed new energy meter by UGVCL.it connect to series connection of old meter and only purpose of measuring of HVAR and LVAR parameter.Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 & 3 , total module cleaning-1050. |  | 1050
2019-01-19 | 899 | 1136 | 1109 | 1190 | 41.61 | 4375.61 | 4209.75 | 165.86 | 4379 | 5.506 | 77.52% | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-1&2 , total module cleaning-1281. |  | 1281
2019-01-20 | 809 | 1012 | 973 | 1003 | 37.01 | 3834.01 | 3682.5 | 151.51 | 3838 | 5.087 | 73.54%
2019-01-21 | 780 | 939 | 907 | 897 | 34.79 | 3557.79 | 3428.25 | 129.54 | 3561 | 4.963 | 69.93% | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " GND CLOSER ER (8196)" ,Reset manually Inverter started 9:05.& Grid Failure From-16:40 to 17:50, Module Cleaning has been done in Row-A,B,C,D,E,F & A,B. Inverter No-1 & 4 , total module cleaning-834. |  | 834
2019-01-22 | 820 | 984 | 948 | 912 | 37.02 | 3701.02 | 3546.75 | 154.27 | 3710 | 4.942 | 73.17% | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " GND CLOSER ER (8196)" ,Reset manually Inverter started 9:04.& Module Cleaning has been done in Row-C,D,E,F,G. Inverter No-4 , total module cleaning-828. |  | 828
2019-01-23 | 819 | 989 | 952 | 1029 | 34.9 | 3823.9 | 3682.5 | 141.4 | 3827 | 5.214 | 71.54% | Module Cleaning has been done in Row-H,I,J,K,L, &,T, and Trackers, Inverter No-4 & 3 , total module cleaning-945.Grid Failure From-12:50 to 13:02 |  | 945
2019-01-24 | 910 | 1108 | 1094 | 1189 | 41.6 | 4342.6 | 4194.75 | 147.85 | 4346 | 5.726 | 73.98% | Module Cleaning has been done in Row-M,N,O,P,Q,R,S, Inverter No- 3 , total module cleaning-1071. |  | 1071
2019-01-25 | 910 | 1131 | 1109 | 1179 | 41.45 | 4370.45 | 4208.25 | 162.2 | 4375 | 5.856 | 72.82% | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 , total module cleaning -1092.Grid Failure From-11:35 to 11:40 and 12:24 to 12:33 & 14:46 to 14:52 & 17:31 to 17:35. |  | 1092
2019-01-26 | 956 | 1187 | 1144 | 1210 | 43.54 | 4540.54 | 4366.5 | 174.04 | 4544 | 5.775 | 76.69% | Grid Failure From-16:09 to 16:14, Module Cleaning has been done in Row-F,G,H, Inverter No-1 , total module cleaning-630. |  | 630
2019-01-27 | 978 | 1204 | 1164 | 1240 | 43.45 | 4629.45 | 4464 | 165.45 | 4633 | 5.712 | 79.05%
2019-01-28 | 939 | 1153 | 1109 | 1169 | 42.47 | 4412.47 | 4251.75 | 160.72 | 4416 | 6.152 | 69.96% | Grid Failure From-9:49 to 10:18, Module Cleaning has been done in Row-A,B,C,D,E & A,B,C,D, Inverter No-1 & 4 , total module cleaning-915. |  | 915
2019-01-29 | 1000 | 1221 | 1179 | 1245 | 43.67 | 4688.67 | 4517.25 | 171.42 | 4690 | 6.029 | 75.82% | Module Cleaning has been done in Row-,E,F,G,H,I,J, Inverter No- 4 , total module cleaning-1134. |  | 1134
2019-01-30 | 972 | 1193 | 1155 | 1275 | 43.88 | 4638.88 | 4485 | 153.88 | 4642 | 6.157 | 73.48% | Module Cleaning has been done in Row-K,L, &,Q,R,S,T, and Trackers, Inverter No-4 & 3 , total module cleaning-642. |  | 642
2019-01-31 | 736 | 871 | 872 | 903 | 33.14 | 3415.14 | 3274.5 | 140.64 | 3419 | 4.369 | 76.27% | Today atmosphere was cloudy ,Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 & 3, Total module cleaning-1050. |  | 1050
2019-02-01 | 898 | 1125 | 1098 | 1174 | 40.42 | 4335.42 | 4188 | 147.42 | 4340 | 5.721 | 73.94% | Grid Failure From-13:00 to 13:05,Module Cleaning has been done in Row-,H,I,J,K, Inverter No-1 & 2, Total module cleaning-1071. |  | 1071
2019-02-02 | 984 | 1216 | 1175 | 1255 | 43.29 | 4673.29 | 4500 | 173.29 | 4680 | 6.012 | 75.87% | Module Cleaning has been done in Row-,A,B,C,D,E,F,G, Inverter No-1, Total module cleaning-882. |  | 882
2019-02-03 | 837 | 1006 | 973 | 993 | 36.94 | 3845.94 | 3702.75 | 143.19 | 3850 | 5.126 | 73.2% | Grid Failure From-15:13 to 15:24.
2019-02-04 | 650 | 763 | 746 | 706 | 27.78 | 2892.78 | 2770.5 | 122.28 | 2896 | 3.963 | 71.22% | Grid Failure From-12:07 to 12:13.Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-4, Total module cleaning-990 and cloudy Day. |  | 990
2019-02-05 | 633 | 746 | 725 | 685 | 28.14 | 2817.14 | 2699.25 | 117.89 | 2821 | 3.87 | 71.05% | Module Cleaning has been done in Row-H,I,J,K, Inverter No-4, Total module cleaning-738 and cloudy Day. |  | 738
2019-02-06 | 803 | 972 | 938 | 1033 | 34.47 | 3780.47 | 3637.5 | 142.97 | 3784 | 5.41 | 68.17% | Grid Failure From- 13:10 to 13:42.Today we are using new 220 Nos cable tie, change and replace old Crack Cable tie .No Module Cleaning due to water are not available in tank.( Water Bor are under maintenance At. PDPU).
2019-02-07 | 938 | 1143 | 1114 | 1235 | 42.88 | 4472.88 | 4308 | 164.88 | 4476 | 5.879 | 74.21% | Module Cleaning has been done in Row-N,O,P,Q,R,S,T, and L ,Trackers. Inverter No-3 & 4 , total module cleaning-1026.Grid Failure From-12:50 to 12:57 |  | 1026
2019-02-08 | 934 | 1136 | 1139 | 1200 | 42.68 | 4451.68 | 4290 | 161.68 | 4370 | 5.842 | 72.91%
2019-02-09 | 989 | 1233 | 1214 | 1285 | 45.13 | 4766.13 | 4595.25 | 170.88 | 4770 | 6.299 | 73.81% | Module Cleaning has been done in Row-J,K,L,M. Inverter No-2 & 3 , total module cleaning-1071. |  | 1071
2019-02-10 | 927 | 1192 | 1155 | 1220 | 43.42 | 4537.42 | 4375.5 | 161.92 | 4541 | 6.291 | 70.35% | Grid Failure From- 15:43 to 15:46 and 15:51 to 16:40.
2019-02-11 | 978 | 1238 | 1179 | 1250 | 44.11 | 4689.11 | 4513.5 | 175.61 | 4695 | 6.065 | 75.45% | Module Cleaning has been done in Row-D,E,F,G,H,I. Inverter No-1 & 2 , total module cleaning-1176. |  | 1176
2019-02-12 | 944 | 1159 | 1104 | 1104 | 40.4 | 4351.4 | 4194.75 | 156.65 | 4355 | 5.936 | 71.51% | Module Cleaning has been done in Row-A,B,C & A,B,C,D,E. Inverter No-1 & 4 , total module cleaning-804. |  | 804
2019-02-13 | 752 | 887 | 857 | 907 | 32.45 | 3435.45 | 3304.5 | 130.95 | 3440 | 4.83 | 69.42% | Grid Failure From- 11:20 to 11:28 and 12:03 to 16:10. Module Cleaning has been done in Row-F,G,H,I,J,K. Inverter No-4 , total module cleaning-1134. |  | 1134
2019-02-14 | 848 | 1030 | 1003 | 1078 | 34.83 | 3993.83 | 3847.5 | 146.33 | 3997 | 5.327 | 73.13% | Grid Failure From- 16:55 to 17:42.Module Cleaning has been done in Row-O,P,Q,R,S,T & L,Tracker. Inverter No-3 & 4 , total module cleaning-727. |  | 727
2019-02-15 | 876 | 1057 | 1058 | 1099 | 38.73 | 4128.73 | 3985.5 | 143.23 | 4132 | 5.458 | 73.79% | Grid Failure From- 11:05 to 11:12.Module Cleaning has been done in Row-K,L,M,N,O. Inverter No-2 & 3 , total module cleaning-1076. |  | 1076
2019-02-16 | 1012 | 1278 | 1245 | 1321 | 43.6 | 4899.6 | 4722 | 177.6 | 4903 | 6.262 | 76.31% | Module Cleaning has been done in Row-F,G,H,I,J. Inverter No-1 & 2 , total module cleaning-1197. |  | 1197
2019-02-17 | 995 | 1238 | 1200 | 1275 | 43.07 | 4751.07 | 4590 | 161.07 | 4755 | 6.176 | 75.04%
2019-02-18 | 894 | 1079 | 1048 | 1084 | 39.32 | 4144.32 | 3998.25 | 146.07 | 4149 | 5.618 | 71.98% | Grid Failure From- 11:53 to 13:59.Module Cleaning has been done in Row-A,B,C,D,E & A,B,C,D,E. Inverter No-1 & 4 , total module cleaning-1077. |  | 1077
2019-02-19 | 949 | 1165 | 1134 | 1179 | 40.69 | 4467.69 | 4299.75 | 167.94 | 4471 | 5.917 | 73.65% | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " DC GND FLT (108)" ,Reset manually Inverter started 8:45..Module Cleaning has been done in Row-F,G,H,I,J Inverter No-4 , total module cleaning-972. |  | 972
2019-02-20 | 961 | 1164 | 1134 | 1260 | 42.31 | 4561.31 | 4372.5 | 188.81 | 4565 | 6.196 | 71.81% | Grid Failure From- 09:42 to 09:56.Module Cleaning has been done in Row-K,L, & O,P,Q,R,S,T, & Trackers. Inverter No-3 & 4, total module cleaning-978. |  | 978
2019-02-21 | 984 | 1199 | 1210 | 1331 | 42.43 | 4766.43 | 4631.25 | 135.18 | 4770 | 6.166 | 75.4% | Module Cleaning has been done in Row-L,M,N. Inverter No- 2 & 3 ,total module cleaning-714. |  | 714
2019-02-22 | 927 | 1159 | 1134 | 1219 | 41.46 | 4480.46 | 4320.75 | 159.71 | 4484 | 5.832 | 74.94% | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " DC GND FLT (108)" ,Reset manually Inverter started 8:40.Module Cleaning has been done in Row-H,I,J,K .Inverter No-1 & 2 , total module cleaning-1071. |  | 1071
2019-02-23 | 707 | 825 | 806 | 842 | 29.9 | 3209.9 | 3086.25 | 123.65 | 3213 | 3.92 | 79.89% | Grid Failure From- 11:53 to 13:59.Module Cleaning has been done in Row-A,B,C,D,E & A. Inverter No-1 & 4 , total module cleaning-954.Today Cloudy day. |  | 954
2019-02-24 | 955 | 1171 | 1129 | 1225 | 40.49 | 4520.49 | 4364.25 | 156.24 | 4524 | 5.97 | 73.86%
2019-02-25 | 1012 | 1238 | 1205 | 1245 | 43.13 | 4743.13 | 4575.75 | 167.38 | 4747 | 6.37 | 72.63% | Module Cleaning has been done in Row-B,C,D,E,F,G,H. Inverter No-4 , total module cleaning-1116.
2019-02-26 | 752 | 904 | 882 | 983 | 34.79 | 3555.79 | 3424.5 | 131.29 | 3560 | 5.289 | 65.6% | Grid Failure From- 10:40 to 11:28 & 16:55 to 17:45. Module Cleaning has been done in Row-I,J,K,L and Tracker. Inverter No- 4 , total module cleaning-726.Today Cloudy day, & Today has been replaced sillicagel in main transformer (1250kva) |  | 726
2019-02-27 | 887 | 1069 | 1053 | 1139 | 37.23 | 4185.23 | 4021.5 | 163.73 | 4189 | 5.486 | 74.42% | Grid Failure From- 12:45 to 12:50 & 15:34 to 15:39. .Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3, total module cleaning-630. |  | 630
2019-02-28 | 1064 | 1306 | 1321 | 1431 | 46.59 | 5168.59 | 4997.25 | 171.34 | 5175 | 6.588 | 76.56% | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2 & 3, total module cleaning-987.Today Transformer-2 (300 KVA) Primary Maintenance Done. |  | 977
2019-03-01 | 1005 | 1278 | 1240 | 1351 | 43.74 | 4917.74 | 4748.25 | 169.49 | 4921 | 5.999 | 79.95% | Module Cleaning has been done in Row-G,H,I,J, Inverter No-1 and 2, total module cleaning-1008.Today evening time (13:18 to 13:32)short circuit in H pole (11KV side)by monkey fall in line .so VCB are trip, measuring P.T Fuses are blown off in R,Y,B. |  | 1008
2019-03-02 | 854 | 1040 | 1013 | 1084 | 33.72 | 4024.72 | 3883.5 | 141.22 | 4028 | 5.276 | 74.41% | Module Cleaning has been done in Row-A,B,C,D,E,F& A,B,C .Inverter No-1 & 4 , total module cleaning-960.Today Cloudy day. |  | 960
2019-03-03 | 702 | 819 | 801 | 872 | 29.14 | 3223.14 | 3094.5 | 128.64 | 3227 | 4.152 | 75.75% | Today Cloudy day.Grid Failure From- 15:16 to 15:18.
2019-03-04 | 1028 | 1255 | 1220 | 1325 | 42.65 | 4870.65 | 4699.5 | 171.15 | 4874 | 6.234 | 76.2% | Grid Failure From- 7:16 to 7:21.
2019-03-05 | 989 | 1205 | 1174 | 1185 | 42.06 | 4595.06 | 4437 | 158.06 | 4601 | 6.125 | 73.21% | Grid Failure From- 10:56 to 11:03. Module Cleaning has been done in Row-,D,E,F,G,H,I, Inverter No- 4 , total module cleaning-1098.Today Cloudy day, & Today has been replaced sillicagel in transformer No-2 (300kva). |  | 1098
2019-03-06 | 1024 | 1255 | 1220 | 1376 | 43.24 | 4918.24 | 4748.25 | 169.99 | 4879 | 6.461 | 73.6% | Grid Failure From- 09:42 to 09:56.Module Cleaning has been done in Row-J,K,L, & Q,R,S,T, & Trackers. Inverter No-3 & 4, total module cleaning-822. |  | 822
2019-03-07 | 1007 | 1232 | 1235 | 1376 | 32.29 | 4882.29 | 4719.75 | 162.54 | 4886 | 6.4 | 74.41% | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 , total module cleaning-798.Today has been replaced sillicagel in transformer No-3 & 4 (300kva). |  | 798
2019-03-08 | 972 | 1222 | 1215 | 1320 | 42.7 | 4771.7 | 4606.5 | 165.2 | 4775 | 6.025 | 77.24% | Module Cleaning has been done in Row-H,I,J,K,L.Inverter No-1 & 2 , total module cleaning-1323. |  | 1323
2019-03-09 | 1029 | 1277 | 1245 | 1356 | 43.78 | 4950.78 | 4794 | 156.78 | 4955 | 6.437 | 75.03% | Module Cleaning has been done in Row-A,B,C,D,E,F,G& A,B,.Inverter No-1 & 4 , total module cleaning-1044.Today Cloudy day. |  | 1044
2019-03-10 | 995 | 1215 | 1179 | 1285 | 42.07 | 4716.07 | 4549.5 | 166.57 | 4720 | 6.274 | 73.32% | No Module cleaning.
2019-03-11 | 1062 | 1306 | 1275 | 1351 | 45 | 5039 | 4872 | 167 | 5045 | 6.67 | 73.72% | Module Cleaning has been done in Row-,C,D,E,F,G. Inverter No- 4, total module cleaning-828. |  | 828
2019-03-12 | 1063 | 1307 | 1265 | 1396 | 45 | 5076 | 4893 | 183 | 5082 | 6.641 | 74.59% | Module Cleaning has been done in Row-,H,I,J,K,L, & Trackers. Inverter No- 4, total module cleaning-924. |  | 924
2019-03-13 | 645 | 745 | 746 | 802 | 19 | 2957 | 2841 | 116 | 2958 | 3.796 | 75.95% | Module Cleaning has been done in Row-,N,O,P,Q,R,S,T. Inverter No- 3, total module cleaning-840. |  | 840
2019-03-14 | 983 | 905 | 1281 | 1411 | 43.5 | 4623.5 | 4418.25 | 205.25 | 4630 | 6.646 | 67.9% | Today Inverter No-2 ABB 250KW Auto off 12:54, Due to Err Grid mom Fault (8185) Reset The Err Inverter started 14:45. & Module Cleaning has been done in Row-,J,K,L,M. Inverter No- 3, total module cleaning-1071. Grid Failure From-16:20 to 18:02. |  | 1071
2019-03-15 | 1029 | 1284 | 1250 | 1351 | 43.69 | 4957.69 | 4770.75 | 186.94 | 4961 | 6.345 | 76.21% | Module Cleaning has been done in Row-D,E,F,G,H,I.Inverter No-1 & 2 , total module cleaning-1176. |  | 1176
2019-03-16 | 984 | 1187 | 1154 | 1234 | 40.87 | 4599.87 | 4447.5 | 152.37 | 4603 | 5.969 | 75.16% | Today replaced UPS Battery 1 Nos. due to negative terminal are linkage in battery by Change Exide Industries Ltd.Grid Failure From 16:45 to 16:48.Module Cleaning has been done in Row-A,B,C & A,B,C,D,E,.Inverter No-1 & 4 , total module cleaning-771. |  | 771
2019-03-17 | 1006 | 1237 | 1199 | 1316 | 42.14 | 4800.14 | 4644.75 | 155.39 | 4805 | 6.424 | 72.9%
2019-03-18 | 1041 | 1273 | 1235 | 1361 | 43.04 | 4953.04 | 4770.75 | 182.29 | 4958 | 6.596 | 73.26% | No Module cleaning due to water pipe crack in pdpu campus side.
2019-03-19 | 1000 | 1227 | 1195 | 1310 | 41.49 | 4773.49 | 4623.75 | 149.74 | 4777 | 6.491 | 71.73% | No Module cleaning due to water pipe crack in pdpu campus.Grid Failure From- 08:20 to 08:28.
2019-03-20 | 1040 | 1272 | 1240 | 1361 | 42.77 | 4955.77 | 4779.75 | 176.02 | 4959 | 6.524 | 74.09% | Module Cleaning has been done in Row-F,G. Inverter No- 3, total module cleaning-396. |  | 396
2019-03-21 | 1018 | 1255 | 1219 | 1306 | 42.2 | 4840.2 | 4672.5 | 167.7 | 4845 | 6.609 | 71.45%
2019-03-22 | 995 | 1209 | 1180 | 1310 | 41.27 | 4735.27 | 4575 | 160.27 | 4739 | 6.409 | 72.07% | Today Morning time short circuit (7:53 to 7:57) in H Pole by pigeon Fall in line ,Grid failure from 7:53 to 7:57.Module Cleaning has been done in Row-,H,I,J,K,L, &S ,T , Trackers. Inverter No- 4 & 3, total module cleaning-1010. |  | 1010
2019-03-23 | 967 | 1170 | 1170 | 1305 | 41.87 | 4653.87 | 4497.75 | 156.12 | 4657 | 6.256 | 72.55% | Module Cleaning has been done in Row-O,P,Q,R Inverter No- 3, total module cleaning-546. |  | 546
2019-03-24 | 972 | 1188 | 1190 | 1346 | 42.04 | 4738.04 | 4580.25 | 157.79 | 4742 | 6.374 | 72.51%
2019-03-25 | 933 | 1136 | 1159 | 1285 | 39.09 | 4552.09 | 4406.25 | 145.84 | 4555 | 6.002 | 73.97% | Module Cleaning has been done in Row-J,K,L,M,N, Inverter No-2 & 3, total module cleaning-1137. |  | 1137
2019-03-26 | 989 | 1159 | 1220 | 1336 | 43.5 | 4747.5 | 4593.75 | 153.75 | 4750 | 6.455 | 71.72% | Today Afternoon time 13:40 Inverter No: 2 fault of " DC BRK TRIP (8188)",So safemaster relay (Emergency relay) by-pass to inverter after manually started 14:10. Module Cleaning has been done in Row-E,F,G,H,I,J, Inverter No-1 & 2, total module cleaning-1194. |  | 1194
2019-03-27 | 1001 | 1239 | 1204 | 1291 | 42 | 4777 | 4602.75 | 174.25 | 4781 | 6.556 | 71.08% | Module Cleaning has been done in Row-A,B,C,D & A,B,C,D,E.Inverter No-1 & 4 , total module cleaning-1044.Today Cloudy day. |  | 930
2019-03-28 | 967 | 1198 | 1160 | 1295 | 40.92 | 4660.92 | 4511.25 | 149.67 | 4664 | 6.49 | 70.04% | Today Replaced The D.C.12 Amp Fuse Link of The String-07++tive in AJB-100 of The Inverter-4 during The Period of 9:30 To 9:35.Grid Failure from : 10:18 to 10:21 and 18:19 to 18:28.Module Cleaning has been done in Row-F,G,H,I,J. Inverter No-4, total module cleaning-972. |  | 972
2019-03-29 | 995 | 1233 | 1204 | 1391 | 42.79 | 4865.79 | 4709.25 | 156.54 | 4869 | 6.313 | 75.17% | Module Cleaning has been done in Row-K,L, &P,Q,R,S ,T , Trackers. Inverter No- 4 & 3, total module cleaning-789 |  | 789
2019-03-30 | 995 | 1232 | 1235 | 1386 | 42.58 | 4890.58 | 4720.5 | 170.08 | 4895 | 6.535 | 73.01% | Module Cleaning has been done in Row-K,L,M,N,O Inverter No-2 & 3, total module cleaning-1176. |  | 1176
2019-03-31 | 967 | 1221 | 1205 | 1336 | 41.97 | 4770.97 | 4611 | 159.97 | 4774 | 6.481 | 71.79%
2019-04-01 | 927 | 1176 | 1149 | 1270 | 40.91 | 4562.91 | 4404.75 | 158.16 | 4566 | 6.209 | 71.67% | Module Cleaning has been done in Row-H,I,J, Inverter No-1 & 2, total module cleaning-798. |  | 798
2019-04-02 | 977 | 1209 | 1174 | 1300 | 40.64 | 4700.64 | 4545 | 155.64 | 4704 | 6.486 | 70.69% | Module Cleaning has been done in Row-C,D,E,F,G, Inverter No-1 total module cleaning-777.Grid Failure From-14:03 to 14:08. |  | 777
2019-04-03 | 990 | 1205 | 1164 | 1265 | 40.95 | 4664.95 | 4515 | 149.95 | 4668 | 6.431 | 70.75% | Module Cleaning has been done in Row-A,B & A,B,C,D,E,F, Inverter No-1 & 4 total module cleaning-897. |  | 897
2019-04-04 | 984 | 1204 | 1165 | 1341 | 40 | 4734 | 4581 | 153 | 4738 | 6.536 | 70.65% | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-4 total module cleaning-936.Grid Failure From-16:23 to 16:30. |  | 936
2019-04-05 | 972 | 1153 | 1139 | 1341 | 41.14 | 4646.14 | 4494.75 | 151.39 | 4650 | 6.121 | 74.04% | Module Cleaning has been done in Row- L, &N,O,P,Q,R,S ,T , Trackers. Inverter No- 4 & 3, total module cleaning-1026 |  | 1026
2019-04-06 | 989 | 1216 | 1220 | 1371 | 42.16 | 4838.16 | 4683.75 | 154.41 | 4800 | 6.403 | 73.07% | Module Cleaning has been done in Row-J,K,L,M Inverter No-3, total module cleaning-871. |  | 871
2019-04-07 | 962 | 1198 | 1189 | 1345 | 40.5 | 4734.5 | 4587.75 | 146.75 | 4738 | 6.397 | 72.19% | Grid Failure From- 17:15 to 17:30.
2019-04-08 | 995 | 1255 | 1225 | 1401 | 41.82 | 4917.82 | 4752.75 | 165.07 | 4921 | 6.52 | 73.56% | Module Cleaning has been done in Row-G,H,I,J Inverter No-1 & 2, total module cleaning-914. |  | 914
2019-04-09 | 1034 | 1261 | 1225 | 1356 | 41.06 | 4917.06 | 4755 | 162.06 | 4921 | 6.626 | 72.39% | Grid Failure From-08:24 to 8:34.Module Cleaning has been done in Row-A,B,C,D,E,F,& A,B,C,D. Inverter No-4 total module cleaning-1104. |  | 1104
2019-04-10 | 1012 | 1233 | 1204 | 1336 | 40.27 | 4825.27 | 4671 | 154.27 | 4830 | 6.616 | 71.15% | Module Cleaning has been done in Row-E,F,G,H,I. Inverter No-4, total module cleaning-954. |  | 954
2019-04-11 | 1012 | 1232 | 1205 | 1376 | 39.32 | 4864.32 | 4695 | 169.32 | 4868 | 6.551 | 72.43% | Module Cleaning has been done in Row-J,K,L, & P,Q,R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-969. |  | 969
2019-04-12 | 978 | 1199 | 1210 | 1386 | 40.61 | 4813.61 | 4664.25 | 149.36 | 4815 | 6.475 | 72.48% | Today Replaced The D.C.12 Amp Fuse Link of The String-03--tive in AJB-102 of The Inverter-4 during The Period of 10:10 To 10:15.Module Cleaning has been done in Row-K,L,M,N,O, Inverter No-2 & 3, total module cleaning-1103. |  | 1103
2019-04-13 | 950 | 1215 | 1189 | 1346 | 40.59 | 4740.59 | 4585.5 | 155.09 | 4744 | 6.352 | 72.79% | Module Cleaning has been done in Row-H,I,J Inverter No-1 & 2, total module cleaning-798. |  | 798
2019-04-14 | 921 | 1142 | 1119 | 1250 | 37.99 | 4469.99 | 4320 | 149.99 | 4473 | 6.005 | 72.6%
2019-04-15 | 849 | 1006 | 988 | 1094 | 36 | 3973 | 3816.75 | 156.25 | 3975 | 5.224 | 74.16% | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A,B,C,D. Inverter No-1 & 4 , total module cleaning-1314.Today Cloudy Day. |  | 1314
2019-04-16 | 667 | 780 | 766 | 816 | 27.52 | 3056.52 | 2940 | 116.52 | 3060 | 4.124 | 72.32% | Grid Failure From- 15:57 to 16:35 and 16:53 to 17:50 , Today Module clean by rain.
2019-04-17 | 876 | 1194 | 1179 | 1285 | 39.61 | 4573.61 | 4413.75 | 159.86 | 4577 | 6.443 | 69.24% | Today Morning time Inverter No: 1 are not wake up due to fault of " DC BRK TRIP (8188)" inverter after manually started 9:10.Module Cleaning has been done in Row-A,B,C,D,E,F,G,H. Inverter No- 4 , total module cleaning-1188.Today Cloudy Day., Grid Failure From- 14:15 to 14:32 and 16:52 to 17:56. |  | 1188
2019-04-18 | 1046 | 1277 | 1266 | 1442 | 42.04 | 5073.04 | 4899 | 174.04 | 5077 | 6.713 | 73.71% | Module Cleaning has been done in Row-I,J,K,L, & Q,R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-1020. |  | 1020
2019-04-19 | 1051 | 1295 | 1290 | 1482 | 42.31 | 5160.31 | 4990.5 | 169.81 | 5164 | 6.84 | 73.58% | Module Cleaning has been done in Row-K,L,M,N,O,P,Inverter No- 2 & 3, total module cleaning-1323. |  | 1323
2019-04-20 | 995 | 1261 | 1235 | 1406 | 40.52 | 4937.52 | 4767 | 170.52 | 4941 | 6.697 | 71.91% | Module Cleaning has been done in Row-F,G,H,I,J,Inverter No- 1 & 2, total module cleaning-1108.Grid Failure From- 17:23 to 17:32 |  | 1108
2019-04-21 | 1018 | 1260 | 1235 | 1396 | 41.27 | 4950.27 | 4788.75 | 161.52 | 4954 | 6.673 | 72.36%
2019-04-22 | 1017 | 1249 | 1219 | 1381 | 40.4 | 4906.4 | 4752 | 154.4 | 4910 | 6.828 | 70.09% | Grid Failure From-16:37 to 16:43.Module Cleaning has been done in Row-A,B,C,D,E,& A,B,C,D,E. Inverter No-1 & 4 total module cleaning-1077. |  | 1077
2019-04-23 | 990 | 1210 | 1185 | 1341 | 39.72 | 4765.72 | 4615.5 | 150.22 | 4770 | 6.629 | 70.13% | Module Cleaning has been done in Row-F,G,H,Inverter No-4 , total module cleaning-594. |  | 594
2019-04-24 | 989 | 1204 | 1179 | 1361 | 39.21 | 4772.21 | 4616.25 | 155.96 | 4775 | 6.523 | 71.35% | Module Cleaning has been done in Row-I,J,K,L, & Q,R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-1020. |  | 1020
2019-04-25 | 950 | 1148 | 1159 | 1330 | 38.28 | 4625.28 | 4478.25 | 147.03 | 4530 | 6.211 | 71.09% | Grid Failure From-12:42 to 12:48.Module Cleaning has been done in Row-,L,M,N,O,P. Inverter No-2 & 3, Total module cleaning-1050. |  | 1050
2019-04-26 | 949 | 1181 | 1180 | 1341 | 38.92 | 4689.92 | 4524.75 | 165.17 | 4673 | 6.279 | 72.54% | Module Cleaning has been done in Row-H,I,J,K, Inverter No- 1 & 2, total module cleaning-1071. |  | 1071
2019-04-27 | 1024 | 1267 | 1235 | 1421 | 40.91 | 4987.91 | 4816.5 | 171.41 | 4991 | 6.741 | 72.16% | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A,B,C. Inverter No-1 & 4 , total module cleaning-1170. |  | 1170
2019-04-28 | 1046 | 1283 | 1255 | 1437 | 40.92 | 5061.92 | 4912.5 | 149.42 | 5065 | 6.91 | 71.44%
2019-04-29 | 1006 | 1250 | 1224 | 1325 | 40.16 | 4845.16 | 4701.75 | 143.41 | 4850 | 6.785 | 69.67% | Module Cleaning has been done in Row-D,E,F,G,H. Inverter No- 4 , total module cleaning-900. |  | 900
2019-04-30 | 989 | 1221 | 1195 | 1396 | 39.38 | 4840.38 | 4668 | 172.38 | 4844 | 6.735 | 70.1% | Grid Failure From-7:32 to 7:40.Module Cleaning has been done in Row-I,J,K,L, & R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-898. |  | 898
2019-05-01 | 927 | 1125 | 1109 | 1250 | 36.95 | 4447.95 | 4299.75 | 148.2 | 4451 | 6.171 | 70.3% | Grid Failure From-15:24 to 15:28.
2019-05-02 | 934 | 1130 | 1119 | 1311 | 37.89 | 4531.89 | 4380 | 151.89 | 4535 | 6.262 | 70.59% | Grid Failure From-8:20 to 8:29.
2019-05-03 | 768 | 922 | 912 | 1063 | 32.09 | 3697.09 | 3578.25 | 118.84 | 3701 | 6.105 | 59.09% | Grid Failure From-10:08 to 11:28 and 16:26 to 16:35.
2019-05-04 | 905 | 1097 | 1084 | 1271 | 36.6 | 4393.6 | 4250.25 | 143.35 | 4397 | 6.037 | 70.99% | Grid Failure From-17:34 to 17:37.
2019-04-05 | 921 | 1102 | 1093 | 1275 | 36.77 | 4427.77 | 4286.25 | 141.52 | 4431 | 6.125 | 70.51%
2019-05-06 | 927 | 1137 | 1119 | 1305 | 37.53 | 4525.53 | 4378.5 | 147.03 | 4529 | 6.319 | 69.86%
2019-05-07 | 945 | 1142 | 1140 | 1331 | 37.75 | 4595.75 | 4443.75 | 152 | 4599 | 6.424 | 69.78% | Today has been done Air filter clean of all inverter.(Cabinet door Filter)
2019-05-08 | 876 | 1068 | 1058 | 1240 | 34.21 | 4276.21 | 4176 | 100.21 | 4280 | 6.493 | 64.25% | Grid Failure From-17:34 to 17:37 & 12:11 to 12:26 and 17:08 to 17:42.
2019-05-09 | 910 | 1097 | 1084 | 1275 | 36 | 4402 | 4261.5 | 140.5 | 4406 | 6.07 | 70.75% | Today Cloudy day & Grid Failure From-8:37 to 8:45.
2019-05-10 | 729 | 882 | 877 | 952 | 29.21 | 3469.21 | 3342.75 | 126.46 | 3473 | 6.336 | 53.42% | Grid Failure From-10:04 to 11:54 and 14:42 to 14:47.
2019-05-11 | 877 | 1063 | 1053 | 1266 | 34.47 | 4293.47 | 4148.25 | 145.22 | 4297 | 6.046 | 69.27% | Grid Failure From-16:28 to 16:58.
2019-05-12 | 882 | 1057 | 1053 | 1245 | 34.4 | 4271.4 | 4135.5 | 135.9 | 4275 | 5.955 | 69.97%
2019-05-13 | 915 | 1102 | 1094 | 1300 | 35.62 | 4446.62 | 4329.75 | 116.87 | 4450 | 6.365 | 68.14%
2019-05-14 | 899 | 1086 | 1079 | 1265 | 35.11 | 4364.11 | 4212 | 152.11 | 4370 | 6.283 | 67.79%
2019-05-15 | 899 | 1091 | 1083 | 1290 | 34.74 | 4397.74 | 4237.5 | 160.24 | 4401 | 6.307 | 68.01%
2019-05-16 | 893 | 1074 | 1064 | 1255 | 34.35 | 4320.35 | 4182.75 | 137.6 | 4325 | 6.235 | 67.61%
2019-05-17 | 843 | 1001 | 998 | 1185 | 32.07 | 4059.07 | 3918.75 | 140.32 | 4063 | 5.798 | 68.3% | Today Cloudy weather
2019-05-18 | 871 | 1051 | 1043 | 1219 | 33.41 | 4217.41 | 4079.25 | 138.16 | 4221 | 6.096 | 67.49%
2019-05-19 | 847 | 1029 | 1023 | 1185 | 31.68 | 4115.68 | 3977.25 | 138.43 | 4119 | 6.04 | 66.47% | Grid Failure From-06:45 to 06:56 and 17:28 to 17:36 & 17:43 to 17:48.
2019-05-20 | 865 | 1051 | 1084 | 1225 | 32.53 | 4257.53 | 4106.25 | 151.28 | 4261 | 6.276 | 66.17%
2019-05-21 | 871 | 1063 | 1134 | 1240 | 32.73 | 4340.73 | 4203.75 | 136.98 | 4344 | 6.267 | 67.56%
2019-05-22 | 882 | 1091 | 1169 | 1245 | 32.32 | 4419.32 | 4272 | 147.32 | 4423 | 6.412 | 67.23%
2019-05-23 | 706 | 928 | 948 | 1003 | 27.64 | 3612.64 | 3485.25 | 127.39 | 3616 | 6.158 | 57.23% | Grid Failure From-07:54 to 09:58 and 10:04 to 10:11.
2019-05-24 | 888 | 1141 | 1144 | 1199 | 31.92 | 4403.92 | 4263 | 140.92 | 4408 | 6.176 | 69.56%
2019-05-25 | 910 | 1109 | 1104 | 1159 | 30.9 | 4312.9 | 4178.25 | 134.65 | 4316 | 6.204 | 67.81%
2019-05-26 | 752 | 893 | 897 | 928 | 29.92 | 3499.92 | 3366 | 133.92 | 3503 | 6.062 | 56.32% | Grid Failure From-10:46 to 12:05.
2019-05-27 | 899 | 1091 | 1079 | 1129 | 30.21 | 4228.21 | 4098.75 | 129.46 | 4232 | 6.336 | 65.1% | Grid Failure From-06:00 to 06:35 and 13:44 to 13:54.
2019-05-28 | 911 | 1091 | 1083 | 1129 | 30.22 | 4244.22 | 4107 | 137.22 | 4249 | 6.303 | 65.7% | Grid Failure From-10:46 to 10:54.
2019-05-29 | 915 | 1108 | 1094 | 1144 | 30.19 | 4291.19 | 4150.5 | 140.69 | 4295 | 6.287 | 66.58%
2019-05-30 | 922 | 1114 | 1104 | 1154 | 30.33 | 4324.33 | 4180.5 | 143.83 | 4328 | 6.358 | 66.35%
2019-05-31 | 887 | 1080 | 1068 | 1109 | 29.33 | 4173.33 | 4041 | 132.33 | 4178 | 6.163 | 66.07% | Today Replaced The D.C.12 Amp Fuse Link of The String-03 ++tive in AJB-114 of The Inverter-3 during The Period of 7:35 To 7:40
2019-06-01 | 826 | 983 | 978 | 1003 | 26.83 | 3816.83 | 3689.25 | 127.58 | 3820 | 6.007 | 61.98% | Grid Failure From-10:02 to 10:21 and 16:13 to 16:39.
2019-06-02 | 893 | 1069 | 1059 | 1079 | 28.67 | 4128.67 | 3992.25 | 136.42 | 4132 | 6.18 | 65.17%
2019-06-03 | 887 | 1057 | 1048 | 1063 | 28.54 | 4083.54 | 3951.75 | 131.79 | 4087 | 6.119 | 65.1%
2019-06-04 | 871 | 1040 | 1038 | 1038 | 30 | 4017 | 3890.25 | 126.75 | 4010 | 6.047 | 64.63%
2019-06-05 | 876 | 1046 | 1039 | 1049 | 27.82 | 4037.82 | 3903.75 | 134.07 | 4041 | 6.011 | 65.52%
2019-06-06 | 831 | 995 | 988 | 988 | 27.3 | 3829.3 | 3702.75 | 126.55 | 3833 | 5.977 | 62.5% | comissioning and installation of 110V DC FCBC Charger and Battery set (UPST 110V AH Battery) by Servilink engineer Pvt.Ltd ,Grid Failure From-14:42 to 15:00.
2019-06-07 | 837 | 1001 | 998 | 1003 | 27.08 | 3866.08 | 3744 | 122.08 | 3870 | 5.936 | 63.54% | Today PM of Y Phase cable changed and replaced new phase in VCB side on 'H' pole and Measuring P.T. (3 Nos) Fuses are changed and replaced new R,Y,B Line fuse in V.C.B.(12KV HCR fuses)
2019-06-08 | 825 | 995 | 992 | 998 | 27.14 | 3837.14 | 3720.75 | 116.39 | 3840 | 6.065 | 61.71% | Grid Failure From-11:36 to 11:40.
2019-06-09 | 826 | 1000 | 993 | 988 | 26.97 | 3833.97 | 3709.5 | 124.47 | 3837 | 6.044 | 61.88%
2019-06-10 | 808 | 956 | 953 | 942 | 26.19 | 3685.19 | 3560.25 | 124.94 | 3689 | 5.773 | 62.28%
2019-06-11 | 786 | 938 | 932 | 917 | 25.76 | 3598.76 | 3483.75 | 115.01 | 3602 | 5.709 | 61.49%
2019-06-12 | 673 | 792 | 787 | 797 | 22.18 | 3071.18 | 2961.75 | 109.43 | 3075 | 4.824 | 62.13% | Today Cloudy weather.Today Replaced The D.C.12 Amp Fuse Link of The String-02 --tive in AJB-102 of The Inverter-4 during The Period of 16:00 To 16:05.
2019-06-13 | 430 | 774 | 771 | 907 | 26.67 | 2908.67 | 2794.5 | 114.17 | 2912 | 4.315 | 65.78% | Grid Failure From-10:07 to 10:20 and 13:58 to 14:02. Today Inverter No.1 Auto trip from 10:48 to 14:00.Today Eight Module remove from Inverter No.1 due to testing purpose for sending Laboratory (REC Singapore (4module) and HI-PYSIX LAB (4 module) .Today Cloudy weather.
2019-06-14 | 752 | 888 | 887 | 1023 | 29.19 | 3579.19 | 3459 | 120.19 | 3583 | 4.722 | 73.96% | Today Cloudy weather. Today four module send to HI-PYSIX LAB (PUNE) by OM Mover and Packages courier pvt ltd. Sending REC Module Details (1.JMPD100903452, 2.JMPD100904140,3.JMPD100903872,4.JMPD100902565)for module degradation testing purpose.
2019-06-15 | 475 | 548 | 549 | 605 | 16.58 | 2193.58 | 2098.5 | 95.08 | 2197 | 2.89 | 74.09% | Module clean by Rain & cloudy day & Grid Failure From-12:19 to 12:43 and 16:35 to 16:39.
2019-06-16 | 745 | 899 | 897 | 973 | 25.13 | 3539.13 | 3415.5 | 123.63 | 3543 | 4.799 | 71.96% | Module clean by Rain & cloudy day.Grid Failure From-7:51 to 8:00 and 14:26 to 14:35.
2019-06-17 | 741 | 893 | 882 | 1043 | 27.93 | 3586.93 | 3429.75 | 157.18 | 3590 | 5.134 | 68.15% | Module clean by Rain & cloudy day.Grid Failure From-12:56 to 13:15 and 15:22 to 16:00 & 17:21 to 17:30.
2019-06-18 | 317 | 362 | 373 | 383 | 10.95 | 1445.95 | 1374.75 | 71.2 | 1449 | 1.985 | 71.15% | Module clean by Rain & full cloudy day.Grid Failure From-10:56 to 11:42 and 12:18 to 12:23 & 13:32 to 13:40.
2019-06-19 | 735 | 871 | 862 | 1008 | 27.99 | 3503.99 | 3360 | 143.99 | 3505 | 4.647 | 73.51% | cloudy day.Grid Failure From-16:07 to 16:12.
2019-06-20 | 690 | 808 | 802 | 928 | 26.16 | 3254.16 | 3147 | 107.16 | 3258 | 4.262 | 74.51% | cloudy day.
2019-06-21 | 830 | 1006 | 998 | 1179 | 34.57 | 4047.57 | 3927 | 120.57 | 4051 | 5.486 | 71.97% | cloudy day.
2019-06-22 | 854 | 1029 | 1023 | 1210 | 33.75 | 4149.75 | 4012.5 | 137.25 | 4150 | 5.697 | 71% | cloudy day.
2019-06-23 | 888 | 1075 | 1068 | 1250 | 35.03 | 4316.03 | 4181.25 | 134.78 | 4320 | 5.837 | 72.14%
2019-06-24 | 475 | 542 | 545 | 604 | 18.28 | 2184.28 | 2118 | 66.28 | 2188 | 2.876 | 74.15% | cloudy day.Grid Failure From-10:59 to 11:03 and 13:25 to 13:46 & 17:54 to 17:57.
2019-06-25 | 695 | 826 | 821 | 963 | 28.75 | 3333.75 | 3217.5 | 116.25 | 3337 | 4.383 | 74.21% | cloudy day.Grid Failure From-08:06 to 08:15 and 08:58 to 9:03.
2019-06-26 | 780 | 927 | 923 | 1069 | 31.07 | 3730.07 | 3595.5 | 134.57 | 3734 | 4.914 | 74.06% | cloudy day.
2019-06-27 | 848 | 1029 | 1013 | 1194 | 34.75 | 4118.75 | 3986.25 | 132.5 | 4122 | 5.557 | 72.3% | cloudy day.
2019-06-28 | 600 | 701 | 700 | 791 | 24.32 | 2816.32 | 2714.25 | 102.07 | 2820 | 3.542 | 77.6% | Today Replaced The D.C.12 Amp Fuse Link of The String-08 --tive in AJB-111 of The Inverter-2 during The Period of 18:35 To 18:40.Cloudy day.
2019-06-29 | 763 | 916 | 918 | 1074 | 31.89 | 3702.89 | 3575.25 | 127.64 | 3706 | 4.886 | 73.93%
2019-06-30 | 865 | 1040 | 1023 | 1205 | 35.11 | 4168.11 | 4026.75 | 141.36 | 4172 | 5.612 | 72.46% | cloudy day.Grid Failure From-7:02 to 7:10.
2019-07-01 | 786 | 944 | 937 | 1083 | 32.19 | 3782.19 | 3672 | 110.19 | 3786 | 5.113 | 72.17% | Today has been replaced silica gel in Transformer No-4.(300KVA), & cloudy day.
2019-07-02 | 842 | 1018 | 1013 | 1180 | 32.3 | 4085.3 | 3949.5 | 135.8 | 4089 | 5.486 | 72.65% | Today has been done all Air filter cleaned of all inverter (Cabinet door),cloudy day.
2019-07-03 | 859 | 1040 | 1034 | 1199 | 33.93 | 4165.93 | 4026 | 139.93 | 4169 | 5.602 | 72.53% | Today visual Inspection all Array and checked connection of MC4 connectors and rebuild all cables throught Tie cable.cloudy day.Grid Failure From-17:25 to 18:25 and 18:29 to 18:32.cloudy day.
2019-07-04 | 311 | 351 | 353 | 283 | 10.04 | 1308.04 | 1214.25 | 93.79 | 1312 | 1.654 | 77.31% | Today we are found one module crack in visual inspection,Inveter no -3(Delsolar) module no-122,String line-B,ROW-M,serial no-PB10B048480207.full cloudy day.
2019-07-05 | 469 | 553 | 554 | 620 | 19.39 | 2215.39 | 2102.25 | 113.14 | 2219 | 2.839 | 76.18% | full cloudy day.
2019-07-06 | 549 | 628 | 630 | 710 | 20.96 | 2537.96 | 2454.75 | 83.21 | 2540 | 3.201 | 77.34% | full cloudy day.
2019-07-07 | 627 | 724 | 726 | 822 | 23.44 | 2922.44 | 2817.75 | 104.69 | 2925 | 3.673 | 77.62% | full cloudy day.
2019-07-08 | 690 | 819 | 811 | 927 | 27.04 | 3274.04 | 3146.25 | 127.79 | 3278 | 4.326 | 73.85% | cloudy day.Grid Failure From-08:44 to 08:52 and 09:06 to 09:11 & 13:16 to 13:20.
2019-07-09 | 701 | 826 | 827 | 943 | 27.37 | 3324.37 | 3204.75 | 119.62 | 3328 | 4.451 | 72.87% | Today has been done of Preventive Maintenance in Main Transformer (1250KVA) & Transformer-4 (315 KVA).(Oil Leakege of LV side,bushing gasket and tightness of cables connection and bus-bar supporter).full cloudy day.
2019-07-10 | 763 | 916 | 912 | 1043 | 29.6 | 3663.6 | 3546 | 117.6 | 3667 | 4.913 | 72.75% | Today we are found oil leakage in visual inspection on Transformer No-4 in LV side so after again (315 KVA) Preventive Maintenance has been done.
2019-07-11 | 656 | 769 | 766 | 867 | 26.6 | 3084.6 | 2959 | 125.6 | 3085 | 4.112 | 73.12% | full cloudy day.
2019-07-12 | 797 | 955 | 953 | 1109 | 32.86 | 3846.86 | 3721.5 | 125.36 | 3850 | 5.257 | 71.38% | cloudy day.
2019-07-13 | 781 | 939 | 932 | 1078 | 31.58 | 3761.58 | 3628.5 | 133.08 | 3765 | 5.128 | 71.56% | cloudy day.Grid Failure From-7:41 to 7:52.
2019-07-14 | 717 | 847 | 847 | 978 | 29.11 | 3418.11 | 3297.75 | 120.36 | 3422 | 4.658 | 71.6% | cloudy day.
2019-07-15 | 667 | 798 | 791 | 897 | 28.17 | 3181.17 | 3068.25 | 112.92 | 3185 | 4.369 | 71.05% | Today Replaced The D.C.12 Amp Fuse Link of The String-07--tive in AJB-117 of The Inverter-3 during The Period of 9:30 to 9:35.cloudy day.
2019-07-16 | 696 | 831 | 832 | 958 | 28.5 | 3345.5 | 3222.75 | 122.75 | 3349 | 4.719 | 69.17% | cloudy day.Grid Failure From-07:40 to 07:47 and 14:25 to 14:32 & 16:07 to 16:22.
2019-07-17 | 119 | 146 | 146 | 146 | 4.39 | 561.39 | 499.5 | 61.89 | 565 | 2.234 | 24.65% | Today P.M of A.C.D.B. Panel.(change the all neutral cables in neutral busbar to MCB becuase the cables are light sparks and corrosion in lugs.)
2019-07-18 | 802 | 973 | 968 | 1104 | 31.98 | 3878.98 | 3742.5 | 136.48 | 3882 | 5.264 | 71.88% | cloudy day.
2019-07-19 | 815 | 990 | 988 | 1119 | 33.38 | 3945.38 | 3812.25 | 133.13 | 3949 | 5.357 | 71.85% | cloudy day.
2019-07-20 | 757 | 921 | 912 | 1028 | 27.9 | 3645.9 | 3522.75 | 123.15 | 3649 | 5.156 | 68.98% | cloudy day.Grid Failure From-06:42 to 06:51 and 08:39 to 08:50 & 11:40 to 11:43 &15:06 to 15:08.Today we are replaced the del-solar module, Module No- 122 (ROW NO-M) and B Line , replace old Module no: PB10B048480207 to New Module no: PB10B068470359 in inverter No-3.
2019-07-21 | 718 | 853 | 852 | 983 | 28.4 | 3434.4 | 3315 | 119.4 | 3438 | 4.544 | 73.74% | Full cloudy day.
2019-07-22 | 876 | 1097 | 1078 | 1295 | 35.84 | 4381.84 | 4224.75 | 157.09 | 4385 | 6.001 | 71.22% | Full cloudy day.
2019-07-23 | 820 | 1001 | 993 | 1180 | 32.33 | 4026.33 | 3891.75 | 134.58 | 4030 | 5.564 | 70.59% | Today the courier company (DHL) has taken four module and send to REC GROUP Singapore.REC Module serial number Details : 1.JMPD100901615,2.JMPD100903322,3.JMPD100903188,4.JMPD100904208. Full cloudy day.
2019-07-24 | 684 | 831 | 822 | 922 | 25.48 | 3284.48 | 3170.25 | 114.23 | 3288 | 4.406 | 72.73% | Today Replaced The D.C.12 Amp Fuse Link of The String-07 ++tive in AJB-116 of The Inverter-3 during The Period of 16:05 to16:15.full cloudy day.Grid Failure From-17:04 to 17:11.
2019-07-25 | 582 | 690 | 680 | 756 | 22.25 | 2730.25 | 2617.5 | 112.75 | 2734 | 3.54 | 75.27% | Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 34 (Row No-A) and A Line , old Module no:NPC10BY1130364 to replace the New Module no: NPC10BY1113790. 2)Module No-5 (Row No-D) and A Line , old Module no:NPC10BY1109685 to replace the New Module no: NPC10BY1113791.3)Module No-63 (Row No-D) and B Line , old Module no:NPC10BY108902 to replace the New Module no: NPC10BY1113792.Full cloudy day
2019-07-26 | 486 | 565 | 570 | 640 | 18.6 | 2279.6 | 2185.5 | 94.1 | 2283 | 2.897 | 76.81% | Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 80 (Row No-E) and A Line , old Module no:NPC10BY112719 to replace the New Module no: NPC10BY1113797. 2)Module No-20 (Row No-E) and B Line , old Module no:NPC10BY1114038 to replace the New Module no: NPC10BY1113789.3)Module No-84 (Row No-F) and B Line , old Module no:NPC10BY1111596 to replace the New Module no: NPC10BY1113793.full cloudy day.Grid Failure From16:34 to 16:40.
2019-07-27 | 504 | 582 | 580 | 661 | 18.85 | 2345.85 | 2235 | 110.85 | 2349 | 2.912 | 78.62% | Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 28 (Row No-G) and B Line , old Module no:NPC10BY1116216 to replace the New Module no: NPC10BY1113798. 2)Module No-16 (Row No-H) and B Line , old Module no:NPC10BY1107955 to replace the New Module no: NPC10BY1113794.3)Module No-57 (Row No-J) and B Line , old Module no:NPC10BY1130398 to replace the New Module no: NPC10BY1113795.4)Module No-14 (Row No-K) and A Line , old Module no:NPC10BY1108020 to replace the New Module no: NPC10BY1113796.Full cloudy day
2019-07-28 | 390 | 452 | 453 | 504 | 13.56 | 1812.56 | 1729.5 | 83.06 | 1837 | 2.167 | 82.62% | Full cloudy day.Grid Failure From-7:21 to 7:23.
2019-07-29 | 379 | 430 | 434 | 483 | 13.45 | 1739.45 | 1629.75 | 109.7 | 1733 | 2.213 | 76.33% | Today we are replaced the NexPower Module in Inverter No-4. 1)Module No- 27 (Row No-I) and B Line , old Module no:NPC10BY1130264 to replace the New Module no: NPC10BY1113801. 2)Module No-82 (Row No-I) and B Line , old Module no:NPC10BY1112987 to replace the New Module no: NPC10BY1113799.3)Module No-92 (Row No-I) and B Line , old Module no:NPC10BY1112888 to replace the New Module no: NPC10BY1113800.Full cloudy day
2019-07-30 | 299 | 345 | 347 | 379 | 10.36 | 1380.36 | 1290 | 90.36 | 1389 | 1.655 | 81.8% | Full cloudy day
2019-07-31 | 300 | 339 | 343 | 377 | 10.57 | 1369.57 | 1275 | 94.57 | 1435 | 1.699 | 82.32% | Full cloudy day
2019-08-01 | 198 | 227 | 232 | 253 | 6.48 | 916.48 | 808 | 108.48 | 920 | 1.127 | 79.56% | Full cloudy day
2019-08-02 | 508 | 605 | 600 | 690 | 19.2 | 2422.2 | 2305 | 117.2 | 2426 | 3.147 | 75.14% | Full cloudy day
2019-08-03 | 289 | 333 | 338 | 388 | 10.11 | 1358.11 | 1276 | 82.11 | 1362 | 1.667 | 79.63% | Today Replaced The D.C.12 Amp Fuse Link of The String-09 --tive in AJB-101 of The Inverter-4 during The Period of 10:10 To 10:20 (E-Line).cloudy day
2019-08-04 | 373 | 447 | 448 | 509 | 13.82 | 1790.82 | 1695 | 95.82 | 1794 | 2.2249 | 78.59% | cloudy day
2019-08-05 | 588 | 689 | 696 | 807 | 23.81 | 2803.81 | 2692.5 | 111.31 | 2807 | 3.581 | 76.4% | cloudy day
2019-08-06 | 656 | 780 | 796 | 932 | 26.83 | 3190.83 | 3077.25 | 113.58 | 3194 | 4.228 | 73.63% | cloudy day
2019-08-07 | 345 | 312 | 413 | 469 | 12.94 | 1551.94 | 1462 | 89.94 | 1555 | 2.108 | 71.9% | cloudy day
2019-08-08 | 310 | 299 | 419 | 479 | 14.15 | 1521.15 | 1437 | 84.15 | 1525 | 2.139 | 69.49% | Today we are found the cable fault (Under ground) in AJB No. 8,9 and 10 of the Inverter No.2. So we are bypass MCB and AJB No 8 and 10 in Inverter,Because the MCB No 8 and 10 are Auto trip.cloudy day
2019-08-09 | 176 | 158 | 201 | 226 | 5.89 | 766.89 | 675 | 91.89 | 770 | 1.018 | 73.72% | cloudy day
2019-08-10 | 130 | 125 | 162 | 177 | 4.77 | 598.77 | 519 | 79.77 | 603 | 1.128 | 52.1% | cloudy day.Grid Failure From-10:30 to 10:36 and 12:12 to 12:51 &13:52 to 13:58 and 14:38 to 16:20.
2019-08-11 | 509 | 497 | 589 | 721 | 21.57 | 2337.57 | 2226 | 111.57 | 2341 | 3.158 | 72.25% | cloudy day
2019-08-12 | 667 | 667 | 797 | 957 | 28.01 | 3116.01 | 2986.5 | 129.51 | 3120 | 4.475 | 67.95% | Today has been done all air filter paper clean in all inverter. cloudy day.Grid Failure From-15:22 to 15:27 and 16:32 to 16:34.
2019-08-13 | 757 | 769 | 902 | 1089 | 32.46 | 3549.46 | 3412.5 | 136.96 | 3553 | 5.05 | 68.57% | cloudy day
2019-08-14 | 537 | 531 | 635 | 761 | 23.06 | 2487.06 | 2400 | 87.06 | 2492 | 3.395 | 71.54% | Full Cloudy day,Today evening time Mr.Alpha Engineers team came to cable fault finding ,found the 5 cable fault. 3 cable fault in cable peet & 2 cable fault found near 5meter cable peet. cable fault in AJB No108 ++tive and --tive, AJB No:109 --tive and AJB No:110 ++tive and --tive are faulty cable.
2019-08-15 | 243 | 136 | 287 | 323 | 8.05 | 997.05 | 892.5 | 104.55 | 1001 | 1.413 | 69.05% | cloudy day
2019-08-16 | 419 | 237 | 474 | 569 | 15.92 | 1714.92 | 1601.25 | 113.67 | 1718 | 2.416 | 69.31% | Today Replaced The D.C.12 Amp Fuse Link of The String-02 --tive in AJB-100 of The Inverter-4 during The Period of 9:35 to 09:40. (B-Line).full cloudy day
2019-08-17 | 497 | 227 | 575 | 686 | 19.59 | 2004.59 | 1926.75 | 77.84 | 2008 | 3.061 | 63.94% | full cloudy day
2019-08-18 | 769 | 305 | 927 | 1149 | 34.95 | 3184.95 | 3066 | 118.95 | 3188 | 5.172 | 60.08% | Today we are change the Contactor in AJB No.9 (MJB No-2) Positive Cable of the Inverter No-2.Cloudy Day
2019-08-19 | 673 | 272 | 887 | 1063 | 30.8 | 2925.8 | 2791.5 | 134.3 | 2929 | 4.874 | 58.57%
2019-08-20 | 769 | 627 | 907 | 1104 | 32.57 | 3439.57 | 3321 | 118.57 | 3443 | 5.079 | 66.07%
2019-08-21 | 853 | 707 | 1023 | 1260 | 37.1 | 3880.1 | 3750 | 130.1 | 3884 | 5.799 | 65.28% | Today we are found the cable fault in string no 3 (--tive cable) and 1( --tive cable) of the AJB No : 116 and 117. those cable are Crack and burn in cable duct. We are link the joint MC4 connector between cable.
2019-08-22 | 837 | 695 | 1044 | 1255 | 37.34 | 3868.34 | 3723 | 145.34 | 3872 | 5.743 | 65.71%
2019-08-23 | 859 | 718 | 1073 | 1265 | 38.03 | 3953.03 | 3822 | 131.03 | 3957 | 5.95 | 64.82%
2019-08-24 | 865 | 718 | 1079 | 1270 | 37.6 | 3969.6 | 3843 | 126.6 | 3973 | 5.968 | 64.88%
2019-08-25 | 628 | 509 | 761 | 872 | 26.61 | 2796.61 | 2684.25 | 112.36 | 2800 | 4.216 | 64.73% | cloudy day.Grid Failure From-15:29 to 15:40 to 16:29 and 16:31 to 16:59 &17:06.
2019-08-26 | 107 | 102 | 181 | 192 | 5.84 | 587.84 | 524.25 | 63.59 | 636 | 0.959 | 64.64% | Full cloudy day.Grid Failure From-13:38 to 13:40 to 14:27 and 14:35 to 16:55 &16:58.Today P.M of Inverter No-1 has been done during 14:10 to 16:20.
2019-08-27 | 379 | 294 | 444 | 509 | 14.14 | 1640.14 | 1513 | 127.14 | 1644 | 2.294 | 69.85%
2019-08-28 | 424 | 333 | 514 | 585 | 16.94 | 1872.94 | 1795.5 | 77.44 | 1876 | 2.823 | 64.77% | cloudy day.Grid Failure From-12:12 to 12:55 and 14:04 to 14:06...
2019-08-29 | 644 | 536 | 791 | 932 | 25.05 | 2928.05 | 2814 | 114.05 | 2932 | 4.073 | 70.16%
2019-08-30 | 775 | 639 | 958 | 1124 | 31.85 | 3527.85 | 3408.7 | 119.15 | 3531 | 5.247 | 65.59%
2019-08-31 | 447 | 351 | 530 | 604 | 21.35 | 1953.35 | 2049 | -95.65 | 1957 | 2.752 | 69.31% | Scada net connection failure .cloudy day.Grid Failure From-14:07 to 14:19.
2019-09-01 | 837 | 695 | 1043 | 1200 | 43.48 | 3818.48 | 3702.75 | 115.73 | 3823 | 5.809 | 64.14%
2019-09-02 | 604 | 497 | 746 | 877 | 30.56 | 2754.56 | 2636.25 | 118.31 | 2758 | 4.057 | 66.26% | cloudy day.Grid Failure From-08:27 to 08:35.
2019-09-03 | 617 | 498 | 756 | 872 | 30.091 | 2773.091 | 2670.75 | 102.341 | 2774 | 4.077 | 66.32% | cloudy day.
2019-09-04 | 517 | 458 | 690 | 806 | 27.445 | 2498.445 | 2459.25 | 39.195 | 2502 | 3.776 | 64.58% | cloudy day.
2019-09-05 | 322 | 260 | 404 | 469 | 16.06 | 1471.06 | 1434 | 37.06 | 1475 | 3.689 |  | Today morning time we are found VCB and Master relay are operated due to night time heavy rain and more time grid failure , we are cleared the fault and manually plant started on 12:30.
2019-09-06 | 639 | 526 | 786 | 927 | 32.48 | 2910.48 | 2798.25 | 112.23 | 2914 | 4.408 | 64.43% | cloudy day.
2019-09-07 | 605 | 502 | 766 | 827 | 32.95 | 2732.95 | 2641.5 | 91.45 | 2736 | 4.277 | 62.35% | cloudy day.
2019-09-08 | 599 | 499 | 751 | 751 | 32.4 | 2632.4 | 2524.5 | 107.9 | 2604 | 4.798 | 52.9% | cloudy day.Grid Failure From-09:47 to 10:58.
2019-09-09 | 385 | 310 | 469 | 529 | 16.22 | 1709.22 | 1616.25 | 92.97 | 1713 | 2.463 | 67.79% | Today we are changed the SPD (--tive) in AJB-104 of The Inverter-4 during the period of 18:15 to 18:30.full cloudy day
2019-09-10 | 130 | 91 | 151 | 167 | 4.22 | 543.22 | 454.5 | 88.72 | 547 | 0.853 | 62.5% | Full cloudy day.Grid Failure From-09:21 to 10:31 and 11:51 to 11:56 & 12:08 to 12:13 and 13:01 to 13:05.
2019-09-11 | 373 | 288 | 449 | 493 | 15.18 | 1618.18 | 1530.75 | 87.43 | 1622 | 2.418 | 65.38% | Full cloudy day.Grid Failure From-07:18 to 7:25 and 09:15 to 09:23 & 09:44 to 09:56.
2019-09-12 | 299 | 226 | 352 | 389 | 11.42 | 1277.42 | 1225.5 | 51.92 | 1281 | 1.812 | 68.9% | Full Cloudy day
2019-09-13 | 147 | 102 | 172 | 186 | 4.97 | 611.97 | 523.5 | 88.47 | 615 | 0.881 | 68.04% | Full Cloudy day
2019-09-14 | 141 | 107 | 176 | 187 | 4.94 | 615.94 | 523.5 | 92.44 | 619 | 0.882 | 68.4% | Full cloudy day.Grid Failure From-11:06 to 11:08 and 13:17 to 13:19.
2019-09-15 | 362 | 283 | 439 | 504 | 15.96 | 1603.96 | 1506.75 | 97.21 | 1607 | 2.331 | 67.19% | Full Cloudy day
2019-09-16 | 684 | 565 | 851 | 993 | 37.16 | 3130.16 | 3011.25 | 118.91 | 3134 | 4.664 | 65.49%
2019-09-17 | 752 | 622 | 993 | 1103 | 39.94 | 3509.94 | 3343.5 | 166.44 | 3513 | 5.319 | 64.37%
2019-09-18 | 685 | 565 | 852 | 993 | 20.72 | 3115.72 | 3016.5 | 99.22 | 3119 | 4.148 | 73.29% | cloudy day.Grid Failure From-09:42 to 09:43 and 16:13 to 16:17.
2019-09-19 | 734 | 611 | 912 | 1074 | 41.14 | 3372.14 | 3258 | 114.14 | 3376 | 5.138 | 64.04% | cloudy day
2019-09-20 | 651 | 543 | 817 | 968 | 34.78 | 3013.78 | 2900.25 | 113.53 | 3017 | 4.581 | 64.19% | cloudy day
2019-09-21 | 582 | 475 | 720 | 836 | 29.13 | 2642.13 | 2535.75 | 106.38 | 2646 | 3.945 | 65.37% | cloudy day.Grid Failure From-15:17 to 15:19.
2019-09-22 | 452 | 367 | 555 | 656 | 22.57 | 2052.57 | 1962 | 90.57 | 2056 | 3.097 | 64.7% | cloudy day.Grid Failure From-11:36 to 11:41.
2019-09-23 | 594 | 487 | 741 | 836 | 30.08 | 2688.08 | 2572.5 | 115.58 | 2753 | 4.001 | 67.06% | cloudy day.Grid Failure From-11:36 to 11:41.
2019-09-24 | 825 | 706 | 1053 | 1275 | 49.02 | 3908.02 | 3790.5 | 117.52 | 3912 | 6.117 | 62.33%
2019-09-25 | 684 | 594 | 882 | 1059 | 39.26 | 3258.26 | 3132.75 | 125.51 | 3262 | 4.988 | 63.74% | Grid Failure From-12:47 to 12:49.
2019-09-26 | 486 | 390 | 595 | 695 | 21.58 | 2187.58 | 2087.25 | 100.33 | 2191 | 3.158 | 67.62% | Full cloudy day
2019-09-27 | 305 | 232 | 363 | 409 | 11.83 | 1320.83 | 1230.75 | 90.08 | 1324 | 1.826 | 70.67% | Full cloudy day.Grid Failure From-08:02 to 08:11.
2019-09-28 | 526 | 435 | 655 | 761 | 26.22 | 2403.22 | 2300.25 | 102.97 | 2407 | 3.539 | 66.29% | Full cloudy day
2019-09-29 | 436 | 345 | 529 | 600 | 18.01 | 1928.01 | 1827 | 101.01 | 1926 | 2.538 | 73.96% | Full cloudy day.Grid Failure From-13:38 to 13:45.
2019-09-30 | 192 | 147 | 232 | 272 | 8 | 851 | 759 | 92 | 854 | 1.232 | 67.56% | Full cloudy day.Grid Failure From-14:30 to 14:42.
2019-10-01 | 633 | 531 | 801 | 942 | 33.88 | 2940.88 | 2828.25 | 112.63 | 2944 | 4.547 | 63.11% | Today Replaced The D.C.12 Amp Fuse Link of The String-09 --tive in AJB-105 of The Inverter-1 during The Period of 8:40 to 08:47. (H-Line).Grid Failure From-14:54 to 15:05.full cloudy day
2019-10-02 | 774 | 656 | 983 | 1149 | 44.6 | 3606.6 | 3483.75 | 122.85 | 3610 | 5.482 | 64.18% | Cloudy day
2019-10-03 | 255 | 582 | 872 | 1008 | 33.88 | 2750.88 | 2685.75 | 65.13 | 2755 | 4.922 | 54.55% | Today Inverter No 1 under breakdown during 11:00 (3-10-19) to 19:00 (4-10-19) due to Install MIRU-01 in Inverter by ABB. Cloudy day.Grid Failure From-16:45 to 16:54 and 17:16 to 17:18.
2019-10-04 | 329 | 520 | 1064 | 1230 | 47.41 | 3190.41 | 3090.25 | 100.16 | 3196 | 6.071 | 51.31% | Today Inverter No 2 under breakdown during 14:02 (4-10-19) to 19:00(4-10-19) due to Install MIRU-01 in Inverter by ABB. Grid Failure From-9:44 to 9:49.
2019-10-05 | 766 | 661 | 993 | 1180 | 45.88 | 3645.88 | 3515.25 | 130.63 | 3651 | 5.655 | 62.93% | Today we are Install new Cooling fan in inverter no-1.
2019-10-06 | 751 | 670 | 1003 | 1149 | 46.17 | 3619.17 | 3491.25 | 127.92 | 3625 | 5.737 | 61.59%
2019-10-07 | 766 | 671 | 993 | 1134 | 42.97 | 3606.97 | 3471 | 135.97 | 3610 | 5.794 | 60.73% | Grid Failure From-12:33 to 12:45 and 13:48 to 13:53.
2019-10-08 | 811 | 730 | 1093 | 1255 | 50.7 | 3939.7 | 3814.5 | 125.2 | 3944 | 6.107 | 62.95%
2019-10-09 | 736 | 655 | 968 | 1114 | 43.87 | 3516.87 | 3388.5 | 128.37 | 3520 | 5.566 | 61.64%
2019-10-10 | 792 | 661 | 1048 | 1209 | 48.81 | 3758.81 | 3629.25 | 129.56 | 3762 | 5.946 | 61.67% | Today morning time inverter No-1 ABB 250KW are not wakeup due to Err DC Bracker Trip(8188), Reset the Err manually than inverter started-8:49.
2019-10-11 | 856 | 781 | 1150 | 1336 | 55.04 | 4178.04 | 4042.5 | 135.54 | 4182 | 6.627 | 61.51% | Full cloudy day
2019-10-12 | 867 | 776 | 1154 | 1326 | 54.87 | 4177.87 | 4043.25 | 134.62 | 4181 | 6.505 | 62.64% | Full cloudy day
2019-10-13 | 827 | 741 | 1094 | 1255 | 53.66 | 3970.66 | 3837.75 | 132.91 | 3975 | 6.238 | 62.11%
2019-10-14 | 796 | 711 | 1033 | 1214 | 48.24 | 3802.24 | 3670.5 | 131.74 | 3806 | 6.112 | 60.69% | Today we are found the cable fault in string no 1(--tive cable) of the AJB No:117 of inverter no-3. those cable are crack and burn in cable duct. We are link and joint new MC4 connector.
2019-10-15 | 782 | 700 | 1038 | 1205 | 47.97 | 3772.97 | 3651.75 | 121.22 | 3776 | 6.013 | 61.21% | Today has been done all Air filter paper cleaned of all inverter and inverter no-2 only one change sqaure filter paper.(Cabinet door Filter).Grid Failure From-16:07 to 16:13.
2019-10-16 | 776 | 686 | 1008 | 1154 | 47.82 | 3671.82 | 3467.25 | 204.57 | 3675 | 5.848 | 61.25%
2019-10-17 | 751 | 650 | 978 | 1129 | 46.17 | 3554.17 | 3504.75 | 49.42 | 3560 | 5.701 | 60.86% | Today we are found oil leakage in visual inspection on Transformer No-4 in LV side, (315 KVA) Preventive Maintenance is not done oil leakge continue in B-Phase...,Module Cleaning has been done in Row- A,B,C. Inverter No-4 , total module cleaning-288. |  | 288
2019-10-18 | 736 | 645 | 953 | 1104 | 44.06 | 3482.06 | 3360 | 122.06 | 3486 | 5.585 | 60.84% | Today we are found oil leakage in visual inspection on Transformer No-4 in LV side, (315 KVA) Preventive Maintenance is not done oil leakge continue in B-Phase..,Module Cleaning has been done in Row- A,D,E. Inverter No-4 , total module cleaning-275. |  | 275
2019-10-19 | 741 | 640 | 942 | 1074 | 43.33 | 3440.33 | 3310.5 | 129.83 | 3444 | 5.507 | 60.95% | Full cloudy day
2019-10-20 | 690 | 590 | 872 | 993 | 40.21 | 3185.21 | 3066 | 119.21 | 3189 | 5.113 | 60.79% | Module Cleaning has been done in Row-F,G, nverter No-4 , total module cleaning-410. |  | 410
2019-10-21 | 595 | 489 | 726 | 836 | 31.35 | 2677.35 | 2571 | 106.35 | 2681 | 4.134 | 63.21% | Full cloudy day
2019-10-22 | 549 | 549 | 685 | 802 | 31.05 | 2616.05 | 2418 | 198.05 | 2620 | 4.651 | 54.9% | Today Replaced The D.C.12 Amp Fuse Link of The String-05 ++tive in AJB-104 of The Inverter-4 during The Period of 8:30 to 08:35.Grid Failure From 10:49 to 11:47 and 16:14 to 16:22.
2019-10-23 | 101 | 80 | 121 | 136 | 13.19 | 451.19 | 372.75 | 78.44 | 455 | 5.765 | 7.692% | Grid Failure From-09:27 to 14:00. Grid failure after All Inverter not start because Inverter NO -1 and 2 error is " GRID MON FLT" and Inverter NO-3 and 4 error is " Under Votage and Over Current during 14:00 (23.10.19) to 18:00 (24.10.19) and after called ABB and came Arifbhai and resolve problem on 25.10.2019.
2019-10-24 | [5 empty] | 0 |  | 0 |  | 5.247 | 0%
2019-10-25 | 257 | 227 | 504 | 645 | 48.07 | 1681.07 | 1559.25 | 121.82 | 1685 | 5.126 | 32.04% | Yesterday night Government side 11KV line fuse failure after plant started on 12:30.
2019-10-26 | 560 | 414 | 686 | 786 | 24.21 | 2470.21 | 2356.5 | 113.71 | 2475 | 3.844 | 62.75% | Today we are changed and replaced MCB (ABB ,3-Pole and 125Amp) in AJB No: 8 of Inverter No-2 in Main Junction Box because the negative terminal by pass in MCB.Today we are Install the new DC RR Cable 70Sqmm in AJB No-8 (++tive and --tive)and 10(++tive and --tive) of Inverter No-2 due to those cable are underground fault (puncture and cut) on 8 Aug 2019
2019-10-27 | 332 | 397 | 393 | 469 | 14.03 | 1605.03 | 1509.75 | 95.28 | 1610 | 2.179 | 72.01% | full cloudy day
2019-10-28 | 469 | 590 | 585 | 700 | 20.87 | 2364.87 | 2241 | 123.87 | 2368 | 3.339 | 69.12% | full cloudy day
2019-10-29 | 494 | 620 | 604 | 741 | 21.84 | 2480.84 | 2366.25 | 114.59 | 2484 | 3.459 | 69.99% | Today Replaced the D.C.12 Amp fuse link of the string-08 --tive in AJB-110 of The Inverter-2 during the period of 7:35 to 07:40.
2019-10-30 | 796 | 1084 | 1059 | 1260 | 29.76 | 4228.76 | 4077.25 | 151.51 | 4232 | 5.638 | 73.16% | Module clean by rain
2019-10-31 | 731 | 943 | 932 | 1084 | 29.35 | 3719.35 | 3583.5 | 135.85 | 3723 | 5.281 | 68.71%
2019-11-01 | 751 | 977 | 978 | 1124 | 30.54 | 3860.54 | 3720 | 140.54 | 3864 | 5.589 | 67.38% | Grid Failure From-17:06 to 17:08.
2019-11-02 | 343 | 403 | 408 | 469 | 13.61 | 1636.61 | 1548 | 88.61 | 1640 | 2.204 | 72.52% | Today Replaced the D.C.12 Amp fuse link of the string-07 ++tive in AJB-105 of The Inverter-4 during the period of 9:30 to 09:35.Fully cloudy day.Module clean by rain.
2019-11-03 | 403 | 484 | 489 | 569 | 15.99 | 1960.99 | 1849.5 | 111.49 | 1964 | 2.559 | 74.8% | Full cloudy day
2019-11-04 | 640 | 701 | 847 | 998 | 26.64 | 3212.64 | 3099.75 | 112.89 | 3216 | 4.97 | 63.07% | Today we are Install the new DC RR Cable 70Sqmm in AJB No-106 ( --tive)and AJB No: 109(++tive and --tive) of Inverter No-2 due to those cable are underground fault (puncture and cutting) on 8 Aug 2019.Grid Failure From-10:04 to 10:21.
2019-11-05 | 666 | 852 | 857 | 988 | 28.19 | 3391.19 | 3262.5 | 128.69 | 3395 | 4.953 | 66.81% | Grid Failure From-06:40 to 08:00.
2019-11-06 | 654 | 836 | 842 | 958 | 27.35 | 3317.35 | 3189 | 128.35 | 3321 | 4.794 | 67.52%
2019-11-07 | 459 | 565 | 569 | 645 | 17.42 | 2255.42 | 2147.25 | 108.17 | 2259 | 3.143 | 70.05% | Today breakdown of Inverter No-4 during 17:08 18:51 due to Oil leakege in B Phase has been completed by Alpha Engineers Company Pvt.ltd and Change O-ring in B-phase.Grid Failure From-15:42 to 15:46.
2019-11-08 | 600 | 756 | 751 | 887 | 24.94 | 3018.94 | 2879.25 | 139.69 | 3022 | 4.294 | 68.59% | Grid Failure From-08:03 to 08:32 and 08:53 to 08:58 and 17:05 to 17:40..
2019-11-09 | 716 | 922 | 923 | 1053 | 29.98 | 3643.98 | 3525 | 118.98 | 3647 | 5.262 | 67.55% | Grid Failure From-13:15 to 13:20.
2019-11-10 | 665 | 852 | 851 | 963 | 28.28 | 3359.28 | 3242.25 | 117.03 | 3363 | 4.889 | 67.04%
2019-11-11 | 595 | 756 | 761 | 832 | 25.84 | 2969.84 | 2856 | 113.84 | 2973 | 4.415 | 65.63% | Grid Failure From-07:07 to 07:57 and 16:51 to 16:58.
2019-11-12 | 645 | 852 | 847 | 968 | 28.38 | 3340.38 | 3206.25 | 134.13 | 3344 | 4.961 | 65.7%
2019-11-13 | 661 | 846 | 847 | 972 | 27.84 | 3353.84 | 3222.75 | 131.09 | 3357 | 4.949 | 66.11% | Grid Failure From-08:15 to 08:26 and 16:40 to 16:47.
2019-11-14 | 670 | 857 | 852 | 958 | 28.07 | 3365.07 | 3228 | 137.07 | 3369 | 4.938 | 66.5%
2019-11-15 | 131 | 147 | 147 | 156 | 5.61 | 586.61 | 518.25 | 68.36 | 590 | 3.915 | 14.69% | Today Replaced the D.C.12 Amp fuse link of the string-06 --tive in AJB-102 of The Inverter-4 during the period of 8:40 to 08:45.Grid Failure From-09:23 to 015:42.Today we are send submersible pump to service and repaire at Umiya Electrical,Gandhinagar.MOdule cleaning not done 5-11-19 to 17-11-19 due to motor not start.
2019-11-16 | 534 | 710 | 695 | 817 | 27.89 | 2783.89 | 2653.5 | 130.39 | 2787 | 4.861 | 55.88% | Grid Failure From-07:07 to 09:58 and 16:49 to 16:54.
2019-11-17 | 645 | 827 | 837 | 892 | 27.5 | 3228.5 | 3073.5 | 155 | 3232 | 4.746 | 66.37% | Module Cleaning has been done in Row-A,B,C, Inverter No-4 , total module cleaning-288. |  | 288
2019-11-18 | 615 | 776 | 796 | 867 | 26.65 | 3080.65 | 2937 | 143.65 | 3084 | 4.486 | 67.01%
2019-11-19 | 676 | 888 | 903 | 993 | 29.55 | 3489.55 | 3334.5 | 155.05 | 3493 | 5.17 | 65.85% | Today Replaced the D.C.12 Amp fuse link of the string-05 ++tive in AJB-105 of The Inverter-4 during the period of 9:00 to 09:05.
2019-11-20 | 614 | 795 | 811 | 897 | 25.45 | 3142.45 | 2991 | 151.45 | 3146 | 5.203 | 58.93% | Module Cleaning has been done in Row-D,E,F, Inverter No-4 , total module cleaning-504.Grid Failure From-10:37 to 10:58 and 12:50 to 13:12. |  | 504
2019-11-21 | 681 | 882 | 897 | 1033 | 28.8 | 3521.8 | 3369.75 | 152.05 | 3525 | 5.272 | 65.17% | Module Cleaning has been done in Row-G,H,I, Inverter No-4 , total module cleaning-496.Grid Failure From-08:52 to 08:58. |  | 496
2019-11-22 | 635 | 832 | 837 | 988 | 27.04 | 3319.04 | 3162 | 157.04 | 3323 | 5.134 | 63.09% | Module Cleaning has been done in Row-I,J, Inverter No-4 , total module cleaning-280.Grid Failure From-08:30 to 08:52 and 09:43 to 09:51. |  | 280
2019-11-23 | 595 | 751 | 771 | 907 | 25.88 | 3049.88 | 2910.75 | 139.13 | 3053 | 4.421 | 67.31% | Grid Failure From-08:54 to 08:57.
2019-11-24 | 615 | 792 | 802 | 953 | 27.44 | 3189.44 | 3048 | 141.44 | 3193 | 4.7 | 66.21% | Module Cleaning has been done in Row K,L & S,T and Tracker ,Inverter No-4 and 3 , total module cleaning-432. |  | 432
2019-11-25 | 589 | 750 | 776 | 887 | 26.31 | 3028.31 | 2892.75 | 135.56 | 3032 | 4.449 | 66.42% | Module Cleaning has been done in Row Q,R,S,T ,Inverter No-3 ,total module cleaning-294 |  | 294
2019-11-26 | 580 | 741 | 796 | 872 | 29.29 | 3018.29 | 2867.25 | 151.04 | 3022 | 4.343 | 67.82% | Module Cleaning has been done in Row N.O.P ,Inverter No-3, total module cleaning-546. |  | 546
2019-11-27 | 529 | 666 | 751 | 771 | 24.17 | 2741.17 | 2612.25 | 128.92 | 2745 | 3.985 | 67.14% | Module Cleaning has been done in Row-L, M, Inverter No-2 and 3, total module cleaning-504. |  | 504
2019-11-28 | 544 | 731 | 776 | 817 | 24.98 | 2892.98 | 2755.5 | 137.48 | 2896 | 4.106 | 68.74% | Module Cleaning has been done in Row-J,K , Inverter No-2 , total module cleaning-567. |  | 567
2019-11-29 | 550 | 761 | 787 | 806 | 25.25 | 2929.25 | 2794.5 | 134.75 | 2933 | 4.15 | 68.88% | Module Cleaning has been done in Row-I , Inverter No-2 , total module cleaning-273. |  | 273
2019-11-30 | 590 | 826 | 846 | 887 | 13.19 | 3162.19 | 3036.75 | 125.44 | 3164 | 4.498 | 68.56% | Today we are install new Tracker controller with display unit in Tracker no-6.Now Tracker no-5 and 6 working condition.Grid Failure From-16:17 to 16:24.
2019-12-01 | 625 | 857 | 867 | 928 | 43.61 | 3320.61 | 3170.25 | 150.36 | 3324 | 4.668 | 69.4% | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-1 , total module cleaning-903. |  | 903
2019-12-02 | 650 | 827 | 837 | 871 | 41.17 | 3226.17 | 3070.5 | 155.67 | 3230 | 4.594 | 68.53% | Module Cleaning has been done in Row-A,B,C and A,B,C, Inverter No-1 & 4 , total module cleaning-498. |  | 498
2019-12-03 | 655 | 836 | 852 | 903 | 42.77 | 3288.77 | 3141 | 147.77 | 3292 | 4.668 | 68.74% | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-4 , total module cleaning-900. |  | 900
2019-12-04 | 600 | 757 | 766 | 841 | 36.93 | 3000.93 | 2858.25 | 142.68 | 3004 | 4.156 | 70.45% | Module Cleaning has been done in Row-I,J,K, Inverter No-4 , total module cleaning-540. |  | 540
2019-12-05 | 534 | 670 | 690 | 777 | 32.06 | 2703.06 | 2568 | 135.06 | 2707 | 3.639 | 72.5% | Module Cleaning has been done in Row L & O,P,Q,R,S,T and Tracker ,Inverter No-4 and 3 , total module cleaning-816.Grid Failure From-15:36 to 15:41. |  | 816
2019-12-06 | 393 | 469 | 514 | 549 | 20.24 | 1945.24 | 1824 | 121.24 | 1949 | 2.485 | 76.44% | Module Cleaning has been done in Row-K,L,M,N Inverter No-2 and 3 , total module cleaning-987.Today we are change safe master relay "BD5935" in Inverter No:2 and Installed new relay by Salimbhai ABB. |  | 987
2019-12-07 | 610 | 786 | 787 | 867 | 40.48 | 3090.48 | 2964.75 | 125.73 | 3094 | 4.289 | 70.31%
2019-12-08 | 661 | 866 | 857 | 912 | 45.01 | 3341.01 | 3217.5 | 123.51 | 3350 | 4.701 | 69.46% | Module Cleaning has been done in Row-H,I,J ,Inverter No-1 and 2 , total module cleaning-798. |  | 798
2019-12-09 | 690 | 903 | 887 | 953 | 46.48 | 3479.48 | 3344.25 | 135.23 | 3483 | 4.87 | 69.71% | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A,B,C,D ,Inverter No-1 and 4 , total module cleaning-1314. |  | 1314
2019-12-10 | 705 | 918 | 902 | 998 | 48.65 | 3571.65 | 3439.5 | 132.15 | 3575 | 5.064 | 68.81% | Module Cleaning has been done in Row-E,F,G ,Inverter No-4 , total module cleaning-558. |  | 558
2019-12-11 | 706 | 927 | 907 | 1018 | 48.99 | 3606.99 | 3475.5 | 131.49 | 3610 | 5.164 | 68.14% | Module Cleaning has been done in Row-H,I,J,K,L and Tracker ,Inverter No-4 , total module cleaning-924. |  | 924
2019-12-12 | 670 | 861 | 857 | 973 | 46.26 | 3407.26 | 3274.5 | 132.76 | 3412 | 4.746 | 70.07% | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T ,Inverter No-3 , total module cleaning-1092. |  | 1092
2019-12-13 | 661 | 873 | 872 | 983 | 46.86 | 3435.86 | 3297.75 | 138.11 | 3439 | 4.751 | 70.55% | Module Cleaning has been done in Row-I,J,K,L ,Inverter No-2 , total module cleaning-969. |  | 969
2019-12-14 | 731 | 973 | 952 | 1068 | 53.99 | 3777.99 | 3642 | 135.99 | 3781 | 5.26 | 70.06% | Today we are change string cable of AJB No-07 and 10,String Number 7 in AJB No-7 and String number-1 in AJB No-10 due to Under ground fault.
2019-12-15 | 741 | 1043 | 978 | 1094 | 55.61 | 3911.61 | 3767.25 | 144.36 | 3915 | 5.304 | 71.94% | Module Cleaning has been done in Row-F,G,H ,Inverter No-1 , total module cleaning-630. |  | 630
2019-12-16 | 766 | 1058 | 998 | 1114 | 57.35 | 3993.35 | 3840.75 | 152.6 | 3997 | 5.445 | 71.55% | Module Cleaning has been done in Row-A,B,C,D,E & A ,Inverter No-1 and 4 , total module cleaning-636. |  | 636
2019-12-17 | 791 | 1099 | 1028 | 1149 | 59.52 | 4126.52 | 3972 | 154.52 | 4131 | 5.632 | 71.49% | Module Cleaning has been done in Row-B,C,D,E,F ,Inverter No-4 , total module cleaning-720.Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 64 (Row No-E) and A Line , old Module no:NPC10BY1109824 to replace the New Module no: NPC10BY1113802. |  | 720
2019-12-18 | 680 | 932 | 878 | 978 | 47.06 | 3515.06 | 3384.75 | 130.31 | 3536 | 4.765 | 72.33% | Module Cleaning has been done in Row-,G,H,I, Inverter No-4 , total module cleaning-594. & Today we are replaced new phase failure relay (S2 VMR3) in inverter No-1 ABB 250KW. & Grid Failure from-16:48 to 16:54. |  | 594
2019-12-19 | 706 | 978 | 922 | 1058 | 51.02 | 3715.02 | 3570.75 | 144.27 | 3719 | 5.099 | 71.09% | Module Cleaning has been done in Row-J,K,L & Q,R,S,T and Tracker ,Inverter No-4 and 3 , total module cleaning-822. and Grid Failure from-08:25 to 08:30. |  | 822
2019-12-20 | 691 | 953 | 912 | 1033 | 51.01 | 3640.01 | 3500.25 | 139.76 | 3645 | 4.971 | 71.47% | Module Cleaning has been done in row-L,M,N,O,P ,Inverter No-2 and 3 , total module cleaning-1050. and Grid Failure from-17:17 to 17:19. |  | 1050
2019-12-21 | 670 | 922 | 892 | 988 | 49.03 | 3521.03 | 3386.25 | 134.78 | 3525 | 4.842 | 70.96% | Today has been done all Air filter paper cleaned of all inverter (Cabinet door Filter).Grid Failure From-11:41 to 11:45 and 17:17 to 17:25.
2019-12-22 | 600 | 826 | 792 | 842 | 39.83 | 3099.83 | 2973 | 126.83 | 3104 | 3.988 | 75.86% | Module Cleaning has been done in row-I,J,K ,Inverter No-2, total module cleaning-840. |  | 840
2019-12-23 | 569 | 772 | 730 | 761 | 35.55 | 2867.55 | 2751 | 116.55 | 2868 | 3.875 | 72.14% | Module Cleaning has been done in row-H,G,F,Inverter No-1, total module cleaning-630. |  | 630
2019-12-24 | 640 | 872 | 817 | 872 | 41.99 | 3242.99 | 3117 | 125.99 | 3245 | 4.511 | 70.11% | Module Cleaning has been done in row-,A,B,C,D,E, Inverter No-1, total module cleaning-594 & Today we are replaced 2 led lamp in CRC Panel (DC110) & 1 in VCB Panel (230AC). |  | 594
2019-12-25 | 651 | 877 | 832 | 882 | 42.78 | 3284.78 | 3155 | 129.78 | 3287 | 4.56 | 70.26% | Module Cleaning has been done in row-A,B,C,D,E,F,G,Inverter No-4, total module cleaning-990. |  | 990
2019-12-26 | 695 | 972 | 887 | 1013 | 51.22 | 3618.22 | 3480 | 138.22 | 3622 | 4.815 | 73.32% | Module Cleaning has been done in row-H,I,J,K,Inverter No-4, total module cleaning-732. |  | 732
2019-12-27 | 832 | 1175 | 1083 | 1260 | 65.57 | 4415.57 | 4254.75 | 160.82 | 4418 | 6.182 | 69.65% | Module Cleaning has been done in row-L,& Q,R,S,T, & Tracker,Inverter No-4 & 3, total module cleaning-480. Today Replaced the D.C.12 Amp fuse link of the string-03 ++tive in AJB-111 of The Inverter-3 during the period of 14:30 to 14:35. |  | 480
2019-12-28 | 831 | 1164 | 1099 | 1250 | 67.57 | 4411.57 | 4245.75 | 165.82 | 4415 | 6.046 | 71.17%
2019-12-29 | 610 | 827 | 796 | 852 | 40.48 | 3125.48 | 2993.25 | 132.23 | 3129 | 4.103 | 74.33% | Module Cleaning has been done in Row-N,O,P ,Inverter No-3 , total module cleaning-546. cloudy day |  | 546
2019-12-30 | 751 | 1053 | 1013 | 1099 | 57.45 | 3973.45 | 3828 | 145.45 | 3974 | 5.503 | 70.39% | Module Cleaning has been done in Row- J,K,L,M ,Inverter No-2 and 3 , total module cleaning-925.Today Replaced the D.C.12 Amp fuse link of the string-09 ++tive in AJB-101 of The Inverter-4 during the period of 8:35 to 08:40.and replaced the connector in string-02 in AJB-113 of The Inverter-3. |  | 925
2020-12-31 | 645 | 907 | 852 | 882 | 44.45 | 3330.45 | 3238 | 92.45 | 3332 | 4.605 | 70.52% | Module Cleaning has been done in Row-G,H,I, Inverter No-1&2, total module cleaning-714. cloudy day and Grid Failure from-16:40 to 17:46. |  | 714
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!

## 2020
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2020
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
[8 empty] | Difference | Onsite Useage
PDPU
[6 empty] | Total Generation (KWH) | (ABT Meter) Aggregate Meter Reading (KWH) GRID | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | Total NO- Of Clean Modules
Inverter generation (KWH)
Date | Poly crystaline1104500527 | Polycrystaline1104500529 | 9175000042 | Thin Film Amorphous Silicon9170301408 | 2100570073/ 2100567820/ 2100567898 Concentrate Photo voltainc
2020-01-01 | 545 | 721 | 686 | 690 | 31.78 | 2673.78 | 2559 | 114.78 | 2679 | 3.556 | 73.43% | Module Cleaning has been done in Row-B,C,D,E,F, Inverter No-1, total module cleaning-624. cloudy day and Grid Failure from-14:20 to 14:24 . |  | 624
2020-01-02 | 580 | 781 | 731 | 756 | 34.56 | 2882.56 | 2748.75 | 133.81 | 2888 | 3.974 | 70.83% | Module Cleaning has been done in Row-A,& A,B,C,D,E,F,G Inverter No-1&4, total module cleaning-1032. cloudy day and Grid Failure from-15:13 to 15:15 and 15:20 to 15:25. |  | 1032
2020-01-03 | 604 | 807 | 766 | 817 | 37.06 | 3031.06 | 2903.25 | 127.81 | 3036 | 4.061 | 72.87% | Module Cleaning has been done in Row-H,I,J,K, Inverter No-4, total module cleaning-738.Today Replaced the connector of the string-01 in AJB-112 of The Inverter-3. |  | 738
2020-01-04 | 666 | 912 | 852 | 892 | 44 | 3366 | 3226.5 | 139.5 | 3371 | 4.634 | 70.9% | crack
2020-01-05 | 625 | 852 | 811 | 922 | 47.54 | 3257.54 | 3126.75 | 130.79 | 3263 | 5.407 | 58.82% | Module Cleaning has been done in Row-O,R,S,T and L and Tracker, Inverter No-3 and 4, total module cleaning-480. cloudy day and Grid Failure from-11:30 to 12:38 .Today we are replaced the connector in string-08 in AJB-111 of The Inverter-3(L-line). |  | 480
2020-01-06 | 710 | 973 | 953 | 1054 | 53.16 | 3743.16 | 3609.75 | 133.41 | 3749 | 5.167 | 70.72% | Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 and 3, total module cleaning-924. |  | 924
2020-01-07 | 524 | 700 | 695 | 731 | 33.05 | 2683.05 | 2559.75 | 123.3 | 2688 | 3.688 | 71.04% | Today came Mahindra Teqo company for On-site Testing of PV Module . Today only Flash Test Done on REC module(5+1 new module(6 Qty) and DEL Solar (5 Qty)module by REC Groups ,At- 1MW Solar Power Plant ,PDPU., Module Cleaning has been done in Row-K,L Inverter No-2 total module cleaning-399,cloudy day. |  | 399
2020-01-08 | 706 | 993 | 948 | 1028 | 51.23 | 3726.23 | 3586 | 140.23 | 3732 | 5.054 | 71.97% | Module Cleaning has been done in Row-F,G,H,I, Inverter No-1&2, total module cleaning-903. cland Grid Failure from-11:06 to 11:11 |  | 903
2020-01-09 | 837 | 1185 | 1124 | 1230 | 66.68 | 4442.68 | 4275 | 167.68 | 4448 | 5.652 | 76.7% | Today came Mahindra Teqo company for On-site Testing of PV Module . Today only EL Test Done on REC module(5+1 new module(6 Qty) and DEL Solar (5 Qty)module by REC Groups ,At- 1MW Solar Power Plant ,PDPU., Module Cleaning has been done in Row-C,D,E,Inverter No-1 total module cleaning-438. |  | 438
2020-01-10 | 685 | 973 | 897 | 972 | 54.02 | 3581.02 | 3461 | 120.02 | 3587 | 5.878 | 59.48% | Module Cleaning has been done in Row-A,B.And,A,B,C, Inverter No-1&4, total module cleaning-393,Today we are replaced the 2(32A-2P) MCB in ACDB.Grid Failure from-12:14 to 13:23.Today we are reconnect testing module (10 Module) |  | 393
2020-01-11 | 726 | 998 | 937 | 1019 | 51.28 | 3731.28 | 3582.75 | 148.53 | 3737 | 4.893 | 74.44%
2020-01-12 | 625 | 861 | 807 | 866 | 42.46 | 3201.46 | 3093.75 | 107.71 | 3207 | 4.614 | 67.74% | Module Cleaning has been done in Row-D,E,F, Inverter No-4, total module cleaning-504. Grid Failure from-11:55 to 12:07 and 12:43 to 12:46. |  | 504
2020-01-13 | 423 | 535 | 514 | 560 | 22.42 | 2054.42 | 1942.5 | 111.92 | 2059 | 2.673 | 75.08% | Today we are change ++tive string DC 6 Sqmm cable (25m) in string no-7 of AJB No: 107 in due to underground fault(Cable Puncture) and fault observed in 14 Dec 2019.Module Cleaning has been done in Row-G,H, Inverter No-4, total module cleaning-396. Grid Failure from-09:30 to 09:33. |  | 396
2020-01-14 | 762 | 1083 | 1008 | 1139 | 58.14 | 4050.14 | 3915 | 135.14 | 4056 | 5.702 | 69.33% | Grid Failure from-11:02 to 11:11.
2020-01-15 | 786 | 1104 | 1028 | 1154 | 59.49 | 4131.49 | 3975 | 156.49 | 4137 | 5.679 | 71%
2020-01-16 | 721 | 993 | 943 | 1023 | 50.88 | 3730.88 | 3582 | 148.88 | 3736 | 5.216 | 69.81% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4,and Tracker, total module cleaning-852. Grid Failure from-10:30 to 10:49. |  | 852
2020-01-17 | 625 | 847 | 816 | 852 | 40.91 | 3180.91 | 3058 | 122.91 | 3187 | 4.29 | 72.41% | Module Cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No-3, total module cleaning-840. |  | 840
2020-01-18 | 720 | 1013 | 988 | 1039 | 52.12 | 3812.12 | 3672 | 140.12 | 3818 | 5.165 | 72.05% | Module Cleaning has been done in Row-J,K,L,M, Inverter No-2 and 3, total module cleaning-1071. |  | 1071
2020-01-19 | 766 | 1098 | 1038 | 1113 | 57.5 | 4072.5 | 3927 | 145.5 | 4078 | 5.389 | 73.76% | Module Cleaning has been done in Row-E,F,G,H,I Inverter No-1 & 2, total module cleaning-1050. |  | 1050
2020-01-20 | 847 | 1210 | 1145 | 1245 | 64.89 | 4511.89 | 4345 | 166.89 | 4517 | 5.962 | 73.84% | Module Cleaning has been done in Row-A,B,C,D and A,B, Inverter No-1 & 4, total module cleaning-498. Today we are Remove 500ml Oil in all Transformer for Oil Testing Purpose. |  | 498
2020-01-21 | 812 | 1149 | 1078 | 1185 | 61.44 | 4285.44 | 4132 | 153.44 | 4291 | 5.784 | 72.31% | Module Cleaning has been done in Row-C,D,E,F. Inverter No-4 , total module cleaning-630+M228 |  | 630
2020-01-22 | 806 | 1130 | 1069 | 1179 | 59.77 | 4243.77 | 4080 | 163.77 | 4849 | 5.665 | 83.43% | Module Cleaning has been done in Row-G,H. Inverter No-4 , total module cleaning-396.today we are again remove 200 ml oil in all trasformer for oil testing peropse. |  | 396
2020-01-23 | 791 | 1109 | 1048 | 1154 | 57.96 | 4159.96 | 4017 | 142.96 | 4165 | 5.498 | 73.84% | Module Cleaning has been done in Row-S,T and I,J,K,L . Inverter No-3 and 4,and Tracker, total module cleaning-810. Grid Failure from-16:11 to 16:13. |  | 810
2020-01-24 | 832 | 1184 | 1134 | 1266 | 65.07 | 4481.07 | 4322 | 159.07 | 4487 | 5.931 | 73.74% | Module Cleaning has been done in Row-N,O,P,Q,R, Inverter No-3 total module cleaning-756
2020-01-25 | 594 | 811 | 781 | 861 | 39.89 | 3086.89 | 2964.75 | 122.14 | 3092 | 4.041 | 74.58% | Cloudy Day,Today we are install 24watt solar street light (2 Nos)in Campus Boundary of Solar plant.Grid Failure from 17:08 to 17:15.
2020-01-26 | 797 | 1114 | 1084 | 1195 | 61.03 | 4251.03 | 4087 | 164.03 | 4257 | 5.662 | 73.28%
2020-01-27 | 670 | 918 | 887 | 958 | 47.25 | 3480.25 | 3341.25 | 139 | 3486 | 4.717 | 72.03% | Module Cleaning has been done in Row-L,M, Inverter No-2,and 3 total module cleaning-504, Cloudy Day |  | 504
2020-01-28 | 685 | 947 | 907 | 998 | 49.11 | 3586.11 | 3456 | 130.11 | 3592 | 4.775 | 73.32% | Today early mornig 2:45am UGVCL staff Came and Disconnect Power Supply of 1MW Solar Power Plant and remove UGVCL energy meter and after we are taken temporary Power Suppy by Maruti Excellance and connect with ACDB.(3-Phase A.C).Module Cleaning has been done in Row-I,J,K, Inverter No-2 total module cleaning-840, Cloudy Day |  | 840
2020-01-29 | 817 | 1169 | 1094 | 1159 | 60.76 | 4299.76 | 4144 | 155.76 | 4305 | 5.789 | 72.48% | Module Cleaning has been done in Row-H,G,F,E,D,C inverter no 1 total module cleaning-1008, Cloudy Day |  | 1008
2020-01-30 | 857 | 1190 | 1114 | 1204 | 63.31 | 4428.31 | 4267 | 161.31 | 4444 | 6 | 72.19% | Module Cleaning has been done in Row-A,B & A,B,C,D,E,F,Inverter no 1&4 total module cleaning-897 |  | 897
2020-01-31 | 826 | 1154 | 1079 | 1195 | 60.51 | 4314.51 | 4191 | 123.51 | 4319 | 5.864 | 71.79% | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-4, total module cleaning-936. Grid Failure from-01:00am to 08:10am. |  | 936
2020-02-01 | 888 | 1235 | 1159 | 1316 | 65.75 | 4663.75 | 4483.5 | 180.25 | 4669 | 6.207 | 73.32%
2020-02-02 | 857 | 1189 | 1124 | 1259 | 64.43 | 4493.43 | 4341 | 152.43 | 4499 | 5.924 | 74.02% | Module Cleaning has been done in Row-O,P,Q,R,S,T & L, and Tracker, Inverter No-3&4, total module cleaning-627. |  | 627
2020-02-03 | 791 | 1099 | 1068 | 1150 | 57.44 | 4165.44 | 4016 | 149.44 | 4171 | 5.51 | 73.78% | Module Cleaning has been done in Row-K,L,M,N,O,Inverter No-2&3, total module cleaning-1103 |  | 1103
2020-02-04 | 842 | 1195 | 1149 | 1219 | 64.06 | 4469.06 | 4307.25 | 161.81 | 4475 | 5.954 | 73.25% | Module Cleaning has been done in Row-J,K,Inverter No-2, total module cleaning-367 |  | 367
2020-02-05 | 806 | 1144 | 1069 | 1145 | 60.11 | 4224.11 | 4068 | 156.11 | 4230 | 5.751 | 71.69% | Module Cleaning has been done in Row-D,E,F,G,H,I, Inverter No-1 & 2, total module cleaning-1176.Grid failure from 11:00 to 11:13. |  | 1176
2020-02-06 | 857 | 1194 | 1134 | 1209 | 61.79 | 4455.79 | 4299 | 156.79 | 4461 | 6.011 | 72.33% | Module Cleaning has been done in Row-A,B,C and A,B,C,D Inverter No-1 & 4, total module cleaning-642 |  | 642
2020-02-07 | 837 | 1155 | 1099 | 1175 | 58.68 | 4324.68 | 4173.75 | 150.93 | 4330 | 5.746 | 73.45% | Module Cleaning has been done in Row-E,F,G,H,I Inverter No-4, total module cleaning-954.Today Preventive maintenance of Inverter No-1 has been done. |  | 954
2020-02-08 | 881 | 1240 | 1169 | 1270 | 64.29 | 4624.29 | 4461 | 163.29 | 4630 | 6.171 | 73.13%
2020-02-09 | 882 | 1229 | 1165 | 1270 | 64.23 | 4610.23 | 4452 | 158.23 | 4616 | 6.155 | 73.1% | Module Cleaning has been done in Row-J,K,L, and Tracker, Inverter No-4, total module cleaning-528. |  | 528
2020-02-10 | 857 | 1195 | 1139 | 1250 | 63.19 | 4504.19 | 4343 | 161.19 | 4510 | 6.016 | 73.07% | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3, total module cleaning-630 |  | 630
2020-02-11 | 812 | 1119 | 1093 | 1174 | 57.69 | 4255.69 | 4103 | 152.69 | 4261 | 5.728 | 72.5% | Module Cleaning has been done in Row-J,K,L,M,N, Inverter No-2 & 3, total module cleaning-1281 |  | 1281
2020-02-12 | 827 | 1159 | 1104 | 1190 | 58.48 | 4338.48 | 4074.75 | 263.73 | 4344 | 5.872 | 72.1% | Module Cleaning has been done in Row-D,E,F,G,H,I, Inverter No-1 & 2, total module cleaning-1176. Grid Failure from-17:22 to 17:30. |  | 1176
2020-02-13 | 846 | 1160 | 1099 | 1184 | 57.92 | 4346.92 | 4201.5 | 145.42 | 4352 | 5.895 | 71.95% | Module Cleaning has been done in Row-A,B,C and A,B,C,D,E, Inverter No-1 & 4, total module cleaning-804.Grid Failure IACE from -08:38 to 09:00. |  | 804
2020-02-14 | 852 | 1168 | 1114 | 1210 | 58.97 | 4402.97 | 4251.75 | 151.22 | 4408 | 5.976 | 71.89% | Module Cleaning has been done in Row-F,G, Inverter No 4, total module cleaning-396.Grid Failure from-16:26 to 16:31. Today we are install new communication card in string inveter no-07(2100570073) for tracker. |  | 396
2020-02-15 | 842 | 1150 | 1099 | 1210 | 55.62 | 4356.62 | 4192.5 | 164.12 | 4362 | 5.991 | 70.96%
2020-02-16 | 816 | 1109 | 1053 | 1154 | 56.08 | 4188.08 | 4050 | 138.08 | 4194 | 5.723 | 71.43% | Module Cleaning has been done in Row-G,H,I, Inverter No 4, total module cleaning- 594. |  | 594
2020-02-17 | 852 | 1154 | 1114 | 1219 | 60.46 | 4399.46 | 4238.25 | 161.21 | 4405 | 6.105 | 70.33% | Module Cleaning has been done in Row-J,K,L, and Tracker Inverter No 4, total module cleaning- 528.Grid Failure from-17:01 to 17:20. |  | 528
2020-02-18 | 857 | 1179 | 1129 | 1261 | 64.03 | 4490.03 | 4338 | 152.03 | 4496 | 6.236 | 70.27% | Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No 03, total module cleaning- 441 |  | 441
2020-02-19 | 640 | 847 | 837 | 861 | 42.45 | 3227.45 | 3108 | 119.45 | 3233 | 4.81 | 65.51% | Module Cleaning has been done in Row-O,N,M,Inverter No 03, total module cleaning- 651.Grid Failure from-16:27 to 18:17. Today we are repleced the d.c 12 amp fuselink of the string no 09++tive line ajb no 103 of the inverter no 04 during the time of (16:50 to 16:55) .Today Came Arifbhai from Abb.Ltd for Checked all Parameter of Inverter. |  | 651
2020-02-20 | 882 | 1225 | 1194 | 1291 | 66.4 | 4658.4 | 4487 | 171.4 | 4664 | 6.386 | 71.18% | Module Cleaning has been done in Row-M,N,Inverter No 03, total module cleaning- 462 |  | 462
2020-02-21 | 822 | 1164 | 1104 | 1184 | 58.27 | 4332.27 | 4185 | 147.27 | 4338 | 5.802 | 72.87% | Module Cleaning has been done in Row-J,K,L,Inverter No 02, total module cleaning- 819. |  | 819
2020-02-22 | 902 | 1255 | 1174 | 1260 | 64.31 | 4655.31 | 4476.75 | 178.56 | 4661 | 6.084 | 74.67% | Module Cleaning has been done in Row-H,I,Inverter No 01 and 02, total module cleaning-504. |  | 504
2020-02-23 | 832 | 1109 | 1044 | 1104 | 54.73 | 4143.73 | 4005 | 138.73 | 4149 | 5.54 | 72.99% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,Inverter No 01, total module cleaning-882.Cloudy day |  | 882
2020-02-24 | 877 | 1174 | 1098 | 1205 | 57.67 | 4411.67 | 4247.25 | 164.42 | 4417 | 5.898 | 72.99% | Module Cleaning has been done in Row-A,B,C,D,E,F,Inverter No 04, total module cleaning-792.Cloudy day |  | 792
2020-02-25 | 846 | 1145 | 1079 | 1199 | 57.18 | 4326.18 | 4187.25 | 138.93 | 4332 | 5.843 | 72.26% | Module Cleaning has been done in Row-G,H,I,Inverter No 04, total module cleaning-594.Cloudy day |  | 594
2020-02-26 | 786 | 1058 | 988 | 1114 | 51.62 | 3997.62 | 3854 | 143.62 | 4004 | 5.536 | 70.49% | Module Cleaning has been done in Row-J,K,L, and tracker , Inverter No 04, total module cleaning-528.Cloudy day,Grid Failure from 14:44 to 14:47. |  | 528
2020-02-27 | 812 | 1099 | 1053 | 1190 | 54.51 | 4208.51 | 4053.75 | 154.76 | 4214 | 5.757 | 71.34% | Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No -03, total module cleaning-441. Today we are install new tracker controller with display unit in tracker no-3. |  | 630
2020-02-28 | 706 | 927 | 933 | 993 | 48.62 | 3607.62 | 3477.75 | 129.87 | 3613 | 4.737 | 74.34% | Module Cleaning has been done in Row-L,M,N,Inverter No 02&03, total module cleaning-714.Cloudy day |  | 714
2020-02-29 | 811 | 1104 | 1088 | 1154 | 61.16 | 4218.16 | 4065 | 153.16 | 4244 | 5.645 | 73.28% | Today has been done Air filter paper clean of all inverter.(Cabinet door Filter)
2020-03-01 | 827 | 1159 | 1119 | 1199 | 65.09 | 4369.09 | 4219.5 | 149.59 | 4374 | 5.923 | 71.98% | Module Cleaning has been done in Row-J,K,Inverter No 02, total module cleaning-567 |  | 567
2020-03-02 | 806 | 1119 | 1049 | 1104 | 60.54 | 4138.54 | 3992.25 | 146.29 | 4144 | 5.626 | 71.79% | Module Cleaning has been done in Row-E,F,G,H,I, Inverter No 1& 02, total module cleaning- 1050.Grid Failure from-14:49 to 14:54. |  | 1050
2020-03-03 | 786 | 1039 | 967 | 1023 | 54.08 | 3869.08 | 3736.05 | 133.03 | 3875 | 5.377 | 70.24% | Module Cleaning has been done in Row-A,B,C,D,&A,B,C,D,E,,Inverter No 01&04, total module cleaning-930 |  | 930
2020-03-04 | 893 | 1209 | 1129 | 1265 | 65.34 | 4561.34 | 4406.25 | 155.09 | 4567 | 6.251 | 71.21% | Grid Failure from-18:04 to 18:10.
2020-03-05 | 816 | 1023 | 1024 | 1160 | 56.97 | 4079.97 | 3933 | 146.97 | 4085 | 5.694 | 69.92% | Today we are change and install new ++tive and --tive string DC 6 Sqmm cable (234meter) in string no- 1,2,3 of AJB No: 110 in Inverter No-2 due to underground fault(Cable Puncture).Cloudy Day.
2020-03-06 | 822 | 1099 | 1058 | 1199 | 62.62 | 4240.62 | 4069.5 | 171.12 | 4246 | 5.894 | 70.21% | Grid Failure IACE side due to VCB trip from-08:30 to 09:05 and 13:01 to 13:14.Cloudy Day.
2020-03-07 | 953 | 1331 | 1270 | 1432 | 79.74 | 5065.74 | 4895.25 | 170.49 | 5071 | 6.868 | 71.96% | Today came Powertech Engineers pvt.ltd for Oil filteration and testing of all 5 transformer, BDV test has been done of oil in all transformer.
2020-03-08 | 509 | 685 | 655 | 720 | 39.51 | 2608.51 | 2532 | 76.51 | 2614 | 3.518 | 72.42% | Grid failure from 9:38 to 13:38 because IACE side Grid failure due to VCB Trip.Module Cleaning has been done in Row-F,G,H, Inverter No 04, total module cleaning- 594. |  | 594
2020-03-09 | 927 | 1265 | 1210 | 1381 | 71.53 | 4854.53 | 4692.75 | 161.78 | 4855 | 6.508 | 72.71% | Module Cleaning has been done in Row-I,J,K,L, and tracker , Inverter No 04, total module cleaning-726. |  | 726
2020-03-10 | 897 | 1215 | 1169 | 1316 | 66.36 | 4663.36 | 4496.25 | 167.11 | 4669 | 6.319 | 72.02%
2020-03-11 | 792 | 1058 | 1034 | 1164 | 62.4 | 4110.4 | 3957.75 | 152.65 | 4111 | 5.44 | 73.65% | Module Cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No -03, total module cleaning-840.Cloudy Day |  | 840
2020-03-12 | 967 | 1336 | 1325 | 1457 | 88.69 | 5173.69 | 4993.5 | 180.19 | 5174 | 7.004 | 72% | Module Cleaning has been done in Row-J,K,L,M, Inverter No -02 and 03, total module cleaning-1071.IACE side Grid failure from 15:40 to 15:48. |  | 1071
2020-03-13 | 867 | 1200 | 1149 | 1250 | 72.49 | 4538.49 | 4381.5 | 156.99 | 4539 | 6.02 | 73.49% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I ,Inverter No- 1&2, total module cleaning-1386 |  | 1386
2020-03-14 | 968 | 1345 | 1291 | 1411 | 86 | 5101 | 4926 | 175 | 5101 | 6.989 | 71.14% | Grid Failure IACE side due to VCB trip from-11:41 to 12:07.
2020-03-15 | 705 | 973 | 912 | 978 | 59.34 | 3627.34 | 3489 | 138.34 | 3628 | 6.28 | 56.31% | Today Replaced the D.C.12 Amp fuse link of the string-03 --tive line in AJB-104 of The Inverter-4 during the period of 8:25 to 08:30, & Grid Failure IACE side due to VCB trip from-09:07 to 09:44 and 13:02 to 14:25(11KV Side). Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-4, total module cleaning-594, & Cloudy Day. |  | 594
2020-03-16 | 575 | 766 | 726 | 801 | 50.56 | 2918.56 | 2790 | 128.56 | 2919 | 6.776 | 41.99% | Module Cleaning has been done in Row-F,G,H,I, Inverter No -4 total module cleaning-792.Grid failure from 11:19 to 14:25(11KV Side). |  | 792
2020-03-17 | 922 | 1291 | 1230 | 1407 | 80.91 | 4930.91 | 4753.5 | 177.41 | 4931 | 6.709 | 71.64% | Module Cleaning has been done in Row-J,K,L, and trackers, Inverter No 4, total module cleaning-528. |  | 528
2020-03-18 | 887 | 1229 | 1184 | 1350 | 69.45 | 4719.45 | 4568.25 | 151.2 | 4725 | 6.488 | 70.98% | Today we are installed New LBS (650A) & 63KVA distribution transformer (11/.433KV) and get new supply in Plant(60 meter installed new 70Sq mm cable cable in 415V (LT) side).We are install new Analog Volt meter 415/110V (make: Rishab) in LT panel and Module Cleaning has been done in Row-P,Q,R,S,T , Inverter No 3, total module cleaning-441. |  | 441
2020-03-19 | 792 | 1089 | 1059 | 1170 | 66.92 | 4176.92 | 4008.75 | 168.17 | 4177 | 6.205 | 65.61% | Module Cleaning has been done in Row-N,O , Inverter No 3, total module cleaning-399.Today Came UGVCL Line man in evening time due to "B" Phase AB Switch are Sparking, So G.O.D Switch are disconnected for UGVCL Pole and add new link and joint the cable in during 16:14 to 16:55 |  | 399
2020-03-20 | 937 | 1296 | 1270 | 1431 | 84.33 | 5018.33 | 4773 | 245.33 | 5019 | 6.746 | 72.51% | Module Cleaning has been done in Row-K,L,M, Inverter No 2&3, total module cleaning-777 |  | 777
2020-03-21 | 872 | 1219 | 1184 | 1331 | 65.41 | 4671.41 | 4464 | 207.41 | 4677 | 6.434 | 70.85% | No Module cleaning (No Man power)
2020-03-22 | 822 | 1149 | 1114 | 1245 | 58.41 | 4388.41 | 4199.25 | 189.16 | 4394 | 6.097 | 70.24% | No Module cleaning (No Man power)
2020-03-23 | 801 | 1089 | 1054 | 1179 | 56.89 | 4179.89 | 3993 | 186.89 | 4185 | 5.777 | 70.61% | Cloudy Day and No Module cleaning (No Man power)
2020-03-24 | 852 | 1170 | 1134 | 1275 | 60.94 | 4491.94 | 4295.25 | 196.69 | 4500 | 6.152 | 71.29% | No Module cleaning (No Man power)
2020-03-25 | 469 | 584 | 569 | 615 | 23.8 | 2260.8 | 2085 | 175.8 | 2266 | 2.928 | 75.43% | Fully Cloudy Day and No Module cleaning (No Man power)
2020-03-26 | 594 | 771 | 741 | 822 | 31.68 | 2959.68 | 2805 | 154.68 | 2965 |  | #DIV/0! | Fully Cloudy Day and No Module cleaning (No Man power)
2020-03-27 | 741 | 978 | 937 | 1104 | 0 | 3760 | 3557.25 | 202.75 | 3765 |  | #DIV/0! | Today we are found Trackers 'ACDB' fire due to yesterday night time heavy rain with air flow so whole mcb burn in 'ACDB' box because water spread in Box ,So we are disconnect All string Inverter, and Grid failure from 12:55 to 13:05.Fully Cloudy Day and No Module cleaning (No Man power)
2020-03-28 | 963 | 1340 | 1286 | 1466 | 0 | 5055 | 4830.75 | 224.25 | 5060 |  | #DIV/0! | No Module cleaning (No Man power)
2020-03-29 | 957 | 1346 | 1290 | 1477 | 0 | 5070 | 4860.75 | 209.25 | 5075 |  | #DIV/0! | No Module cleaning (No Man power)
2020-03-30 | 918 | 1301 | 1255 | 1411 | 0 | 4885 | 4686.75 | 198.25 | 4890 |  | #DIV/0! | No Module cleaning (No Man power)
2020-03-31 | 912 | 1280 | 1230 | 1391 | 0 | 4813 | 4599.75 | 213.25 | 4818 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-01 | 913 | 1275 | 1225 | 1392 | 34.37 | 4839.37 | 4628.25 | 211.12 | 4845 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-02 | 922 | 1305 | 1260 | 1421 | 82.77 | 4990.77 | 4767 | 223.77 | 4991 |  | #DIV/0! | Today we are changed burn MCB and install new MCB connection of "ACDB" in trackers.today we are give water in all Earth Pit.No Module cleaning (No Man power)
2020-04-03 | 933 | 1301 | 1245 | 1426 | 83.18 | 4988.18 | 4774.5 | 213.68 | 4989 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-04 | 907 | 1275 | 1224 | 1381 | 82.28 | 4869.28 | 4664.25 | 205.03 | 4870 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-05 | 872 | 1240 | 1200 | 1336 | 79.41 | 4727.41 | 4521 | 206.41 | 4728 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-06 | 866 | 1220 | 1169 | 1310 | 77.34 | 4642.34 | 4443.75 | 198.59 | 4643 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-07 | 882 | 1225 | 1180 | 1341 | 77.69 | 4705.69 | 4493.25 | 212.44 | 4706 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-08 | 877 | 1209 | 1164 | 1316 | 74.43 | 4640.43 | 4432 | 208.43 | 4641 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-09 | 862 | 1190 | 1149 | 1295 | 73.41 | 4569.41 | 4371 | 198.41 | 4570 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-10 | 868 | 1199 | 1154 | 1285 | 75.58 | 4581.58 | 4374 | 207.58 | 4582 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-11 | 861 | 1190 | 1150 | 1280 | 74.06 | 4555.06 | 4333.5 | 221.56 | 4556 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-12 | 847 | 1194 | 1144 | 1260 | 75.6 | 4520.6 | 4317.75 | 202.85 | 4521 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-13 | 867 | 1190 | 1149 | 1271 | 74.96 | 4551.96 | 4347 | 204.96 | 4552 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-14 | 852 | 1179 | 1134 | 1260 | 74.68 | 4499.68 | 4292.25 | 207.43 | 4500 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-15 | 831 | 1114 | 1079 | 1199 | 69.17 | 4292.17 | 4075.5 | 216.67 | 4293 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-16 | 840 | 1127 | 1101 | 1221 | 70.17 | 4359.17 | 4139.25 | 219.92 | 4360 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-17 | 784 | 1040 | 985 | 1093 | 58.66 | 3960.66 | 3776.25 | 184.41 | 3961 |  | #DIV/0! | Cloudy day and No Module cleaning (No Man power)
2020-04-18 | 841 | 1125 | 1084 | 1189 | 68.18 | 4307.18 | 4102.5 | 204.68 | 4308 |  | #DIV/0! | Cloudy day and No Module cleaning (No Man power)
2020-04-19 | 852 | 1164 | 1124 | 1270 | 70.64 | 4480.64 | 4265.25 | 215.39 | 4481 |  | #DIV/0! | Cloudy day and No Module cleaning (No Man power)
2020-04-20 | 877 | 1200 | 1154 | 1306 | 78.13 | 4615.13 | 4404 | 211.13 | 4616 |  | #DIV/0! | Cloudy day and No Module cleaning (No Man power)
2020-04-21 | 837 | 1134 | 1094 | 1255 | 72.48 | 4392.48 | 4178.25 | 214.23 | 4393 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-22 | 841 | 1134 | 1094 | 1250 | 70.25 | 4389.25 | 4177.5 | 211.75 | 4390 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-23 | 877 | 1184 | 1144 | 1320 | 77.12 | 4602.12 | 4378.5 | 223.62 | 4603 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-24 | 872 | 1200 | 1159 | 1346 | 78.54 | 4655.54 | 4430.25 | 225.29 | 4656 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-25 | 872 | 1179 | 1129 | 1305 | 74.42 | 4559.42 | 4344.75 | 214.67 | 4560 |  | #DIV/0! | Grid failure from 17:17 to 17:37.Today Replaced the D.C.12 Amp fuse link of the string-03 --tive in AJB-102 of The Inverter-4 during the period of 18:30 to 18:35.No Module cleaning (No Man power)
2020-04-26 | 852 | 1159 | 1119 | 1306 | 74.14 | 4510.14 | 4287 | 223.14 | 4511 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-27 | 837 | 1149 | 1104 | 1295 | 74.07 | 4459.07 | 4237.5 | 221.57 | 4460 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-28 | 842 | 1165 | 1124 | 1306 | 75.39 | 4512.39 | 4299.75 | 212.64 | 4513 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-29 | 831 | 1144 | 1108 | 1290 | 73.81 | 4446.81 | 4227.75 | 219.06 | 4447 |  | #DIV/0! | No Module cleaning (No Man power)
2020-04-30 | 801 | 1104 | 1064 | 1225 | 71.02 | 4265.02 | 4056 | 209.02 | 4266 |  | #DIV/0! | Today has been done Air filter paper clean of all inverter.(Cabinet door Filter).No Module cleaning (No Man power)
2020-05-01 | 827 | 1123 | 1089 | 1260 | 70.01 | 4369.01 | 4153.5 | 215.51 | 4670 |  | #DIV/0! | Today we are change Brether of all Transformer(5 Nos).No Module cleaning (No Man power)
2020-05-02 | 862 | 1180 | 1139 | 1335 | 78.05 | 4594.05 | 4376.25 | 217.8 | 4595 |  | #DIV/0! | No Module cleaning (No Man power)
2020-05-03 | 836 | 1139 | 1093 | 1291 | 71.63 | 4430.63 | 4210.5 | 220.13 | 4431 |  | #DIV/0! | No Module cleaning (No Man power)
2020-05-04 | 847 | 1149 | 1109 | 1325 | 74.17 | 4504.17 | 4287 | 217.17 | 4505 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F Inverter No 4, total module cleaning-792. |  | 792
2020-05-05 | 792 | 1079 | 1039 | 1291 | 66.76 | 4267.76 | 4059.75 | 208.01 | 4268 |  | #DIV/0! | Module Cleaning has been done in Row- G,H,I,J,K,L and Trackers Inverter No 4, total module cleaning-1122. |  | 1122
2020-05-06 | 796 | 1099 | 1109 | 1335 | 70.92 | 4409.92 | 4185.75 | 224.17 | 4410 |  | #DIV/0! | Module Cleaning has been done in Row- N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-840. |  | 840
2020-05-07 | 801 | 1194 | 1164 | 1346 | 74.83 | 4579.83 | 4359.75 | 220.08 | 4580 |  | #DIV/0! | Module Cleaning has been done in Row- K,L,M, Inverter No 2 and 3, total module cleaning-777. |  | 777
2020-05-08 | 822 | 1215 | 1174 | 1348 | 76.24 | 4635.24 | 4408.5 | 226.74 | 4636 |  | #DIV/0! | Module Cleaning has been done in Row- ,I,J, Inverter No 1&2, total module cleaning-567. |  | 567
2020-05-09 | 851 | 1222 | 1159 | 1340 | 76.19 | 4648.19 | 4428 | 220.19 | 4649 |  | #DIV/0! | Module Cleaning has been done in Row- ,F,G,H, Inverter No 1 , total module cleaning-630. |  | 630
2020-05-10 | 882 | 1224 | 1160 | 1346 | 77.61 | 4689.61 | 4469.25 | 220.36 | 4690 |  | #DIV/0! | Module Cleaning has been done in Row- ,A,B,C,D,E,& A,B,C,D,E, Inverter No 1&2 , total module cleaning-1464. |  | 1464
2020-05-11 | 873 | 1185 | 1134 | 1356 | 75.29 | 4623.29 | 4405.5 | 217.79 | 4624 |  | #DIV/0! | Module Cleaning has been done in Row- F,G,H,I,J,K,L, and Trackers Inverter No 4, total module cleaning-1320. |  | 1320
2020-05-12 | 846 | 1174 | 1134 | 1316 | 76.26 | 4546.26 | 4334.25 | 212.01 | 4547 |  | #DIV/0! | Module Cleaning has been done in Row- N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-840. |  | 840
2020-05-13 | 868 | 1211 | 1159 | 1340 | 78.06 | 4656.06 | 4419 | 237.06 | 4657 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L,M, Inverter No- 2&3, total module cleaning-1344. |  | 1344
2020-05-14 | 882 | 1213 | 1159 | 1341 | 78.6 | 4673.6 | 4455.75 | 217.85 | 4674 |  | #DIV/0! | Grid failure from-16:55 to 17:04 and 18:00 to 18:06, & Module Cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No- 1, total module cleaning-1113. |  | 1113
2020-05-15 | 877 | 1195 | 1149 | 1351 | 78.47 | 4650.47 | 4414.5 | 235.97 | 4651 |  | #DIV/0! | Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990
2020-05-16 | 857 | 1174 | 1135 | 1320 | 74.69 | 4560.69 | 4347.75 | 212.94 | 4561 |  | #DIV/0! | Module Cleaning has been done in Row- H,I,J,K,L & Inverter No- 4 and Tracker , total module cleaning-924 |  | 924
2020-05-17 | 892 | 1230 | 1169 | 1356 | 79.1 | 4726.1 | 4480.5 | 245.6 | 4727 |  | #DIV/0! | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T & Inverter No-3 and Tracker , total module cleaning-1092 |  | 1092
2020-05-18 | 888 | 1205 | 1159 | 1341 | 75.37 | 4668.37 | 4424.25 | 244.12 | 4669 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L ,Inverter No-2 total module cleaning-1092.Today we are repleced the d.c 12 amp fuse link of the string no 03 --tive line AJB No-102 of the inverter No-04 during the time of 17:40 to 17:45. |  | 1092
2020-05-19 | 884 | 1228 | 1174 | 1406 | 80.59 | 4772.59 | 4539.75 | 232.84 | 4773 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113. |  | 1113
2020-05-20 | 880 | 1207 | 1175 | 1391 | 79.46 | 4732.46 | 4511.25 | 221.21 | 4733 |  | #DIV/0! |  |  | 990
2020-05-21 | 872 | 1219 | 1179 | 1341 | 79.5 | 4690.5 | 4458.75 | 231.75 | 4691 |  | #DIV/0! | Today we are repleced the d.c 12 amp fuse link of the string no 08 ++tive line AJB No-102 of the inverter No-04 during the time of 17:45 to 17:50.Module Cleaning has been done in Row- H,I,J,K,L & Trackers Inverter No- 4 and, total module cleaning-924 |  | 924
2020-05-22 | 882 | 1215 | 1170 | 1366 | 79.38 | 4712.38 | 4497 | 215.38 | 4713 |  | #DIV/0! | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092. |  | 1092
2020-05-23 | 887 | 1214 | 1169 | 1391 | 79.14 | 4740.14 | 4499.25 | 240.89 | 4741 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092. |  | 1092
2020-05-24 | 881 | 1220 | 1179 | 1406 | 81.76 | 4767.76 | 4533.75 | 234.01 | 4767 |  | #DIV/0! | Today has been done Air filter paper clean of all inverter.(Cabinet door Filter).Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113. |  | 1113
2020-05-25 | 641 | 892 | 862 | 1023 | 82.48 | 3500.48 | 3308.25 | 192.23 | 4767 |  | #DIV/0! | Today we are replaced 125A Change over switch of Incoming line 415V during 10:34 to 13:00..Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990
2020-05-26 | 766 | 1053 | 1018 | 1205 | 71.18 | 4113.18 | 3897.75 | 215.43 | 4114 |  | #DIV/0! | Grid failure from 7:32 to 7:54 and 12:52 to 13:51.Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924 |  | 924
2020-05-27 | 358 | 46 | 449 | 534 | 34.81 | 1421.81 | 1307.25 | 114.56 | 1308 |  | #DIV/0! | Grid failure from 7:38 to 13:30. Today grid failure after Inverter No-2 ABB 250kw failure due to Err. D.C Bracker trip (8188) replaced the bracker switch handle after started inverter-18:00. (During the Brack down time 13:50 to 18:00) and today we are changed AB switch of B-phase in Solar H-pole side due to grid failure. Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092. |  | 1092
2020-05-28 | 862 | 1154 | 1114 | 1326 | 74.42 | 4530.42 | 4290.75 | 239.67 | 4531 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092. |  | 1092
2020-05-29 | 826 | 1094 | 1053 | 1275 | 65.53 | 4313.53 | 4095 | 218.53 | 4314 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113. |  | 1113
2020-05-30 | 827 | 1094 | 1054 | 1285 | 67.36 | 4327.36 | 4121.25 | 206.11 | 4328 |  | #DIV/0! | Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990, and Cloudy day |  | 990
2020-05-31 | 821 | 1108 | 1093 | 1275 | 69.63 | 4366.63 | 4139.25 | 227.38 | 4367 |  | #DIV/0! | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day |  | 924
2020-06-01 | 792 | 1084 | 1039 | 1216 | 67.06 | 4198.06 | 3976.5 | 221.56 | 4199 |  | #DIV/0! | Grid failure from 7:38 to 13:30. Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092
2020-06-02 | 841 | 1119 | 1078 | 1255 | 9.77 | 4302.77 | 4130.25 | 172.52 | 4294 |  | #DIV/0! | Today evening time tracker postion automatically change so we are change and replace MCB(2 Nos - C32A TP & 3 Nos 2DP C16A ) in ACDB Tracker Box after manually strated 17:45, Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092 and Cloudy day. |  | 1092
2020-06-03 | 666 | 862 | 822 | 963 | 3.5 | 3316.5 | 3167.25 | 149.25 | 3317 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G,H, Inverter No- 1, total module cleaning-1113.Grid failure from 7:30 to 7:45 and 12:06 to 12:15 & 13.44 to 13:47.Cloudy day |  | 1113
2020-06-04 | 776 | 1023 | 993 | 1174 | 54.64 | 4020.64 | 3816.75 | 203.89 | 4021 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990.Grid failure from 07:27 to 07:38, Cloudy day. |  | 990
2020-06-05 | 811 | 1079 | 1043 | 1240 | 65.07 | 4238.07 | 4033.5 | 204.57 | 4239 |  | #DIV/0! | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day |  | 924
2020-06-06 | 782 | 1048 | 1003 | 1205 | 63.23 | 4101.23 | 3839.25 | 261.98 | 4102 |  | #DIV/0! | Grid failure from 8:37 to 8:45 and 12:42 to 12:50. Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092
2020-06-07 | 690 | 887 | 867 | 1013 | 48.52 | 3505.52 | 3375 | 130.52 | 3506 |  | #DIV/0! | Cloudy day.
2020-06-08 | 660 | 893 | 862 | 1008 | 51.39 | 3474.39 | 3258.75 | 215.64 | 3475 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092.Cloudy day. |  | 1092
2020-06-09 | 721 | 962 | 917 | 1093 | 65.33 | 3758.33 | 3578.25 | 180.08 | 3759 |  | #DIV/0! | Module cleaning by rain,Grid failure from 10:52 to 11:03,11:04 to 11:15, 11:30 to 11:45 , 11:48 to 11:59 and 12:03 to 12:26.
2020-06-10 | 736 | 963 | 938 | 1110 | 48.19 | 3795.19 | 3553.5 | 241.69 | 3796 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990
1900-01-05 | 695 | 877 | 846 | 1002 | 45.25 | 3465.25 | 3291.75 | 173.5 | 3466 |  | #DIV/0! | Module cleaning by rain.
1900-01-11 | 787 | 1048 | 1014 | 1215 | 57.51 | 4121.51 | 3909.75 | 211.76 | 4122 |  | #DIV/0! | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day,Grid failure from 17:10 to 17:40. |  | 924
2020-06-13 | 665 | 857 | 831 | 973 | 42.35 | 3368.35 | 3184.5 | 183.85 | 3369 |  | #DIV/0! | Module cleaning by rain.
2020-06-14 | 630 | 812 | 787 | 927 | 32.2 | 3188.2 | 3036 | 152.2 | 3189 |  | #DIV/0! | Module clean by rain.Grid failure from 7:30 to 8:36.
2020-06-15 | 662 | 977 | 942 | 1124 | 39.19 | 3744.19 | 3609 | 135.19 | 3745 |  | #DIV/0! | Module clean by rain.Grid failure from 9:17 to 9:25.
2020-06-16 | 664 | 968 | 938 | 1109 | 37.32 | 3716.32 | 3609 | 107.32 | 3717 |  | #DIV/0! | Module cleaning by rain.
2020-06-17 | 746 | 978 | 947 | 1109 | 37.53 | 3817.53 | 3597 | 220.53 | 3818 |  | #DIV/0! | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092
2020-06-18 | 771 | 1013 | 978 | 1164 | 42.07 | 3968.07 | 3765.75 | 202.32 | 3969 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092.Cloudy day. |  | 1092
2020-06-19 | 882 | 1079 | 1033 | 1270 | 46.16 | 4310.16 | 4035.75 | 274.41 | 4311 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113.Cloudy day. |  | 1113
2020-06-20 | 827 | 1094 | 1069 | 1286 | 48.99 | 4324.99 | 4112.25 | 212.74 | 4325 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990.Today we are replaced silica gel in Transformer No-2.(300KVA)Cloudy day. |  | 990
2020-06-21 | 735 | 957 | 927 | 1093 | 38.43 | 3750.43 | 3549.75 | 200.68 | 3751 |  | #DIV/0! | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day |  | 924
2020-06-22 | 832 | 1119 | 1084 | 1281 | 48.77 | 4364.77 | 4117.5 | 247.27 | 4365 |  | #DIV/0! | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092
2020-06-23 | 776 | 998 | 952 | 1179 | 43.52 | 3948.52 | 3774 | 174.52 | 3949 |  | #DIV/0! | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092.Cloudy day. |  | 1092
2020-06-24 | 580 | 726 | 696 | 816 | 30.34 | 2848.34 | 2658 | 190.34 | 2849 |  | #DIV/0! | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113.Grid failure from 10:35 to 10:38.Cloudy day. |  | 1113
2020-06-25 | 695 | 907 | 877 | 1069 | 43.27 | 3591.27 | 3403.5 | 187.77 | 3592 |  | #DIV/0! | Module cleaning by rain.
2020-06-26 | 676 | 887 | 862 | 1013 | 40.41 | 3478.41 | 3313.5 | 164.91 | 3479 |  | #DIV/0! | Module clean by rain.Grid failure from 16:34 to 16:47 & 17:46 to 17:57 and 18:06 to 18:22.
2020-06-27 | 761 | 1008 | 973 | 1164 | 58.06 | 3964.06 | 3738.75 | 225.31 | 3965 |  | #DIV/0! | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092
2020-06-28 | 832 | 1124 | 1088 | 1296 | 73.89 | 4413.89 | 4168.5 | 245.39 | 4414 |  | #DIV/0!
2020-06-29 | 574 | 1053 | 1018 | 1220 | 62.73 | 3927.73 | 3681 | 246.73 | 3928 |  | #DIV/0! | Today Inverter No:1(11:45 to 13:50) Breakdown due to Preventive Maintenance by AMC (ABB).Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092. |  | 1092
2020-06-30 | 499 | 641 | 625 | 720 | 30.72 | 2515.72 | 2388.75 | 126.97 | 2516 | 3.32 | 73.86% | Module clean by rain.Grid failure from 09:58 to 10:09 .
2020-07-01 | 529 | 685 | 655 | 776 | 39.09 | 2684.09 | 2470.5 | 213.59 | 2685 | 5.294 | 49.43% | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113.Grid failure from 10:39 to 13:25.Cloudy day. |  | 1113
2020-07-02 | 822 | 1109 | 1074 | 1296 | 72.83 | 4373.83 | 4167 | 206.83 | 4375 | 5.838 | 73.04% | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990
2020-07-03 | 635 | 842 | 812 | 983 | 47.98 | 3319.98 | 3165.75 | 154.23 | 3320 |  | #DIV/0! | Module clean by rain.Grid failure from 15:26 to 15:30 and 16:18 to 16.27 .
2020-07-04 | 781 | 1053 | 1013 | 1224 | 60.35 | 4131.35 | 3914.25 | 217.1 | 4132 | 5.722 | 70.38% | Module clean by rain.Grid failure from 16:08 to 16:10.
2020-07-05 | 651 | 842 | 811 | 958 | 36.52 | 3298.52 | 3126 | 172.52 | 3299 | 4.316 | 74.5% | Fully cloudy day.
2020-07-06 | 367 | 438 | 429 | 484 | 13.4 | 1731.4 | 1610.25 | 121.15 | 1732 | 2.071 | 81.51% | Module clean by rain.
2020-07-07 | 590 | 771 | 740 | 877 | 35.09 | 3013.09 | 2767.5 | 245.59 | 3014 | 4.057 | 72.41% | Module clean by rain.Grid failure from 11:14 to 11:21.
2020-07-08 | 434 | 550 | 535 | 625 | 23.18 | 2167.18 | 2076.75 | 90.43 | 2168 | 2.63 | 80.34% | Module clean by rain.
2020-07-09 | 594 | 776 | 751 | 887 | 36.01 | 3044.01 | 2816.25 | 227.76 | 3045 | 4.082 | 72.71% | Module clean by rain.
2020-07-10 | 736 | 973 | 942 | 1139 | 48.98 | 3838.98 | 3662.5 | 176.48 | 3839 | 5.091 | 73.5% | Module clean by rain.Grid failure from 11:12 to 11:16.
2020-07-11 | 686 | 912 | 887 | 1054 | 41.53 | 3580.53 | 3438.75 | 141.78 | 3581 | 4.512 | 77.35% | Module clean by rain.
2020-07-12 | 534 | 690 | 671 | 786 | 32.65 | 2713.65 | 2565 | 148.65 | 2714 | 3.543 | 74.66% | Module clean by rain.
2020-07-13 | 680 | 913 | 882 | 1033 | 44.45 | 3552.45 | 3315 | 237.45 | 3553 | 4.727 | 73.26% | Module clean by rain.
2020-07-14 | 650 | 887 | 867 | 1013 | 46.01 | 3463.01 | 3327 | 136.01 | 3464 | 4.748 | 71.11% | Fully cloudy day.Grid failure from 18:01 to 18:25.
2020-07-15 | 631 | 821 | 781 | 902 | 39.47 | 3174.47 | 2970.75 | 203.72 | 3175 | 4.269 | 72.49% | Today we are replaced cooling fan(Cabinet door)D.C. side in Inverter No-4 and remove 2 Nos fan (Not working)A.C side(Canbinet door) in Inverter No-3.(total 3 fan not working)Module clean by rain.Grid failure from 17:07 to 17:11.
2020-07-16 | 619 | 817 | 791 | 918 | 33.18 | 3178.18 | 3002.25 | 175.93 | 3179 | 3.992 | 77.62% | Module clean by rain.
2020-07-17 | 636 | 837 | 600 | 957 | 34.07 | 3064.07 | 2847.75 | 216.32 | 3065 | 4.338 | 68.86% | Yesterday night (16-07-2020) Inverter No-3 not working due ACDC Rectifier switch(SMPS) are not work so Inverter are stop after 17-07-2020 manually started 10:45am.
2020-07-18 | 745 | 1048 | 1013 | 1230 | 61.71 | 4097.71 | 3906 | 191.71 | 4098 | 5.951 | 67.12% | Cloudy day.Grid failure from 12:01 to 12:09 and 16:33 to 17:23.
2020-07-19 | 751 | 1028 | 988 | 1200 | 60.87 | 4027.87 | 3845.25 | 182.62 | 4028 | 5.374 | 73.05% | Cloudy day
2020-07-20 | 706 | 948 | 917 | 1098 | 52.76 | 3721.76 | 3487.5 | 234.26 | 3722 | 4.992 | 72.67% | Cloudy day
2020-07-21 | 751 | 1033 | 1003 | 1195 | 51.23 | 4033.23 | 3848.25 | 184.98 | 4034 | 5.5 | 71.49% | Cloudy day
2020-07-22 | 812 | 1144 | 1104 | 1346 | 60.95 | 4466.95 | 4266 | 200.95 | 4467 | 6.277 | 69.36% | Module clean by rain.Cloudy day
2020-07-23 | 720 | 988 | 953 | 1139 | 57.19 | 3857.19 | 3641.25 | 215.94 | 3858 | 5.241 | 71.75% | Module clean by rain.Cloudy day
2020-07-24 | 620 | 867 | 837 | 983 | 41.74 | 3348.74 | 3163.5 | 185.24 | 3349 | 4.398 | 74.22% | Module clean by rain.Cloudy day
2020-07-25 | 534 | 736 | 710 | 836 | 35.45 | 2851.45 | 2730 | 121.45 | 2852 | 4.556 | 61.01% | Grid failure from 08:56 to 10:17. Module clean by rain.Cloudy day
2020-07-26 | 666 | 902 | 872 | 1024 | 49.98 | 3513.98 | 3300.75 | 213.23 | 3514 | 4.778 | 71.68% | Cloudy day
2020-06-27 | 720 | 1018 | 983 | 1159 | 63.76 | 3943.76 | 3738.5 | 205.26 | 3944 | 5.15 | 74.64% | Cloudy day
2020-07-28 | 656 | 907 | 887 | 1028 | 50.53 | 3528.53 | 3335.25 | 193.28 | 3529 | 4.819 | 71.38% | Today has been done Air filter paper clean of all inverter (Cabinet door Filter).Cloudy day
2020-07-29 | 665 | 922 | 887 | 1043 | 45.96 | 3562.96 | 3347.25 | 215.71 | 3563 | 4.988 | 69.62% | Cloudy day.Grid failure from 11:34 to 11:46
2020-07-30 | 519 | 701 | 670 | 781 | 30.88 | 2701.88 | 2580 | 121.88 | 2702 | 3.466 | 75.98% | Module clean by rain.Cloudy day
2020-07-31 | 686 | 953 | 918 | 1094 | 53.63 | 3704.63 | 3461.25 | 243.38 | 3705 | 5.109 | 70.68% | Cloudy day
2020-08-01 | 705 | 983 | 947 | 1149 | 58.14 | 3842.14 | 3654 | 188.14 | 3843 | 4.828 | 77.58% | Cloudy day
2020-08-02 | 696 | 993 | 958 | 1129 | 57.52 | 3833.52 | 3629.25 | 204.27 | 3834 | 5.476 | 68.24% | Cloudy day.Grid failure from 15:39 to 15:46
2020-08-03 | 670 | 942 | 907 | 1059 | 46.93 | 3624.93 | 3417.75 | 207.18 | 3625 | 4.808 | 73.48% | Cloudy day
2020-08-04 | 640 | 902 | 877 | 1053 | 54.3 | 3526.3 | 3337.5 | 188.8 | 3519 | 4.946 | 69.35% | Cloudy day
2020-08-05 | 499 | 671 | 645 | 756 | 35.1 | 2606.1 | 2476.5 | 129.6 | 2604 | 3.453 | 73.5% | Cloudy day.Grid failure from 16:43 to 17:02
2020-08-06 | 202 | 282 | 288 | 318 | 8.73 | 1098.73 | 936.75 | 161.98 | 1099 | 1.413 | 75.81% | Today we are change and replace new phase failure relay in Inverter no-1 during 9:45 to 10:30 and change and replace new SPD in AJB No-109 in Inverter No-2 during 10:40 to 11:45. .Module clean by rain.fully cloudy day
2020-08-07 | 363 | 529 | 504 | 575 | 18.15 | 1989.15 | 1798.5 | 190.65 | 1989 | 2.506 | 77.36% | Today we are change and replace new SPD in AJB No-104 in Inverter No-1 and AJB No-117 in Inverter No-3 during 9:10 to 09:45.Module clean by rain.fully cloudy day
2020-08-08 | 469 | 746 | 726 | 861 | 33.89 | 2835.89 | 2711.25 | 124.64 | 2836 | 3.68 | 75.11% | Module clean by rain.Cloudy day
2020-08-09 | 282 | 428 | 413 | 474 | 13.41 | 1610.41 | 1434.75 | 175.66 | 1611 | 1.958 | 80.19% | Module clean by rain.fully cloudy day
2020-08-10 | 398 | 626 | 600 | 691 | 20.79 | 2335.79 | 2186.25 | 149.54 | 2336 | 3.104 | 73.35% | Module clean by rain.cloudy day
2020-08-11 | 529 | 848 | 826 | 972 | 35.86 | 3210.86 | 3042.75 | 168.11 | 3211 | 3.397 | 92.13% | Today we are replaced connector in string no-03(++tive) of AJB No-104 inverter no-1 during 10:00 to 10:25..Module clean by rain.cloudy day
2020-08-12 | 338 | 523 | 499 | 580 | 18.37 | 1958.37 | 1814.25 | 144.12 | 1959 | 2.576 | 74.12% | Cloudy day.Grid failure from 15:37 to 15:25
2020-08-13 | 242 | 363 | 353 | 398 | 10.78 | 1366.78 | 1222.5 | 144.28 | 1223 | 1.71 | 69.71% | Module clean by rain. cloudy day
2020-08-14 | 378 | 585 | 569 | 666 | 20.28 | 2218.28 | 2049 | 169.28 | 2219 | 2.588 | 83.57% | Cloudy day.Grid failure from 08:30 to 08:37
2020-08-15 | 267 | 413 | 399 | 453 | 13.19 | 1545.19 | 1408.5 | 136.69 | 1546 | 2.022 | 74.52% | Module clean by rain. Fully cloudy day
2020-08-16 | 373 | 479 | 469 | 534 | 11.32 | 1866.32 | 1710 | 156.32 | 1867 | 2.315 | 78.6% | Today we are found (morning time) the error of Isolation resistance in string-3 of string inverter no-6 after remove the string in inverter.Module clean by rain. Fully cloudy day
2020-08-17 | 393 | 499 | 478 | 565 | 15.45 | 1950.45 | 1767.75 | 182.7 | 1951 | 2.33 | 81.61% | Module clean by rain, Cloudy day.Grid failure from 15:30 to 15:36 and 15:42 to 15:51 & 18:15 to 18:18.
2020-08-18 | 403 | 529 | 509 | 600 | 18.72 | 2059.72 | 1953 | 106.72 | 2058 |  | #DIV/0! | today we are not found value of insolation in scada..Module clean by rain, Cloudy day.Grid failure from 13:23 to 13:29.
2020-08-19 | 585 | 787 | 772 | 897 | 30.73 | 3071.73 | 2882.25 | 189.48 | 3072 |  | #DIV/0! | Module clean by rain, Cloudy day
2020-08-20 | 414 | 514 | 509 | 595 | 15.58 | 2047.58 | 1882.05 | 165.53 | 2048 |  | #DIV/0! | Module clean by rain, Cloudy , today we are replace the dc 12 amp fuse link of the string no 06 -- line,Ajb no 103 inverter no 04 during 08:20 to 08:25.
2020-08-21 | 327 | 433 | 418 | 493 | 19.97 | 1690.97 | 1534.5 | 156.47 | 1691 |  | #DIV/0! | Today installed new copper transformer 63KVA and removed aluminium transformer 63KVA during 14:20 to 15:35.we are change and replaced adam-4015-CE in tracker side(WS-2)
2020-08-22 | 227 | 277 | 267 | 318 | 8.51 | 1097.51 | 987 | 110.51 | 1098 |  | #DIV/0! | Today we are change and replaced adam-4118-AE in Inverter-1 side (WS-1).Module clean by rain. Fully cloudy day
2020-08-23 | 151 | 187 | 176 | 212 | 4.91 | 730.91 | 588.75 | 142.16 | 776 |  | #DIV/0! | Module clean by rain. Fully cloudy day
2020-08-24 | 232 | 282 | 268 | 317 | 7.63 | 1106.63 | 966 | 140.63 | 1107 |  | #DIV/0! | Module clean by rain. Fully cloudy day
2020-08-25 | 559 | 741 | 690 | 872 | 34.19 | 2896.19 | 2718 | 178.19 | 2897 |  | #DIV/0! | Today we are Install the new Communication cable CAT 6(128m)in SEED Box-1 inverter -1 side total 3 cable install 1.Anomometer ,2.humidity weather and 3, Signal cable.
2020-08-26 | 529 | 691 | 640 | 822 | 34.07 | 2716.07 | 2514.75 | 201.32 | 2717 |  | #DIV/0! | Today Replaced the D.C.12 Amp fuse link of the string-03 --tive line in AJB-102 of The Inverter-4 during the period of 8:15 to 08:20.
2020-08-27 | 661 | 902 | 832 | 1089 | 50.89 | 3534.89 | 3380.25 | 154.64 | 3535 |  | #DIV/0!
2020-08-28 | 484 | 625 | 574 | 735 | 24.5 | 2442.5 | 2289.75 | 152.75 | 2443 | 2.953 | 80.63%
2020-08-29 | 494 | 670 | 620 | 837 | 32.75 | 2653.75 | 2473.5 | 180.25 | 2654 | 3.715 | 69.63% | Today afternoon time breakdown due to install new Energy meter of Incoming line (415V) during 15:51 to 16:21.
2020-08-30 | 111 | 136 | 126 | 156 | 3.65 | 532.65 | 422.25 | 110.4 | 533 | 0.647 | 80.29%
2020-08-31 | 257 | 318 | 303 | 378 | 11.48 | 1267.48 | 1130.25 | 137.23 | 1268 | 1.408 | 87.77%
2020-09-01 | 650 | 907 | 826 | 1054 | 44.35 | 3481.35 | 3285 | 196.35 | 3482 | 4.282 | 79.26%
2020-09-02 | 595 | 811 | 746 | 947 | 37.23 | 3136.23 | 2988.75 | 147.48 | 3137 | 3.845 | 79.52% | Today P.M of VCB and install new single core cable(230v AC) in VCB to LBS for Auxiliary Suppy to LBS during 17:40 to 18:50.
2020-09-03 | 625 | 882 | 807 | 1008 | 41.22 | 3363.22 | 3150.75 | 212.47 | 3364 | 4.317 | 75.95%
2020-09-04 | 731 | 1033 | 947 | 1185 | 53.42 | 3949.42 | 3751.5 | 197.92 | 3950 | 5.169 | 74.48% | Grid failure from 09:26 to 09:30 and 14:09 to 14:11.
2020-09-05 | 661 | 927 | 847 | 1074 | 45.63 | 3554.63 | 3360 | 194.63 | 3555 | 4.446 | 77.93%
2020-09-06 | 705 | 1008 | 928 | 1174 | 52.63 | 3867.63 | 3691.5 | 176.13 | 3868 | 4.862 | 77.54%
2020-09-07 | 71 | 96 | 75 | 91 | 3.64 | 336.64 | 229.5 | 107.14 | 337 | 4.572 | 7.184% | Grid failure from 09:33 to 16:48
2020-09-08 | 690 | 998 | 912 | 1169 | 50.01 | 3819.01 | 3615.75 | 203.26 | 3820 | 4.929 | 75.54% | Today we are install new REC module (3 Nos) in Inverter No-1. 1)Module No- 15 (Row No-E) and B Line, Module no:JMPD100902548 ,2)Module No- 12 (Row No-G) and B Line, Module no:JMPD100903063,3)Module No- 12 (Row No-H) and B Line , Module no:JMPD100902866 due to old module gone to testing purpose on singapore.
2020-09-09 | 530 | 746 | 681 | 842 | 34.8 | 2833.8 | 2662.5 | 171.3 | 2834 | 3.575 | 77.26% | Today we are install new 15KW ACDB Box in Tracker's Inverter.
2020-09-10 | 695 | 993 | 902 | 1169 | 45.39 | 3804.39 | 3594 | 210.39 | 3805 | 5.027 | 73.77% | Grid Failure From-16:44 to 16:55
2020-09-11 | 585 | 847 | 771 | 958 | 42.42 | 3203.42 | 3031.5 | 171.92 | 3204 | 4.182 | 74.67%
2020-09-12 | 675 | 993 | 897 | 1139 | 49.16 | 3753.16 | 3540 | 213.16 | 3754 | 4.845 | 75.52% | Grid failure from -13:07 to 13:12
2020-09-13 | 610 | 862 | 787 | 993 | 43.04 | 3295.04 | 3132.75 | 162.29 | 3296 | 2.356 | 136.4%
2020-09-14 | 494 | 680 | 625 | 781 | 33.59 | 2613.59 | 2445 | 168.59 | 2614 | 3.313 | 76.9% | Grid failure from -12:29 to12:38
2020-09-15 | 559 | 786 | 715 | 897 | 38.3 | 2995.3 | 2806.5 | 188.8 | 2996 | 3.762 | 77.62%
2020-09-16 | 560 | 796 | 726 | 897 | 35.95 | 3014.95 | 2853.75 | 161.2 | 3015 | 3.852 | 76.29%
2020-09-17 | 463 | 640 | 590 | 731 | 27.85 | 2451.85 | 2250 | 201.85 | 2452 | 3.082 | 77.54%
2020-09-18 | 570 | 792 | 726 | 917 | 37.08 | 3042.08 | 2851.5 | 190.58 | 3043 | 3.767 | 78.73%
2020-09-19 | 655 | 942 | 856 | 1014 | 49.71 | 3516.71 | 3355.5 | 161.21 | 3517 | 4.413 | 77.68%
2020-09-20 | 630 | 943 | 862 | 1128 | 45.49 | 3608.49 | 3361.5 | 246.99 | 3609 | 4.516 | 77.89%
2020-09-21 | 676 | 1003 | 913 | 1150 | 46.45 | 3788.45 | 3568.5 | 219.95 | 3793 | 4.715 | 78.41%
2020-09-22 | 741 | 1119 | 1018 | 1275 | 61.33 | 4214.33 | 4010.25 | 204.08 | 4215 | 5.426 | 75.71%
2020-09-23 | 519 | 715 | 650 | 806 | 30.84 | 2720.84 | 2555.25 | 165.59 | 2721 | 3.045 | 87.1% | Today we are cleaning all inverter Door filters.
2020-09-24 | 720 | 1069 | 973 | 1225 | 58.76 | 4045.76 | 3833.25 | 212.51 | 4046 | 5.261 | 74.96%
2020-09-25 | 651 | 942 | 851 | 1084 | 52.59 | 3580.59 | 3390.75 | 189.84 | 3581 | 4.634 | 75.32%
2020-09-26 | 590 | 857 | 787 | 973 | 44.67 | 3251.67 | 3058.5 | 193.17 | 3252 | 4.066 | 77.95%
2020-09-27 | 529 | 761 | 690 | 856 | 39.46 | 2875.46 | 2702.25 | 173.21 | 2876 | 3.652 | 76.76%
2020-09-28 | 660 | 969 | 907 | 1104 | 56.35 | 3696.35 | 3500.25 | 196.1 | 3697 | 4.82 | 74.76% | Today we are found 3 MC4 connector Burn in Invertor No-3 AJB No-2 string No-8 ++tive site & AJB 4 string No-1 ++tive site & AJB-6 string No-2 ++tive site. we replaced all 3 MC4 connector and started the strings.
2020-09-29 | 640 | 952 | 918 | 1104 | 55.75 | 3669.75 | 3468.75 | 201 | 3670 | 4.767 | 75.04% | Module Cleaning has been done in Row- A,B,C,D,E,F, Inverter No- 4, total module cleaning-792, and Cloudy day. |  | 792
2020-09-30 | 696 | 1053 | 1028 | 1210 | 59.5 | 4046.5 | 3834.75 | 211.75 | 4047 | 4.655 | 84.74% | Module Cleaning has been done in Row- G,H,I Inverter No- 4, total module cleaning-594, and Cloudy day. |  | 594
2020-10-01 | 660 | 983 | 937 | 1179 | 58.19 | 3817.19 | 3616.5 | 200.69 | 3818 | 4.89 | 76.1% | Module Cleaning has been done in Row- J,K,L,A,B,C, and Trackers Inverter No- 4, total module cleaning-816, and Today we are found 2 MC4 connector Burn in Invertor No-3 AJB No-2 string No-2 ++tive site & AJB 3 string No-1 ++tive site. we replaced all 2 MC4 connector and started the strings. |  | 816
2020-10-02 | 680 | 1033 | 1004 | 1235 | 63.3 | 4015.3 | 3804.75 | 210.55 | 4016 | 5.162 | 75.83% | Module Cleaning has been done in Row-,D,E,F,G,H, Inverter No- 4, total module cleaning-702,Grid failure from -12:58 to 13:01 & 17:01 to 17:04 |  | 702
2020-10-03 | 716 | 1120 | 1083 | 1351 | 70.77 | 4340.77 | 4122.75 | 218.02 | 4341 | 5.624 | 75.23% | Module Cleaning has been done in Row- I,J,K,L, Tracker 5,6,7 and Row-Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1020 |  | 1020
2020-10-04 | 670 | 1002 | 983 | 1229 | 64.97 | 3948.97 | 3744.75 | 204.22 | 3949 | 5.089 | 75.63%
2020-10-05 | 706 | 1084 | 1079 | 1306 | 70.4 | 4245.4 | 4021.5 | 223.9 | 4246 | 5.312 | 77.91% | Module Cleaning has been done in Row- L Inverter No- 2 & M,N,O,P Inverter No- 3 total module cleaning-1050 |  | 1050
2020-10-06 | 650 | 1073 | 1038 | 1204 | 66.33 | 4031.33 | 3825.75 | 205.58 | 4032 | 5.541 | 70.92% | Module Cleaning has been done in Row- H Inverter No- 1 & I,J,K Inverter No- 2 total module cleaning-1071 & Grid failure from -11:35 to12:07 |  | 1071
2020-10-07 | 700 | 1150 | 1079 | 1235 | 64.52 | 4228.52 | 4018.5 | 210.02 | 4229 | 5.531 | 74.52% | Module Cleaning has been done in Row- A,B,C,D,E,F,G Inverter No- 1 & R,S,T Inverter No- 3 total module cleaning-1050 & Grid failure from -07:15 to 07:30 & 08:09 to 08:14 & 10:28 to 10:35 & In the cantrol room 1 exhaust fan failure, removed the fan and send to reparing. |  | 1050
2020-10-08 | 707 | 1144 | 1103 | 1225 | 70.81 | 4249.81 | 4045.5 | 204.31 | 4250 | 5.491 | 75.44% | Module Cleaning has been done in Row- L,Inverter No- 2 & M,N,O,P,Q, Inverter No- 3 & total module cleaning-1176 & Grid failure from -05:25 to 06:08. |  | 1176
2020-10-09 | 690 | 1099 | 1049 | 1164 | 61.3 | 4063.3 | 3853.5 | 209.8 | 4064 | 5.011 | 79.05% | Module Cleaning has been done in Row- H,Inverter No- 1 & I,J,K, Inverter No- 2 & total module cleaning-1071 |  | 1071
2020-10-10 | 690 | 1093 | 1033 | 1140 | 63.86 | 4019.86 | 3808.5 | 211.36 | 4020 | 5.144 | 76.17% | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 |  | 1044
2020-10-11 | 666 | 1034 | 983 | 1093 | 59.99 | 3835.99 | 3651.75 | 184.24 | 3836 | 4.893 | 76.41% | Grid failure from -16:23 to16:26
2020-10-12 | 615 | 962 | 907 | 1049 | 53.47 | 3586.47 | 3382.5 | 203.97 | 3587 | 5.029 | 69.52% | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 & Grid failure from -10:03 to10:44 |  | 1026
2020-10-13 | 660 | 998 | 953 | 1144 | 58.9 | 3813.9 | 3622.5 | 191.4 | 3814 | 4.765 | 78.01% | Module Cleaning has been done in Row- I,J,K,L, Inverter No- 4 & Q,R,S,T, Inverter No - 3, total module cleaning-1020 |  | 1020
2020-10-14 | 650 | 983 | 967 | 1119 | 58.9 | 3777.9 | 3587.25 | 190.65 | 3778 | 4.569 | 80.59% | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 & Grid failure from -17:10 to 17:14 |  | 1050
2020-10-15 | 661 | 1053 | 1019 | 1199 | 63.01 | 3995.01 | 3774 | 221.01 | 3996 | 4.865 | 80.06% | Module Cleaning has been done in Row- H, Inverter No- 1 & I,J,K Inverter No - 2, total module cleaning-1071 |  | 1071
2020-10-16 | 619 | 963 | 912 | 1089 | 53.13 | 3636.13 | 3435 | 201.13 | 3637 | 4.464 | 79.41% | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 & Grid failure from -15:00 to15:05 |  | 1044
2020-10-17 | 479 | 706 | 675 | 801 | 32.11 | 2693.11 | 2502 | 191.11 | 2694 | 3.311 | 79.3% | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026
2020-10-18 | 525 | 761 | 726 | 872 | 40.42 | 2924.42 | 2757 | 167.42 | 2925 | 3.541 | 80.51%
2020-10-19 | 594 | 887 | 852 | 1003 | 45.75 | 3381.75 | 3185.25 | 196.5 | 3382 | 3.922 | 84.05% | Module Cleaning has been done in Row- I,J,K,L, Inverter No- 4 & Q,R,S,T, Inverter No - 3, total module cleaning-1020 |  | 1020
2020-10-20 | 625 | 953 | 922 | 1064 | 52.96 | 3616.96 | 3410.25 | 206.71 | 3617 | 4.68 | 75.33% | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 |  | 1050
2020-10-21 | 635 | 993 | 948 | 1099 | 55.09 | 3730.09 | 3543 | 187.09 | 3731 | 4.802 | 75.73% | Module Cleaning has been done in Row- H, Inverter No- 1 & I,J,K Inverter No - 2, total module cleaning-1071 |  | 1071
2020-10-22 | 716 | 1144 | 1083 | 1257 | 71.13 | 4271.13 | 4062.75 | 208.38 | 4272 | 5.474 | 76.06% | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 & Today 1 Module Damage By Monkey, Inverter No-4 Thin Film Side Row No-C Module No-50 'B' Side S.No-NPC 10BY1116233 |  | 1044
2020-10-23 | 731 | 1169 | 1109 | 1275 | 73.98 | 4357.98 | 4151.25 | 206.73 | 4358 | 5.555 | 76.46% | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026
2020-10-24 | 705 | 1144 | 1079 | 1270 | 72.99 | 4270.99 | 4078.5 | 192.49 | 4271 | 9.63 | 43.23% | Module Cleaning has been done in Row- I,J,K, Inverter No- 4 & total module cleaning - 540 |  | 540
2020-10-25 | 615 | 1039 | 988 | 1154 | 61.68 | 3857.68 | 3661.5 | 196.18 | 3858 | 5.066 | 74.22%
2020-10-26 | 650 | 1129 | 1078 | 1270 | 71.27 | 4198.27 | 3997.5 | 200.77 | 4199 | 5.42 | 75.51% | Module Cleaning has been done in Row- L, Inverter No- 4 & Tracker 5,6,7, & N,O,P,Q,R,S,T, & total module cleaning - 1026 Today Failure D2D Blower Fan Inverter No - 1, & We Replaced New D2D Blower Fan. |  | 1026
2020-10-27 | 640 | 952 | 1054 | 1205 | 70.66 | 3921.66 | 3736.5 | 185.16 | 3922 | 5.406 | 70.71% | Grid failure from 10:07 to 10:11 & 11:00 to 11:11 & Today we are cleaning all inverter Door filters. & Today Come to ABB Engineer For Inverter No-2, for PM Activity, Breakdown During 13:14 to 14:06 & Module Cleaning has been done in Row- J,K,L, Inverter No-2 & Row No- M, Inverter NO-3 & total module cleaning - 1071 |  | 1071
2020-10-28 | 671 | 1094 | 1033 | 1149 | 66.5 | 4013.5 | 3816.75 | 196.75 | 4014 | 5.027 | 77.83% | Module Cleaning has been done in Row- E,F,G,H, Inverter No-1 & Row No- I, Inverter NO-2 & total module cleaning - 1050 |  | 1050
2020-10-29 | 660 | 1038 | 978 | 1074 | 61.97 | 3811.97 | 3612 | 199.97 | 3812 | 4.883 | 76.09% | Grid failure from -11:33 to11:38 & Module Cleaning has been done in Row- A,B,C,D, Inverter No-1 & Row No- A,B,C,D,E,F, Inverter NO-4 & total module cleaning - 1128 |  | 1128
2020-10-30 | 671 | 1048 | 998 | 1093 | 64.13 | 3874.13 | 3683.25 | 190.88 | 3875 | 5.034 | 75.03% | Module Cleaning has been done in Row- G,H,I,J,K,L Tracker 5,6,7 and Row-Inverter No- 4 & total module cleaning-1122& Grid failure from-1:34 to 1:37 |  | 1122
2020-10-31 | 655 | 998 | 942 | 1074 | 58.85 | 3727.85 | 3535.5 | 192.35 | 3728 | 4.658 | 78.01%
2020-11-01 | 630 | 973 | 923 | 1038 | 57.27 | 3621.27 | 3453 | 168.27 | 3622 | 4.603 | 76.69%
2020-11-02 | 625 | 948 | 922 | 1008 | 56.12 | 3559.12 | 3370.5 | 188.62 | 3560 | 4.554 | 76.19% | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T Inverter No- 3 & total module cleaning-1085 |  | 1085
2020-11-03 | 645 | 1028 | 993 | 1089 | 61.72 | 3816.72 | 3624.75 | 191.97 | 3817 | 4.73 | 78.65% | Grid failure from -08:12 to 08:17 & Module Cleaning has been done in Row- I,J,K,L, Inverter No- 2 total module cleaning-1092 |  | 1092
2020-11-04 | 700 | 1124 | 1059 | 1174 | 67.37 | 4124.37 | 3927.75 | 196.62 | 4125 | 5.058 | 79.49% | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113 |  | 1113
2020-11-05 | 651 | 1018 | 962 | 1059 | 59.77 | 3749.77 | 3562.5 | 187.27 | 3750 | 4.766 | 76.69% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No- 4, total module cleaning-1188 |  | 1188
2020-11-06 | 675 | 1048 | 988 | 1129 | 62.63 | 3902.63 | 3705 | 197.63 | 3903 | 4.943 | 76.96% | Module Cleaning has been done in Row- I,J,K,L, Tracker 5,6,7 and Row-Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1020 |  | 1020
2020-11-07 | 656 | 1013 | 978 | 1084 | 61.89 | 3792.89 | 3602.25 | 190.64 | 3793 | 4.759 | 77.68% | Today we are found 3 MC4 connector Burn in Inverter No-4 AJB No-105 string No-2 ++tive line & string No-4 --tive line 5--tive&7++tive line. we replaced all 3 MC4 connector and started the strings & Module clening has been done in Row l, inverter No-2 M,N,O,P Inverter no-3 total Module Clening-1050 |  | 1050
2020-11-08 | 645 | 983 | 952 | 1023 | 58.71 | 3661.71 | 3472.5 | 189.21 | 3662 | 4.461 | 80.01% | Today we are found 2 MC4 connector Burn in Inverter No-4 AJB No-106 string No-2 ++tive line & string No-4 --tive line & . we replaced all 2 MC4 connector and started the strings
2020-11-09 | 605 | 933 | 888 | 942 | 53.72 | 3421.72 | 3240 | 181.72 | 3422 | 4.344 | 76.78% | Today we are found 4 MC4 connector Burn in Inverter No-2 AJB No-01 string No-1 ++tive line & string No-4 --tive line & AJB-7 string No-7++tive line. we replaced all 4 MC4 connector and started the strings & Grid failure from 9:19 to 9:24 & Moduule Cleaning has been Done in Row-H, inverter no-1 I,J,K, inverter No-2 total moduel clening 1071 |  | 1071
10Now | 509 | 781 | 705 | 827 | 43.83 | 2865.83 | 2685.75 | 180.08 | 2866 | 4.464 | 62.58% | Yesterday nighat time Grid failure & UGVCL side phase sikvans chang so morning time inverter not wark up after all phase sikvans chang then inverter stated 10:40 & Module cleaning has been done in Row-A,B,C,D,E,F,G inverter no-1 & A,B inverter no-4&total module cleaning-1044 |  | 1044
2020-11-11 | 609 | 912 | 857 | 907 | 47.94 | 3332.94 | 3156.75 | 176.19 | 3333 | 4.208 | 77.2% | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026
2020-11-12 | 585 | 847 | 796 | 847 | 46.23 | 3121.23 | 2943.75 | 177.48 | 3121 | 3.836 | 79.3% | Module Cleaning has been done in Row- I,J,K,L, Inverter no-4 & Tracker 1,2,3, and Row-Q,R,S,T, Inverter No- 3 & total module cleaning-1020 |  | 1020
2020-11-13 | 635 | 983 | 943 | 1058 | 59.24 | 3678.24 | 3487.5 | 190.74 | 3679 | 4.669 | 76.8% | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 & Grid failure from -9:44 to 9:52 |  | 1050
2020-11-14 | 620 | 943 | 907 | 1008 | 55.08 | 3533.08 | 3344.25 | 188.83 | 3534 | 4.453 | 77.35%
2020-11-15 | 574 | 861 | 832 | 923 | 47.99 | 3237.99 | 3069.75 | 168.24 | 3238 | 4.13 | 76.42%
2020-11-16 | 645 | 1034 | 993 | 1124 | 64.06 | 3860.06 | 3671.25 | 188.81 | 3861 | 4.831 | 77.9%
2020-11-17 | 646 | 1003 | 962 | 1088 | 61.18 | 3760.18 | 3568.5 | 191.68 | 3761 | 4.727 | 77.55%
2020-11-18 | 620 | 942 | 887 | 998 | 54.13 | 3501.13 | 3313.5 | 187.63 | 3499 | 4.296 | 79.38% | Moduule Cleaning has been Done in Row-H, inverter no-1 I,J,K, inverter No-2 total moduel clening 1071 |  | 1071
2020-11-19 | 695 | 1084 | 1014 | 1134 | 63.44 | 3990.44 | 3794.25 | 196.19 | 3991 | 4.844 | 80.3% | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 |  | 1044
2020-11-20 | 671 | 1080 | 947 | 1079 | 59.85 | 3836.85 | 3585.75 | 251.1 | 3837 | 4.497 | 83.16% | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026
2020-11-21 | 660 | 993 | 927 | 1028 | 57.49 | 3665.49 | 3474.75 | 190.74 | 3666 | 4.454 | 80.22% | Module Cleaning has been done in Row- I,J,K,L, Inverter no-4 &Tracker 5,6,7 and Row-Q,R,S,T, Inverter No- 3 & total module cleaning-1020 |  | 1020
2020-11-22 | 681 | 1043 | 978 | 1099 | 63.87 | 3864.87 | 3685.5 | 179.37 | 3865 | 4.763 | 79.09%
2020-11-23 | 665 | 1034 | 988 | 1119 | 64.18 | 3870.18 | 3678 | 192.18 | 3871 | 4.862 | 77.6% | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 |  | 1050
2020-11-24 | 680 | 1083 | 1018 | 1119 | 67.4 | 3967.4 | 3766.5 | 200.9 | 3968 | 4.903 | 78.88% | Module Cleaning has been done in Row-I,J,K,L Inverter No-2, total module cleaning-1092 &Today Preventive maintenance of transformer No-3&4 has been done. |  | 1092
2020-11-25 | 509 | 726 | 686 | 741 | 36.94 | 2698.94 | 2537.25 | 161.69 | 2699 | 2.783 | 94.52% | Module Cleaning has been done in Row- A,B,C,D,E,F,G,H, Inverter No- 1 total module cleaning-1113 |  | 1113
2020-11-26 | 595 | 877 | 826 | 907 | 48.66 | 3253.66 | 3077.25 | 176.41 | 3254 | 3.808 | 83.29% | Today we are installed new pyranometer SP-110 at wather Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4 total module cleaning-882 |  | 882
2020-11-27 | 680 | 1028 | 958 | 1099 | 61.31 | 3826.31 | 3630 | 196.31 | 3827 | 4.56 | 81.8% | Today we are cleaning all inverter Door filters. & Today preventive maintenance of transformer No-2 has been done.& Module Cleaning has been done in Row- H,I,J,K,L Inverter No-4 & Tracker 1,2,3, total module cleaning - 924 |  | 924
2020-11-28 | 716 | 1094 | 1033 | 1199 | 70.08 | 4112.08 | 3909.75 | 202.33 | 4113 | 4.904 | 81.74% | Modul Cleaning has been done in Row-N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 840 |  | 840
2020-11-29 | 660 | 1023 | 968 | 1134 | 64.8 | 3849.8 | 3654.75 | 195.05 | 3850 | 4.598 | 81.61%
2020-11-30 | 630 | 978 | 932 | 1089 | 62.1 | 3691.1 | 3506.25 | 184.85 | 3692 | 4.667 | 77.1%
2020-12-01 | 41 | 45 | 46 | 56 | 4.889 | 192.889 | 102 | 90.889 | 193 | 4.903 | 3.837% | Grid failure from 08:53 to 17:20.
2020-12-02 | 660 | 1033 | 988 | 1139 | 58.64 | 3878.64 | 3675.75 | 202.89 | 3879 | 4.919 | 76.86% | Modul Cleaning has been done in Row-M,N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 1092 & Grid failure from 8:59 to 9:03. |  | 1092
2020-12-03 | 660 | 1059 | 1003 | 1144 | 69.29 | 3935.29 | 3733.5 | 201.79 | 3936 | 4.961 | 77.33% | Modul Cleaning has been done in Row-I,J,K,L Inverter No-3 total module cleaning - 1092 & Grid failure from 9:12 to 9:15. |  | 1092
2020-12-04 | 650 | 1033 | 962 | 1088 | 65.37 | 3798.37 | 3600.75 | 197.62 | 3829 | 4.774 | 78.17% | Module Cleaning has been done in Row- A,B,C,D,E,F,G,H Inverter No- 1 & A,B,C Inverter No - 4, total module cleaning-1401 & Grid failure from 3:15 to 3:18 |  | 1401
2020-12-05 | 620 | 963 | 903 | 983 | 58.37 | 3527.37 | 3339.75 | 187.62 | 3528 | 4.592 | 74.88% | Modul Cleaning has been done in Row-D,E,F,G,H Inverter No-4 total module cleaning - 900 |  | 900
2020-12-06 | 636 | 978 | 917 | 1008 | 60.37 | 3599.37 | 3417.75 | 181.62 | 3600 | 4.672 | 75.1% | Modul Cleaning has been done in Row-I,J,K,L Inverter No-4 & S,t inverter no-3 total module cleaning - 750 & Today 1 module damage by inverter No-4 this film side Row No-L module No-37 & A side (S.No-NPC10BY1110756). |  | 750
2020-12-07 | 639 | 987 | 922 | 1064 | 61.62 | 3673.62 | 3485.25 | 188.37 | 3674 | 4.711 | 76.01%
2020-12-08 | 641 | 968 | 913 | 1048 | 61.44 | 3631.44 | 3429.75 | 201.69 | 3632 | 4.653 | 76.08% | Modul Cleaning has been done in Row-M,N,O,P,Q,R,S Inverter No-3 total module cleaning - 1008 & Today the transformer no-3,4 atending oil leakage both L.V and H.V side.& Today we are chang the new-24 MC4 conecter In the inverter No-3 AJB No-16,18. |  | 1008
2020-12-09 | 635 | 978 | 917 | 1049 | 61.27 | 3640.27 | 3447 | 193.27 | 3641 | 4.553 | 77.94% | Today we are chang the new-58 MC4 conecter In the inverter No-3 AJB No-13,14,17.& inverter No-2 AJB No-12.& Module cleaning has been done in Row-I,J,K,L inverter no-2 total module cleaning -1092.
2020-12-10 | 610 | 927 | 877 | 992 | 56.48 | 3462.48 | 3273.75 | 188.73 | 3463 | 4.292 | 78.64% | Today we are chang the new-81 MC4 conecter In the inverter No-2 AJB No-9,10,11.& inverter No-1 AJB No-1,2,3,4,5,6,7,8.& Module cleaning has been done in Row-A,B,C,D,E,F,G,H inverter no-1 total module cleaning -1113. |  | 1113
2020-12-11 | 181 | 227 | 217 | 232 | 7.28 | 864.28 | 732 | 132.28 | 865 | 8.22 | 10.26%
2020-12-12 | 519 | 741 | 670 | 782 | 36.97 | 2748.97 | 2589 | 159.97 | 2749 | 3.255 | 82.31%
2020-12-13 | 555 | 797 | 756 | 816 | 43.1 | 2967.1 | 2794.5 | 172.6 | 2968 | 3.426 | 84.44%
2020-12-14 | 479 | 675 | 650 | 691 | 31.69 | 2526.69 | 2361.75 | 164.94 | 2527 | 2.722 | 90.48% | Modul Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning - 1566 |  | 1566
2020-12-15 | 509 | 731 | 691 | 761 | 36.91 | 2728.91 | 2580 | 148.91 | 2729 | 3.264 | 81.49% | Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 & Grid failure from 05:29 to 5:43 & today we are change the new ( 61 ) MC4 conecter in the inverter no-4 AJB NO-19,20,21,22,23,24 |  | 1440
2020-12-16 | 625 | 922 | 877 | 967 | 49.73 | 3440.73 | 3258 | 182.73 | 3441 | 4.092 | 81.96% | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533
2020-12-17 | 670 | 1008 | 947 | 1059 | 58.48 | 3742.48 | 3559.5 | 182.98 | 3743 | 4.404 | 82.84% | Module Cleaning has been done in Row- A,B,C,D,E,F,Inverter No- 1 &,O,P,Q,R inverter No-3 total module cleaning-1218 |  | 1218
2020-12-18 | 690 | 1039 | 978 | 1109 | 65.48 | 3881.48 | 3680.25 | 201.23 | 3882 | 4.591 | 82.41% | Modul Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning - 1566 |  | 1566
2020-12-19 | 686 | 1048 | 993 | 1147 | 67.24 | 3941.24 | 3741 | 200.24 | 3942 | 4.608 | 83.38% | Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 |  | 1440
2020-12-20 | 675 | 1023 | 978 | 1111 | 64.61 | 3851.61 | 3667.5 | 184.11 | 3852 | 4.552 | 82.48%
2020-12-21 | 695 | 1109 | 1038 | 1194 | 72.82 | 4108.82 | 3906 | 202.82 | 4109 | 5.151 | 77.75% | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533
2020-12-22 | 676 | 1043 | 973 | 1109 | 66.91 | 3867.91 | 3668.25 | 199.66 | 3868 | 4.851 | 77.72% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C,D,E,F Inverter No-4 total module cleaning - 1464 |  | 1464
2020-12-23 | 661 | 1008 | 932 | 1069 | 63.08 | 3733.08 | 3544.5 | 188.58 | 3733 | 4.637 | 78.46% | Module Cleaning has been done in Row-G,H,I,J,K,L, Tracker 1,2,3, and Row-Q,R,S,T, Inverter No- 4 and 3 total module cleaning-1416 |  | 1416
2020-12-24 | 654 | 1003 | 948 | 1058 | 63.1 | 3726.1 | 3539.25 | 186.85 | 3727 | 4.561 | 79.64% | Module Cleaning has been done in Row-M,N,O,P and Row-J,K,L Inverter No-3 and 2 total module cleaning-1617 |  | 1617
2020-12-25 | 646 | 978 | 917 | 1013 | 60.17 | 3614.17 | 3425.25 | 188.92 | 3615 | 4.068 | 86.61% | Module Cleaning has been done in Row-I and Row-A,B,C,D,E,F,G,H Inverter No-2 and 1 total module cleaning-1386 |  | 1386
2020-12-26 | 620 | 932 | 872 | 963 | 56.02 | 3443.02 | 3261 | 182.02 | 3444 | 4.19 | 80.11% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning-1566 |  | 1566
2020-12-27 | 645 | 988 | 923 | 1028 | 61.04 | 3645.04 | 3474 | 171.04 | 3646 | 4.536 | 78.34% | Grid failure from 11:26 to 11:32.
2020-12-28 | 716 | 1099 | 1038 | 1175 | 70.9 | 4098.9 | 3884.25 | 214.65 | 4099 | 4.913 | 81.32% | Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 |  | 1440
2020-12-29 | 660 | 1044 | 978 | 1098 | 66.83 | 3846.83 | 3645.75 | 201.08 | 3847 | 3.054 | 122.8% | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533
2020-12-30 | 716 | 1108 | 1023 | 1155 | 69.52 | 4071.52 | 3873.75 | 197.77 | 4072 | 4.648 | 85.39% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C,D,E,F Inverter No-4 total module cleaning - 1464 |  | 1464
2020-12-31 | 595 | 872 | 831 | 882 | 48.61 | 3228.61 | 3045.75 | 182.86 | 3229 | 3.719 | 84.62% | Module Cleaning has been done in Row-G,H,I,J,K,L, Tracker 1,2,3, and Row-Q,R,S,T, Inverter No- 4 and 3 total module cleaning-1416 & Today 1 module damage by monky, Inverter No-4 thin film side, Row No-I module No-92 & B side (S.No-NPC10BY1112877). |  | 1416
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
Note on K94: Internet Failure
Note on K95: Internet Failure
Note on K96: Internet Failure
Note on K97: Internet Failure
Note on K98: Internet Failure
Note on K99: Internet Failure
Note on K100: Internet Failure
Note on K101: Internet Failure
Note on K102: Internet Failure
Note on K103: Internet Failure
Note on K104: Internet Failure
Note on K105: Internet Failure
Note on K106: Internet Failure
Note on K107: Internet Failure
Note on K108: Internet Failure
Note on K109: Internet Failure
Note on K110: Internet Failure
Note on K111: Internet Failure
Note on K112: Internet Failure
Note on K113: Internet Failure
Note on K114: Internet Failure
Note on K115: Internet Failure
Note on K116: Internet Failure
Note on K117: Internet Failure
Note on K118: Internet Failure
Note on K119: Internet Failure
Note on K120: Internet Failure
Note on K121: Internet Failure
Note on K122: Internet Failure
Note on K123: Internet Failure
Note on K124: Internet Failure
Note on K125: Internet Failure
Note on K126: Internet Failure
Note on K127: Internet Failure
Note on K128: Internet Failure
Note on K129: Internet Failure
Note on K130: Internet Failure
Note on K131: Internet Failure
Note on K132: Internet Failure
Note on K133: Internet Failure
Note on K134: Internet Failure
Note on K135: Internet Failure
Note on K136: Internet Failure
Note on K137: Internet Failure
Note on K138: Internet Failure
Note on K139: Internet Failure
Note on K140: Internet Failure
Note on K141: Internet Failure
Note on K142: Internet Failure
Note on K143: Internet Failure
Note on K144: Internet Failure
Note on K145: Internet Failure
Note on K146: Internet Failure
Note on K147: Internet Failure
Note on K148: Internet Failure
Note on K149: Internet Failure
Note on K150: Internet Failure
Note on K151: Internet Failure
Note on K152: Internet Failure
Note on K153: Internet Failure
Note on K154: Internet Failure
Note on K155: Internet Failure
Note on K156: Internet Failure
Note on K157: Internet Failure
Note on K158: Internet Failure
Note on K159: Internet Failure
Note on K160: Internet Failure
Note on K161: Internet Failure
Note on B162: Author: REC Module production low due to module manufacturing problem (Snail trail)
Note on K162: Internet Failure
Note on K163: Internet Failure
Note on K164: Internet Failure
Note on K165: Internet Failure
Note on K166: Internet Failure
Note on K167: Internet Failure
Note on K168: Internet Failure
Note on K169: Internet Failure
Note on K170: Internet Failure
Note on K171: Internet Failure
Note on K172: Internet Failure
Note on K173: Internet Failure
Note on K174: Internet Failure
Note on K175: Internet Failure
Note on K176: Internet Failure
Note on K177: Internet Failure
Note on K178: Internet Failure
Note on K179: Internet Failure
Note on K180: Internet Failure
Note on K181: Internet Failure
Note on K182: Internet Failure
Note on K183: Internet Failure
Note on K184: Internet Failure
Note on K185: Internet Failure
Note on K186: Internet Failure
Note on K187: Internet Failure
Note on K188: Internet Failure
Note on K189: Internet Failure
Note on L259: Author: Grid Failure From-09:33 to 16:48

## 2021
Project Name |  | PDPU-SEIPL, Gujarat 2010 |  |  |  |  | Generation of 2021
Project Number |  | IN-10-0061
Capacity |  | 1026 KW
PDPU
[6 empty] | Total Generation (KWH) | (ABT Meter) Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%)(Total Genertaion /1026*insolation) | Any Issues/Problems Observed | WO# | Total NO- Of Clean Modules
Inverter generation (KWH)
Date | 1104500527(250KW) | 1104500529(250KW) | 9175000042(250KW) | 9170301408(250KW) | 2100570073/ 2100567820/ 2100567898 (26KW)
2021-01-01 | 514 | 746 | 721 | 756 | 37.83 | 2774.83 | 2605.5 | 169.33 | 2775 | 3.299 | 81.98% | Module Cleaning has been done in Row-M,N,O,P and Row-J,K,L Inverter No-3 and 2 total module cleaning-1617 |  | 1617
2021-01-02 | 498 | 721 | 681 | 730 | 36.27 | 2666.27 | 2504.25 | 162.02 | 2667 | 3.06 | 84.95% | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 |  | 1458
2021-01-03 | 590 | 882 | 831 | 918 | 51.27 | 3272.27 | 3099 | 173.27 | 3273 | 3.936 | 81.05%
2021-01-04 | 504 | 716 | 685 | 725 | 36.5 | 2666.5 | 2506.5 | 160 | 2667 | 3.228 | 80.53% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning-1566 |  | 1566
2021-01-05 | 544 | 786 | 751 | 787 | 41.5 | 2909.5 | 2730 | 179.5 | 2910 | 3.487 | 81.34% | Today we are cleaning all inverter Door filters. & Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 & Today we are chang the new 1 MC4 conecter in the inverter no-1 - AJB-No-1. |  | 1440
2021-01-06 | 661 | 1023 | 967 | 1068 | 62.39 | 3781.39 | 3597 | 184.39 | 3782 | 4.555 | 80.93% | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533
2021-01-07 | 221 | 312 | 298 | 313 | 16.25 | 1160.25 | 1046.25 | 114 | 1161 | 3.304 | 34.25% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C Inverter No-4 total module cleaning - 960 |  | 960
2021-01-08 | 384 | 520 | 494 | 524 | 21.7 | 1943.7 | 1787.25 | 156.45 | 1944 | 2.216 | 85.5% | Module Cleaning has been done in Row-D,E,F,G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1626 & Today we are found 1 MC4 connector Burn in Invertor No-4 AJB No-6 string No-4 --tive site. we replaced 1 MC4 connector and started the strings. |  | 1626
2021-01-09 | 493 | 710 | 690 | 746 | 33.29 | 2672.29 | 2510.25 | 162.04 | 2673 | 3.106 | 83.88% | Module Cleaning has been done in Row-L Inverter No-2 & Row-M,N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 1344 & Today we are found 1 MC4 connector Burn in Invertor No-3 AJB No- string No-2 ++tive site we replaced all 1 MC4 connector and started the strings. |  | 1344
2021-01-10 | 509 | 752 | 711 | 817 | 39.38 | 2828.38 | 2667 | 161.38 | 2829 | 3.089 | 89.26% | Grid failure from -10:15 to 10:22 & 11:32 to 11:47 & 01:51 to 01:59.
2021-01-11 | 656 | 1002 | 953 | 1088 | 58.74 | 3757.74 | 3567.75 | 189.99 | 3758 | 4.046 | 90.53% | Module Cleaning has been done in Row-I,J,K Inverter No-2 & Row-F,G,H Inverter No-1 total module cleaning - 1470 & Today we are found 1 MC4 connector Burn in Invertor No-2 AJB No-5 string No-1 ++tive site we replaced all 1 MC4 connector and started the strings. |  | 1470
2021-01-12 | 695 | 1059 | 987 | 1134 | 63.22 | 3938.22 | 3739.5 | 198.72 | 3939 | 4.697 | 81.74% | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 & Row-A,B,C,D,E,F,G, Inverter No-4 total module cleaning - 1473 & Today we are Recaind ABB -Wavlaty door fan -nos-3 and change the new fan in inverter no-3,4 |  | 1473
2021-01-13 | 736 | 1144 | 1069 | 1230 | 72.15 | 4251.15 | 4053 | 198.15 | 4252 | 5.111 | 81.08% | Module Cleaning has been done in Row-H,I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-P,Q,R,S,T inverter No-3 total module cleaning -1365 |  | 1365
2021-01-14 | 696 | 1109 | 1038 | 1205 | 71.41 | 4119.41 | 3927 | 192.41 | 4120 | 5.3 | 75.77% | Grid failure from -03:54 to 04:32
2021-01-15 | 650 | 1013 | 958 | 1088 | 62.64 | 3771.64 | 3573 | 198.64 | 3772 | 4.552 | 80.76%
2021-01-16 | 635 | 983 | 935 | 1029 | 61.95 | 3643.95 | 3465.75 | 178.2 | 3644 | 4.464 | 79.56% | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Row-K,L, Inverter No-2 total module cleaning - 1617 |  | 1617
2021-01-17 | 590 | 902 | 884 | 917 | 53.06 | 3346.06 | 3161.25 | 184.81 | 3347 | 3.891 | 83.84%
2021-01-18 | 599 | 918 | 867 | 912 | 53.99 | 3349.99 | 3166.5 | 183.49 | 3350 | 4.303 | 75.88% | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-C,D,E,F,G,H Inverter No-1 total module cleaning - 1575 & Grid failure from -02:37 to 2:54 |  | 1575
2021-01-19 | 611 | 922 | 862 | 907 | 52.15 | 3354.15 | 3174 | 180.15 | 3355 | 4.128 | 79.21% | Module Cleaning has been done in Row-A,B & Row-A,B,C,D,E,F,G,H,I,Inverter No-1&4 total module cleaning-1491 |  | 1491
2021-01-20 | 619 | 922 | 882 | 963 | 52.93 | 3438.93 | 3258 | 180.93 | 3439 | 4.168 | 80.42% | Module Cleaning has been done in Row-J,K,L Inverter No-4 & Trecker 1,2,3 & Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1620 |  | 1620
2021-01-21 | 711 | 1134 | 1074 | 1210 | 73.15 | 4202.15 | 3999 | 203.15 | 4203 | 5.056 | 81.02% | Module Cleaning has been done in Row-I,J,K,L Inverter No-2 & Row-G,H inverter No-1 total module cleaning -1533 |  | 1533
2021-01-22 | 670 | 1049 | 1003 | 1099 | 66.17 | 3887.17 | 3684.75 | 202.42 | 3888 | 4.835 | 78.38% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E,F inverter No-4 total module cleaning -1464 & Grid failure from 8:29 to 8:42 |  | 1464
2021-01-23 | 635 | 977 | 917 | 1053 | 56.63 | 3638.63 | 3450 | 188.63 | 3639 | 4.399 | 80.63% | Module Cleaning has been done in Row-G,H,I,J,K,L & Inverter No-4 & Trecker 1,2,3 & Row-Q,R,S,T inverter No-3 total module cleaning -1416 & Grid failure from 6:30 to 8:21 & Grid failure from 10:37 to 10:42 |  | 1416
2021-01-24 | 671 | 1003 | 968 | 1074 | 60.38 | 3776.38 | 3598.5 | 177.88 | 3777 | 4.524 | 81.37%
2021-01-25 | 675 | 1024 | 1003 | 1088 | 65.66 | 3855.66 | 3659.25 | 196.41 | 3856 | 4.87 | 77.17% | Module Cleaning has been done in Row-M,N,O,PInverter No-3 & Row-J,K,L, Inverter No-2 total module cleaning - 1617 & Today we are change the new (2) mc4 conecter in the inverter no-1 AJB No-6 & Grid failure from 11:24 to 11:54 & Today Replaced the D.C.15 Amp fuse link of the string-03 --tive line in AJB-123 of The Inverter-4 during the period of 11:30 to 11:35. |  | 1617
2021-01-26 | 767 | 1194 | 1144 | 1230 | 73.16 | 4408.16 | 4194 | 214.16 | 4409 | 5.026 | 85.5% | Module Cleaning has been done in Row-I,Inverter No-2 & Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning - 1386 |  | 1386
2021-01-27 | 775 | 1215 | 1149 | 1265 | 77.09 | 4481.09 | 4263 | 218.09 | 4482 | 5.295 | 82.5% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning - 1386 Today Replaced the D.C.12 Amp fuse link of the string-08 --tive line in AJB-110 of The Inverter-2during the period of 10:30 to 10:35. |  | 1386
2021-01-28 | 757 | 1174 | 1109 | 1235 | 73.07 | 4348.07 | 4136.25 | 211.82 | 4349 | 5.118 | 82.82%
2021-01-29 | 766 | 1210 | 1134 | 1260 | 76.39 | 4446.39 | 4231.5 | 214.89 | 4447 | 5.276 | 82.15%
2021-01-30 | 771 | 1210 | 1154 | 1295 | 80.31 | 4510.31 | 4295.25 | 215.06 | 4511 | 5.319 | 82.66% | Module Cleaning has been done in Row- J,K,L Inverter No-4 & Tracker 1,2,3, & Row-N,O,P,Q,R,S,T, Inverter No- 3 total module cleaning-1368 & Grid failure from 01:57 to 02:01. |  | 1368
2021-01-31 | 751 | 1189 | 1140 | 1270 | 78.92 | 4428.92 | 4232.25 | 196.67 | 4429 | 5.418 | 79.67%
2021-02-01 | 716 | 1139 | 942 | 1215 | 74.09 | 4086.09 | 3884.25 | 201.84 | 4087 | 5.253 | 75.83% | Module Cleaning has been done in Row-M,N, Inverter No-3 & Row-J,K,L, Inverter No-2 total module cleaning - 1281 |  | 1281
2021-02-02 | 690 | 1089 | 1028 | 1104 | 66.74 | 3977.74 | 3786.75 | 190.99 | 3978 | 4.934 | 78.58% | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 & Today we are found 7 MC4 conecter burn in inverter no-4 AJB NO-19 string no-2 ++ive site & AJB NO-19 string no-4 ++ive site & AJB NO-20 string no-2 --ive site we replaced all-7 MC4 connector and started the string. |  | 1458
2021-02-03 | 620 | 927 | 887 | 938 | 50.84 | 3422.84 | 3242.25 | 180.59 | 3423 | 4.118 | 81.02% | Module cleaning has been done in Row-B,C,D,E,F,G,H,I Inverter no-4 total module cleaning -1314 |  | 1314
2021-02-04 | 650 | 988 | 943 | 1023 | 57.54 | 3661.54 | 3474.75 | 186.79 | 3662 | 4.391 | 81.28% | Module Cleaning has been done in Row-J,K,L Inverter No-4 & Trecker 1,2,3 & Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1620 |  | 1620
2021-02-05 | 731 | 1139 | 1088 | 1171 | 68.95 | 4197.95 | 4002 | 195.95 | 4221 | 4.977 | 82.66% | Module Cleaning has been done in Row-I,J,K,L Inverter No-2 & Row-G,H inverter No-1 total module cleaning -1533 & Today we are found 3 MC4 connecter burn in inverter no-2 AJB NO-108 string no-8 ++ive site & inverter NO-1 AJB NO-103 string no-5,6 ++ive site we replaced all-3 MC4 connector and started the string. |  | 1533
2021-02-06 | 766 | 1205 | 1140 | 1253 | 75.37 | 4439.37 | 4230 | 209.37 | 4440 | 5.172 | 83.67% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E,F inverter No-4 total module cleaning -1464 |  | 1464
2021-02-07 | 796 | 1255 | 1184 | 1321 | 80.9 | 4636.9 | 4425 | 211.9 | 4637 | 5.277 | 85.65%
2021-02-08 | 782 | 1244 | 1174 | 1335 | 81.18 | 4616.18 | 4401.75 | 214.43 | 4617 | 5.465 | 82.34% | Module Cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-Q,R,S,T inverter No-3 total module cleaning -1416 & Today we are found 1MC4 connecter burn in inverter no-1 AJB NO-102 string no-8 ++ive site we replaced 1MC4 connector and started the string. |  | 1416
2021-02-09 | 700 | 1079 | 1039 | 1144 | 67.25 | 4029.25 | 3841.5 | 187.75 | 4030 | 4.851 | 80.97% | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 & Row-J,K,L, inverter No-2 total module cleaning -1617 |  | 1617
2021-02-10 | 741 | 1144 | 1088 | 1190 | 69.6 | 4232.6 | 4026.75 | 205.85 | 4233 | 4.708 | 87.63% | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 |  | 1458
2021-02-11 | 650 | 984 | 943 | 1023 | 55.01 | 3655.01 | 3480 | 175.01 | 3656 | 4.336 | 82.18% | Module cleaning has been done in Row-B,C,D,E,F,G,H,I Inverter no-4 total module cleaning -1314 |  | 1314
2021-02-12 | 681 | 1048 | 993 | 1084 | 62.93 | 3868.93 | 3687.75 | 181.18 | 3869 | 4.64 | 81.27% | Module Cleaning has been done in Row-j,k,l Inverter No-4 & Trecker 1,2,3 & total module cleaning -528 |  | 528
2021-02-13 | 655 | 997 | 963 | 1033 | 58.96 | 3706.96 | 3518.25 | 188.71 | 3707 | 4.528 | 79.79% | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1617 |  | 1617
2021-02-14 | 671 | 1054 | 1013 | 1073 | 62.59 | 3873.59 | 3691.5 | 182.09 | 3874 | 4.726 | 79.89%
2021-02-15 | 685 | 1033 | 978 | 1064 | 59.18 | 3819.18 | 3636 | 183.18 | 3820 | 4.429 | 84.06% | Module Cleaning has been done in Row-I,j inverter-2 & Row-D,E,F,G,H inverter no-1 total module cleaning-1470 |  | 1470
2021-02-16 | 746 | 1165 | 1098 | 1225 | 71.35 | 4305.35 | 4105.5 | 199.85 | 4306 | 4.849 | 86.55% | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F,G inverter No-4 total module cleaning -1200 |  | 1200
2021-02-17 | 731 | 1103 | 1039 | 1174 | 66.71 | 4113.71 | 3917.25 | 196.46 | 4114 | 4.846 | 82.74% | Module Cleaning has been done in Row-I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-R,S,T inverter no-3 total module cleaning -1092
2021-02-18 | 726 | 1089 | 1048 | 1169 | 66.48 | 4098.48 | 3892.5 | 205.98 | 4099 | 4.693 | 85.13% | Module Cleaning has been done in Row-M,N,O,P,Q Inverter No-3 & Row-K,L Inverter No-2 total module cleaning - 1449 |  | 1449
2021-02-19 | 761 | 1179 | 1104 | 1246 | 72.23 | 4362.23 | 4156.5 | 205.73 | 4363 | 4.92 | 86.43% | Today we are change the new (5) mc4 conecter in the inverter no-3 AJB No-116. & today we are found (2)MC4 connector burn in inverter no-3 AJB NO-116 string NO-2 ++ive site &--ive site we replaced all-2 MC4 connector & started the string.& module cleaning has been done in Row-I,J inverter no-2 & Row-D,E,F,G,H, inverter no-1 total module cleaning -1470 |  | 1470
2021-02-20 | 796 | 1241 | 1164 | 1325 | 78.01 | 4604.01 | 4378.5 | 225.51 | 4605 | 5.467 | 82.1% | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F Inverter No-4 total module cleaning - 1002 |  | 1002
2021-02-21 | 761 | 1204 | 1144 | 1270 | 74.83 | 4453.83 | 4269 | 184.83 | 4454 | 5.333 | 81.4%
2021-02-22 | 716 | 1109 | 1049 | 1180 | 66.63 | 4120.63 | 3909 | 211.63 | 4121 | 5.083 | 79.02% | Module Cleaning has been done in Row-G,H,I,J Inverter No-4 total module cleaning - 774 |  | 774
2021-02-23 | 725 | 1129 | 1083 | 1209 | 68.16 | 4214.16 | 4005 | 209.16 | 4215 | 5.057 | 81.24% | Module Cleaning has been done in Row-k,l Inverter No-4 & Trecker 1,2,3 & ROW-P,Q,R,S,T inverter no-3 total module cleaning -789 |  | 789
2021-02-24 | 716 | 1104 | 1084 | 1195 | 67.93 | 4166.93 | 3969.75 | 197.18 | 4167 | 4.791 | 84.77% | Module Cleaning has been done in Row-M,N,O Inverter No-3 & Row-L inverter no-2 total module cleaning - 903 & Grid failure from -15:19 to 15:23 |  | 903
2021-02-25 | 766 | 1229 | 1184 | 1325 | 75.6 | 4579.6 | 4359 | 220.6 | 4580 | 5.299 | 84.24% | Module Cleaning has been done in Row-I,J,K inverter no-2 total module cleaning - 840 |  | 840
2021-02-26 | 752 | 1190 | 1129 | 1271 | 71.17 | 4413.17 | 4199.25 | 213.92 | 4414 | 5.11 | 84.19% | Module Cleaning has been done in Row-D,E,F,G,H inverter no-1 total module cleaning - 903 |  | 903
2021-02-27 | 755 | 1154 | 1099 | 1244 | 67.79 | 4319.79 | 4131 | 188.79 | 4320 | 5.038 | 83.58% | Module Cleaning has been done in Row-A,B,C inverter no-1 & A,B,C,D,E,F total module cleaning - 1002 |  | 1002
2021-02-28 | 736 | 1129 | 1064 | 1220 | 65.81 | 4214.81 | 4019.25 | 195.56 | 4215 | 5.142 | 79.89% | Today we are faund one module damej in Inverter no-4,AJB No-4,String no-2,module no-3,B-site module serial no-NPC10BY1130277 & Grid failure from -10:04 to 10:15
2021-03-01 | 787 | 1215 | 1144 | 1336 | 73.01 | 4555.01 | 4332.75 | 222.26 | 4556 | 5.541 | 80.14% | Module Cleaning has been done in Row-I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1122 |  | 1122
2021-03-02 | 791 | 1235 | 1189 | 1376 | 82.04 | 4673.04 | 4451.25 | 221.79 | 4674 | 5.567 | 81.83% | Today replced the 12-Amp D.C Fuse link of the string-7 in AJB-117 of the inverter no-3 during the poried-09:50 to 10:10 Module Cleaning has been done in Row-N,O,P,Q,R,S,T Inverter no-3 total module cleaning -840 |  | 840
2021-03-03 | 741 | 1189 | 1175 | 1285 | 78.93 | 4468.93 | 4256.25 | 212.68 | 4469 | 5.046 | 86.32% | Module Cleaning has been done in Row-M, inverter no-3 & Row- J,K,L inverter no-2 total module cleaning total module cleaning - 1071 & Grid failure from-11:05 to 10:09 & Grid failure from-11:34 to 11:37 & Grid failure from-03:04 to 03:33 & Today we are found 1MC4 connecter burn in inverter no-1 AJB NO-105 string no-8 --ive site we replaced 1MC4 connector and started the string. |  | 1071
2021-03-04 | 771 | 1225 | 1164 | 1296 | 76.37 | 4532.37 | 4322.25 | 210.12 | 4533 | 5.264 | 83.93% | Module Cleaning has been done in Row-,I inverter no-3 & Row-D,E,F,G,H inverter no-1 total module cleaning - 1176 & Grid failure from-16:43 to 16:49 & Grid failure from-17:32 to 17:54 |  | 1176
2021-03-05 | 776 | 1200 | 1144 | 1295 | 74.29 | 4489.29 | 4276.5 | 212.79 | 4490 | 4.792 | 91.32% | Module Cleaning has been done in Row-A,B,C inverter no-1 & Row-A,B,C,D,E,F inverter no-4 total module cleaning - 1002 |  | 1002
2021-03-06 | 751 | 1159 | 1104 | 1280 | 71.01 | 4365.01 | 4158.75 | 206.26 | 4366 | 5.126 | 83.02% | Module Cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1122 |  | 1122
2021-03-07 | 777 | 1204 | 1149 | 1346 | 79.26 | 4555.26 | 4346.25 | 209.01 | 4556 | 5.395 | 82.31%
2021-03-08 | 756 | 1167 | 1149 | 1295 | 74.98 | 4441.98 | 4236 | 205.98 | 4442 | 4.951 | 87.45% | Grid failure from-07:19 to 07:25 & Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, inverter no-3 & Row-L,inverter no-2 total module cleaning - 1344. |  | 1344
2021-03-09 | 771 | 1233 | 1185 | 1331 | 77.65 | 4597.65 | 4365.75 | 231.9 | 4598 | 5.437 | 82.43% | Module Cleaning has been done in Row-I,J,K inverter no-2 & Row-G,H inverter no-1 total module cleaning - 1281 |  | 1281
2021-03-10 | 766 | 1199 | 1139 | 1280 | 73.83 | 4457.83 | 4249.5 | 208.33 | 4458 | 5.104 | 85.13%
2021-03-11 | 711 | 1064 | 1013 | 1089 | 61.21 | 3938.21 | 3750 | 188.21 | 3939 | 4.312 | 89.03% | Module Cleaning has been done in Row-A,B,C,D,E,F inverter no-1 & Row-A,B,C,D,E inverter no-4 total module cleaning - 1266 |  | 1266
2021-03-12 | 725 | 1103 | 1048 | 1225 | 63.12 | 4164.12 | 3954 | 210.12 | 4165 | 4.884 | 83.12% | Module Cleaning has been done in Row-F,G,H,I,J,L,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1320 |  | 1320
2021-03-13 | 782 | 1205 | 1175 | 1350 | 78.42 | 4590.42 | 4374 | 216.42 | 4591 | 5.522 | 81.03% | module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, inverter no-3 & Row-L,inverter no-2 total module cleaning - 1344. |  | 1344
2021-03-14 | 770 | 1190 | 1174 | 1321 | 75.39 | 4530.39 | 4326.75 | 203.64 | 4531 | 5.186 | 85.16%
2021-03-15 | 766 | 1194 | 1149 | 1290 | 73.62 | 4472.62 | 4266.75 | 205.87 | 4473 | 5.294 | 82.35% | Module cleaning has been done in Row-I,J,k inverter no-2 & Row-F,G,H, inverter no-1 total module cleaning -1470 & Grid failure from-09:42 to 09:46 & Grid failure from-11:01 to 11:17 |  | 1470
2021-03-16 | 727 | 1114 | 1064 | 1184 | 65.33 | 4154.33 | 3944.25 | 210.08 | 4155 | 5.038 | 80.38%
2021-03-17 | 746 | 1139 | 1083 | 1215 | 68 | 4251 | 4042.5 | 208.5 | 4252 | 5.015 | 82.64%
2021-03-18 | 695 | 998 | 958 | 1059 | 56.25 | 3766.25 | 3567.75 | 198.5 | 3767 | 4.488 | 81.81% | Module cleaning has been done in Row- A,B,C,D,E Inverter no-1 & Row-A,B,C,D Inverter No-4 total module cleaning -915 |  | 915
2021-03-19 | 696 | 1024 | 973 | 1119 | 56.94 | 3868.94 | 3681.75 | 187.19 | 3979 | 4.591 | 84.47% | Module cleaning has been done in Row- E,F,G,H,I,J,K Inverter No-4 total module cleaning -1296 |  | 1296
2021-03-20 | 685 | 1007 | 983 | 1124 | 59.78 | 3858.78 | 3657.75 | 201.03 | 3859 | 4.607 | 81.64% | Module Cleaning has been done in Row-L, Inverter No-4 & Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Trecker 1,2,3 total module cleaning -1278 |  | 1278
2021-03-21 | 701 | 1038 | 1053 | 1174 | 64.95 | 4030.95 | 3837 | 193.95 | 4031 | 4.883 | 80.46%
2021-03-22 | 705 | 1089 | 1053 | 1190 | 66.33 | 4103.33 | 3893.25 | 210.08 | 4104 | 4.894 | 81.73% | Module cleaning has been done in Row- I,J,K,L, Inverter No-2 & Row-H, Inverter No-1 total module cleaning -1323 |  | 1323
2021-03-23 | 711 | 1114 | 1039 | 1169 | 66.06 | 4099.06 | 3894 | 205.06 | 4100 | 4.895 | 81.64%
2021-03-24 | 756 | 1149 | 1083 | 1230 | 67.48 | 4285.48 | 4066.5 | 218.98 | 4286 | 5.117 | 81.64% | Module cleaning has been done in Row- A,B,C,D,E,F,G Inverter No-1 & Row-A,B,C,D Inverter No-4 total module cleaning -1314 |  | 1314
2021-03-25 | 837 | 1250 | 1185 | 1386 | 77.36 | 4735.36 | 4504.5 | 230.86 | 4736 | 5.53 | 83.47% | Module cleaning has been done in Row- E,F,G,H,I Inverter No-4 total module cleaning -954 |  | 954
2021-03-26 | 816 | 1225 | 1169 | 1396 | 79.35 | 4685.35 | 4464.75 | 220.6 | 4686 | 4.95 | 92.27% | Module Cleaning has been done in Row-J,K,L, Inverter No-4 & Trecker 1,2,3 Row-M,N,O,P,Q,R,S,T, Inverter No-3 & total module cleaning -1620 |  | 1620
2021-03-27 | 726 | 1124 | 1084 | 1225 | 72.38 | 4231.38 | 4026.75 | 204.63 | 4232 | 5.036 | 81.91% | Module cleaning has been done in Row- I,J,K,L Inverter No-2 total module cleaning -1092 & Grid failure from-08:22 to 08:25 & Grid failure from-12:09 to 12:36 |  | 1092
2021-03-28 | 781 | 1230 | 1169 | 1325 | 77.45 | 4582.45 | 4362.75 | 219.7 | 4583 | 5.611 | 79.61%
2021-03-29 | 796 | 1250 | 1185 | 1356 | 79.23 | 4666.23 | 4448.25 | 217.98 | 4667 | 5.579 | 81.53%
2021-03-30 | 802 | 1245 | 1184 | 1376 | 79.93 | 4686.93 | 4464.75 | 222.18 | 4687 | 5.481 | 83.35%
2021-03-31 | 766 | 1129 | 1074 | 1245 | 65.2 | 4279.2 | 4060.5 | 218.7 | 4280 | 4.879 | 85.5% | Module cleaning has been done in Row- A,B,C,D,E,F,G,H Inverter No-1 & Row-A,B,C, Inverter No-4 total module cleaning -1401 |  | 1401
2021-04-01 | 827 | 1240 | 1179 | 1351 | 79.37 | 4676.37 | 4457.25 | 219.12 | 4677 | 5.505 | 82.81% | Today we are cleaning all inverter Door filters.
2021-04-02 | 811 | 1219 | 1159 | 1350 | 78.46 | 4617.46 | 4403.25 | 214.21 | 4618 | 5.392 | 83.48% | Module cleaning has been done in Row- D,E,F,G,H,I,JInverter No-4 total module cleaning -1278 |  | 1278
2021-04-03 | 787 | 1175 | 1124 | 1366 | 75.36 | 4527.36 | 4306.5 | 220.86 | 4528 | 5.42 | 81.43% | Module Cleaning has been done in Row-K,L, Inverter No-4 & Trecker 1,2,3 Row-P,Q,R,S,T, Inverter No-3 & total module cleaning -789 |  | 789
2021-04-04 | 710 | 1053 | 1028 | 1225 | 65.59 | 4081.59 | 3900 | 181.59 | 4082 | 5.165 | 77.03% | Grid failure from-16:35 to 17:27 & Grid failure from-17:30 to 17:33 & Grid failure from-17:42 to 17:47
2021-04-05 | 772 | 1149 | 1145 | 1341 | 76.2 | 4483.2 | 4257.75 | 225.45 | 4484 | 5.535 | 78.96% | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -1092 |  | 1092
2021-04-06 | 781 | 1210 | 1179 | 1351 | 78.56 | 4599.56 | 4374 | 225.56 | 4600 | 5.588 | 80.23% | Module cleaning has been done in Row-I,J,K, Inverter No-2 total module cleaning -840 |  | 840
2021-04-07 | 811 | 1265 | 1205 | 1391 | 79.58 | 4751.58 | 4535.25 | 216.33 | 4752 | 5.65 | 81.97% | Module cleaning has been done in Row- L, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -693 |  | 693
2021-04-08 | 786 | 1190 | 1134 | 1295 | 74.43 | 4479.43 | 4257 | 222.43 | 4480 | 5.557 | 78.58% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-1 & Row-A,B,C,D, Inverter No-4 & total module cleaning -1104 |  | 1104
2021-04-09 | 772 | 1144 | 1088 | 1280 | 69.87 | 4353.87 | 4158 | 195.87 | 4354 | 5.369 | 79.04% | Module cleaning has been done in Row-E,F,G,H,I,J,K Inverter No-4 total module cleaning -1134 |  | 1134
2021-04-10 | 766 | 1134 | 1089 | 1296 | 72.02 | 4357.02 | 4141.5 | 215.52 | 4358 | 5.451 | 77.92% | Module Cleaning has been done in Row-K,L, Inverter No-4 & Trecker 1,2,3 Row-O,P,Q,R,S,T, Inverter No-3 & total module cleaning -978 |  | 978
2021-04-11 | 766 | 1149 | 1129 | 1305 | 75.55 | 4424.55 | 4229.25 | 195.3 | 4425 |  | #DIV/0!
2021-04-12 | 740 | 1114 | 1094 | 1245 | 69.58 | 4262.58 | 4052.25 | 210.33 | 4263 |  | % | Today we are chang the new (10) mc4 conecter in the inverter no-1,2,3 AJB no-105,106,107,113 &114 &Module Cleaning has been done in Row-M,N, Inverter No-1 & Row-J,K,L, Inverter No-4 & total module cleaning -1281 |  | 1281
2021-04-13 | 762 | 1154 | 1098 | 1255 | 67.09 | 4336.09 | 4109.25 | 226.84 | 4337 |  | #DIV/0! | Module Cleaning has been done in Row-I, Inverter No-2 & Row-D,E,F,G,H, Inverter No-1 & total module cleaning -1176 |  | 1176
2021-04-14 | 750 | 1124 | 1084 | 1255 | 66.69 | 4279.69 | 4089 | 190.69 | 4280 |  | #DIV/0! | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F,G Inverter No-4 & total module cleaning -1200 |  | 1200
2021-04-15 | 767 | 1134 | 1084 | 1275 | 71.74 | 4331.74 | 4125.75 | 205.99 | 4332 |  | #DIV/0! | Module Cleaning has been done in Row-I, Inverter No-2 & Row-H,I,J,K,L Inverter No-4 & Tracker-1,2,3 total module cleaning -924 |  | 924
2021-04-16 | 791 | 1180 | 1144 | 1381 | 76.61 | 4572.61 | 4347.75 | 224.86 | 4573 |  | #DIV/0! | Module cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -840 |  | 840
2021-04-17 | 776 | 1179 | 1149 | 1361 | 74.32 | 4539.32 | 4325.25 | 214.07 | 4540 |  | #DIV/0! | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L Inverter No-2 total module cleaning -1344 |  | 1344
2021-04-18 | 761 | 1164 | 1129 | 1316 | 72.39 | 4442.39 | 4226.25 | 216.14 | 4443 |  | #DIV/0!
2021-04-19 | 777 | 1185 | 1122 | 1351 | 75.1 | 4510.1 | 4317 | 193.1 | 4511 |  | #DIV/0!
2021-04-20 | 751 | 1134 | 1101 | 1259 | 65.16 | 4310.16 | 4077.75 | 232.41 | 4311 | 5.209 | 80.66% | Module Cleaning has been done in Row-I,J,K,L nverter No-2 & Row-H Inverter No-1 total module cleaning -1323 |  | 1323
2021-04-21 | 786 | 1199 | 1124 | 1306 | 72.37 | 4487.37 | 4261.5 | 225.87 | 4488 | 5.211 | 83.94% | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 total module cleaning -1113 |  | 1113
2021-04-22 | 771 | 1160 | 1099 | 1287 | 70.8 | 4387.8 | 4172.25 | 215.55 | 4388 | 5.134 | 83.3% | Module cleaning has been done in Row-A,B,C,D Inverter No-4 total module cleaning -432 |  | 432
2021-04-23 | 776 | 1159 | 1093 | 1299 | 72.18 | 4399.18 | 4173.75 | 225.43 | 4400 | 5.682 | 75.48%
2021-04-24 | 615 | 847 | 802 | 927 | 42.13 | 3233.13 | 3072 | 161.13 | 3234 | 3.9 | 80.82%
2021-04-25 | 736 | 1109 | 1043 | 1215 | 68.35 | 4171.35 | 3944.25 | 227.1 | 4172 | 5.178 | 78.53%
2021-04-26 | 726 | 1068 | 1008 | 1169 | 65.97 | 4036.97 | 3836.25 | 200.72 | 4037 | 5.348 | 73.57%
2021-04-27 | 695 | 1033 | 973 | 1139 | 61.25 | 3901.25 | 3701.25 | 200 | 3902 | 5.057 | 75.21% | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-4 total module cleaning -990 |  | 990
2021-04-28 | 651 | 968 | 922 | 1124 | 49.15 | 3714.15 | 3545.25 | 168.9 | 3715 | 4.798 | 75.47% | Grid failure from-05:04 to 05:08 & Module Cleaning has been done in Row-H,I,J,K,L Inverter No-4 & Tracker-1,2,3 total module cleaning -924 |  | 924
2021-04-29 | 695 | 991 | 1008 | 1205 | 63.76 | 3962.76 | 3787.5 | 175.26 | 3963 | 4.902 | 78.8% | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -1092 |  | 1092
2121-04-30 | 670 | 1061 | 1008 | 1179 | 61.84 | 3979.84 | 3752.25 | 227.59 | 3980 | 4.885 | 79.41% | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -1533 |  | 1533
2021-05-01 | 585 | 886 | 847 | 993 | 43.52 | 3354.52 | 3141.75 | 212.77 | 3355 | 4.072 | 80.3% | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 total module cleaning -483 & Grid failure from-03:26 to 03:32 |  | 483
2021-05-02 | 741 | 1135 | 1089 | 1285 | 69.82 | 4319.82 | 4114.5 | 205.32 | 4320 | 5.408 | 77.86%
2021-05-03 | 766 | 1154 | 1109 | 1316 | 71.27 | 4416.27 | 4189.5 | 226.77 | 4417 | 5.306 | 81.14% | Grid failure from-07:15 to 07:20
2021-05-04 | 731 | 1124 | 1078 | 1270 | 69.88 | 4272.88 | 4069.5 | 203.38 | 4273 | 5.238 | 79.51%
2021-05-05 | 766 | 1190 | 1139 | 1366 | 78.24 | 4539.24 | 4311 | 228.24 | 4540 | 5.684 | 77.85%
2021-05-06 | 751 | 1168 | 1124 | 1336 | 76.55 | 4455.55 | 4245 | 210.55 | 4456 | 5.618 | 77.31%
2021-05-07 | 736 | 1145 | 1099 | 1315 | 73.51 | 4368.51 | 4152 | 216.51 | 4369 | 5.454 | 78.08%
2021-05-08 | 670 | 1018 | 978 | 1139 | 57.92 | 3862.92 | 3677.25 | 185.67 | 3863 | 5.037 | 74.75%
2021-05-09 | 655 | 988 | 947 | 1197 | 58.69 | 3845.69 | 3562.5 | 283.19 | 3846 | 4.811 | 77.92%
2021-05-10 | 737 | 1134 | 1089 | 1320 | 77.29 | 4357.29 | 4146.75 | 210.54 | 4358 | 5.473 | 77.61%
2021-05-11 | 745 | 1144 | 1099 | 1336 | 77.3 | 4401.3 | 4197.75 | 203.55 | 4402 | 5.593 | 76.71%
2021-05-12 | 746 | 1134 | 1089 | 1346 | 75.28 | 4390.28 | 4164.75 | 225.53 | 4391 | 5.507 | 77.71% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-4 total module cleaning -1188 |  | 1188
2021-05-13 | 731 | 1104 | 1063 | 1361 | 73.36 | 4332.36 | 4128 | 204.36 | 4333 | 5.354 | 78.88% | Module cleaning has been done in Row-I,J,K,L Inverter No-4 tracker 1,2,3 & Row- R,S,T inverter No-3 total module cleaning -893 |  | 893
2021-05-14 | 706 | 1083 | 1094 | 1315 | 72.25 | 4270.25 | 4050 | 220.25 | 4271 | 5.337 | 78% | Module cleaning has been done in Row-M,N,O,P,Q, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1449 |  | 1449
2021-05-15 | 645 | 1009 | 978 | 1139 | 54.36 | 3825.36 | 3616.5 | 208.86 | 3826 | 4.631 | 80.52% | Module cleaning has been done in Row-I,J, Inverter No-2 & Row-D,E,F,G,H, inverter No-1 total module cleaning -1470 |  | 1470
2021-05-16 | 524 | 786 | 751 | 867 | 37.29 | 2965.29 | 2807.25 | 158.04 | 2966 | 3.852 | 75.05% | Grid failure from-04:42 to 04:46
2021-05-17 | 303 | 418 | 393 | 449 | 14.46 | 1577.46 | 1423.5 | 153.96 | 1578 | 1.761 | 87.34% | Grid failure from-09:19 to 09:26 & 09:33 to 09:37 & 09:38 to 10:02 & 11:18 to 11:24 & 11:24 to 12:27
2021-05-18 | 120 | 141 | 141 | 146 | 3.3 | 551.3 | 408.75 | 142.55 | 552 | 5.51 | 9.764% | Grid failure from-03:48 to 07:55
2021-05-19 | 373 | 524 | 504 | 595 | 23.49 | 2019.49 | 1884 | 135.49 | 2020 | 2.266 | 86.88% | Grid failure from-09:25 to 09:38 &09:48 to 10:02
2021-05-20 | 752 | 1155 | 1124 | 1330 | 76.67 | 4437.67 | 4233 | 204.67 | 4338 | 5.447 | 77.62%
2021-05-21 | 740 | 1149 | 1114 | 1351 | 73.05 | 4427.05 | 4217.25 | 209.8 | 4428 | 5.485 | 78.68% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning -1386 |  | 1386
2021-05-22 | 686 | 1038 | 1023 | 1205 | 64.44 | 4016.44 | 3819.75 | 196.69 | 4017 | 5.017 | 78.04% | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-O,P,Q,R,S,T inverter No-3 total module cleaning -1302 |  | 1302
2021-05-23 | 675 | 1064 | 1043 | 1240 | 65.29 | 4087.29 | 3897 | 190.29 | 4088 | 5.102 | 78.09%
2021-05-24 | 696 | 1109 | 1069 | 1290 | 69.43 | 4233.43 | 4019.25 | 214.18 | 4234 | 5.458 | 75.61% | Module Cleaning has been done in Row-J,K,L Inverter No-2 & Row-M,N Inverter No-3 total module cleaning -1281 |  | 1281
2021-05-25 | 731 | 1164 | 1114 | 1331 | 75.86 | 4415.86 | 4201.5 | 214.36 | 4416 | 5.692 | 75.62% | Module Cleaning has been done in Row-I, Inverter No-2 & Row-A,B,C,D,E,F,G,H, Inverter No-1 total module cleaning -1386 |  | 1386
2021-05-26 | 650 | 998 | 957 | 1149 | 55.92 | 3809.92 | 3619.5 | 190.42 | 3810 | 4.763 | 77.96% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 & Grid failure from-11:03 to 11:06 |  | 1386
2021-05-27 | 685 | 1008 | 973 | 1220 | 61.1 | 3947.1 | 3741 | 206.1 | 3948 | 4.957 | 77.63% | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 & Grid failure from-01:28 to 01:32 |  | 1368
2021-05-28 | 696 | 1048 | 1023 | 1219 | 60.31 | 4046.31 | 3845.25 | 201.06 | 4047 | 5.171 | 76.28% | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 & Grid failure from-04:53 to 05:22 |  | 1344
2021-05-29 | 721 | 1059 | 1013 | 1215 | 63.41 | 4071.41 | 3865.5 | 205.91 | 4172 | 5.086 | 79.95% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-1 total module cleaning -1113 & Today we are found 1 MC4 connecter born Inverter No-1 AJB-103 string no-3 +tive site we replaced 1-MC4 connecter and started the string |  | 1113
2021-05-30 | 750 | 1103 | 1064 | 1260 | 69.94 | 4246.94 | 4044 | 202.94 | 4247 | 5.331 | 77.65%
2021-05-31 | 747 | 1094 | 1048 | 1265 | 68.05 | 4222.05 | 4017 | 205.05 | 4223 | 5.244 | 78.49% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning -1386 |  | 1386
2021-06-01 | 746 | 1094 | 1064 | 1305 | 70.37 | 4279.37 | 4068.75 | 210.62 | 4280 | 5.183 | 80.49% | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1368
2021-06-02 | 746 | 1134 | 1114 | 1311 | 75.89 | 4380.89 | 4166.25 | 214.64 | 4381 | 5.014 | 85.16% | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344
2021-06-03 | 725 | 1089 | 1043 | 1235 | 68.58 | 4160.58 | 3965.25 | 195.33 | 4161 | 5.106 | 79.43% | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 total module cleaning -1113
2021-06-04 | 691 | 998 | 958 | 1149 | 60.88 | 3856.88 | 3660.75 | 196.13 | 3857 | 4.965 | 75.72% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 & Grid failure from-04:14 to 04:38 |  | 1386
2021-06-05 | 766 | 1154 | 1119 | 1351 | 47.18 | 4437.18 | 3660.75 | 776.43 | 4438 | 5.098 | 84.85% | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368
2021-06-06 | 726 | 1073 | 1038 | 1260 | 67.93 | 4164.93 | 3960 | 204.93 | 4165 | 4.656 | 87.19%
2021-06-07 | 690 | 1029 | 998 | 1189 | 63.17 | 3969.17 | 3790.5 | 178.67 | 3970 | 4.836 | 80.01% | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344
2021-06-08 | 681 | 1003 | 968 | 1140 | 61.84 | 3853.84 | 3643.5 | 210.34 | 3854 | 4.488 | 83.7% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning -1113 |  | 1113
2021-06-09 | 670 | 973 | 927 | 1119 | 60.28 | 3749.28 | 3550.5 | 198.78 | 3750 | 4.403 | 83.01%
2021-06-10 | 650 | 937 | 905 | 1113 | 58.34 | 3663.34 | 3455.25 | 208.09 | 3663 | 4.435 | 80.5% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 |  | 1386
2021-06-11 | 676 | 1008 | 975 | 1210 | 64.03 | 3933.03 | 3729 | 204.03 | 3934 | 5.021 | 76.37% | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1368
2021-06-12 | 675 | 1003 | 956 | 1164 | 61.53 | 3859.53 | 3677.25 | 182.28 | 3860 | 4.939 | 76.17% | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344
2021-06-13 | 650 | 952 | 944 | 1084 | 53.01 | 3683.01 | 3469.5 | 213.51 | 3684 | 4.606 | 77.96% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning -1113 |  | 1113
2021-06-14 | 686 | 1004 | 968 | 1164 | 60.61 | 3882.61 | 3682.5 | 200.11 | 3883 | 4.79 | 79.01% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 |  | 1386
2021-06-15 | 685 | 1003 | 973 | 1185 | 62.79 | 3908.79 | 3708.75 | 200.04 | 3909 | 4.885 | 77.99%
2021-06-16 | 650 | 947 | 917 | 1108 | 52.48 | 3674.48 | 3474.75 | 199.73 | 3675 | 4.595 | 77.95% | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1386
2021-06-17 | 413 | 595 | 575 | 696 | 28.34 | 2307.34 | 2142.75 | 164.59 | 2308 | 3.432 | 65.55% | Grid failure from-07:30 to 07:59 & 01:14 to 02:28 & 02:52 to 02:55 & 03:06 to 03:10 & 04:06 to 04:10
2021-06-18 | 509 | 701 | 680 | 791 | 27.31 | 2708.31 | 2553 | 155.31 | 2709 | 3.09 | 85.45% | Grid failure from-03:34 to 03:36
2021-06-19 | 298 | 393 | 378 | 434 | 13.2 | 1516.2 | 1366.5 | 149.7 | 1517 | 1.856 | 79.66% | Grid failure from-11:02 to 11:17 & 12:57 to 01:36 & 02:17 to 02:19
2021-06-20 | 398 | 529 | 514 | 585 | 18.2 | 2044.2 | 1947.75 | 96.45 | 2045 | 2.213 | 90.07%
2021-06-21 | 378 | 585 | 560 | 660 | 28.8 | 2211.8 | 2082.75 | 129.05 | 2212 | 2.891 | 74.57% | Grid failure from-12:16 to 02:05
2021-06-22 | 514 | 730 | 710 | 836 | 33.34 | 2823.34 | 2648.25 | 175.09 | 2824 | 3.443 | 79.94% | Grid failure from-08:12 to 08:19 & 12:47 to 12:55
2021-06-23 | 701 | 993 | 963 | 1139 | 52.02 | 3848.02 | 3606 | 242.02 | 3849 | 4.658 | 80.54% | Grid failure from-04:44 to 04:46
2021-06-24 | 539 | 711 | 685 | 807 | 33.97 | 2775.97 | 2616 | 159.97 | 2776 | 3.251 | 83.23% | Grid failure from-01:18 to 01:21
2021-06-25 | 681 | 1003 | 963 | 1139 | 57.02 | 3843.02 | 3651 | 192.02 | 3844 | 4.722 | 79.34% | Module Cleaning has been done in Row-I,J,K, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -1281 |  | 1281
2021-06-26 | 645 | 938 | 897 | 1069 | 55.52 | 3604.52 | 3412.5 | 192.02 | 3605 | 4.423 | 79.44% | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E Inverter No-4 total module cleaning -1266 |  | 1266
2021-06-27 | 710 | 1063 | 1023 | 1214 | 59.21 | 4069.21 | 3888.75 | 180.46 | 4070 | 5.144 | 77.12%
2021-06-28 | 379 | 489 | 469 | 539 | 16.32 | 1892.32 | 1785.75 | 106.57 | 1893 | 2.141 | 86.18% | Module cleaning has been done in Row-F,G,H,I,J,K,L Inverter No-4 tracker 1,2,3 total module cleaning -1320 |  | 1320
2021-06-29 | 579 | 821 | 797 | 948 | 40.19 | 3185.19 | 2962.5 | 222.69 | 3186 | 3.755 | 82.7%
2021-06-30 | 630 | 918 | 892 | 1053 | 53.73 | 3546.73 | 3392.25 | 154.48 | 3547 | 4.29 | 80.59% | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1092 |  | 1092
2021-07-01 | 595 | 887 | 857 | 1024 | 39.361 | 3402.361 | 3198 | 204.361 | 3403 | 4.635 | 71.56% | Module cleaning has been done in Row-I,J,K,L inverter No-2 total module cleaning -1092 & Grid failure from-03:04 to 04:02 & 05:20 to 05:25 |  | 1092
2021-07-02 | 635 | 938 | 902 | 1073 | 50.24 | 3598.24 | 3410.25 | 187.99 | 3599 | 4.415 | 79.45% | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,inverter No-1 total module cleaning -1113 & Grid failure from-05:21 to 05:31 |  | 1113
2021-07-03 | 640 | 967 | 937 | 1119 | 54.18 | 3717.18 | 3506.25 | 210.93 | 3718 | 4.62 | 78.44% | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-4 total module cleaning -1188 |  | 1188
2021-07-04 | 645 | 998 | 968 | 1149 | 61.41 | 3821.41 | 3652.5 | 168.91 | 3822 | 4.783 | 77.88%
2021-07-05 | 610 | 948 | 912 | 1104 | 57.24 | 3631.24 | 3419.25 | 211.99 | 3632 | 4.904 | 72.19% | Module cleaning has been done in Row-I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-P,Q,R,S,T, total module cleaning -1167 & Grid failure from-01:11 to 01:12 & 03:32 to 04:09 |  | 1167
2021-07-06 | 645 | 1028 | 1008 | 1200 | 62.57 | 3943.57 | 3761.25 | 182.32 | 3944 | 5.098 | 75.4% | Module Cleaning has been done in Row-M,N,OInverter No-3 & Row-K,L inverter no-2 total module cleaning -1176 |  | 1176
2021-07-07 | 671 | 1073 | 1039 | 1230 | 64.96 | 4077.96 | 3858 | 219.96 | 4078 | 5.084 | 78.18% | Module Cleaning has been done in Row-I,J Inverter No-2 & Row-E,F,G,H inverter no-1 total module cleaning -1344 |  | 1344
2021-07-08 | 685 | 1033 | 992 | 1189 | 58.36 | 3957.36 | 3731.25 | 226.11 | 3958 | 4.934 | 78.19% | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 & Row-A,B,C,D,E,F,G, inverter no-4 total module cleaning -1326 |  | 1326
2021-07-09 | 655 | 994 | 963 | 1159 | 55.54 | 3826.54 | 3661.5 | 165.04 | 3827 | 4.806 | 77.61% | Module cleaning has been done in Row-H,I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-Q,R,S,T, inverter No-3 total module cleaning -1218 |  | 1218
2021-07-10 | 605 | 917 | 902 | 1074 | 43.43 | 3541.43 | 3371.25 | 170.18 | 3542 | 4.464 | 77.34% | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 & Row-K,L, inverter no-2 total module cleaning -1323 |  | 1323
2021-07-11 | 529 | 751 | 726 | 852 | 32.45 | 2890.45 | 2736 | 154.45 | 2891 | 3.426 | 82.25%
2021-07-12 | 474 | 695 | 676 | 791 | 31.4 | 2667.4 | 2493.75 | 173.65 | 2668 | 3.196 | 81.36%
2021-07-13 | 640 | 983 | 947 | 1149 | 56.22 | 3775.22 | 3565.5 | 209.72 | 3776 | 4.738 | 77.68% | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-E,F,G,H, inverter no-1 total module cleaning -1344 |  | 1344
2021-07-14 | 646 | 998 | 968 | 1149 | 53.38 | 3814.38 | 3607.5 | 206.88 | 3815 | 4.715 | 78.86%
2021-07-15 | 634 | 1003 | 968 | 1165 | 53.11 | 3823.11 | 3681 | 142.11 | 3824 | 4.803 | 77.6%
2021-07-16 | 545 | 852 | 831 | 993 | 42.64 | 3263.64 | 3075 | 188.64 | 3264 | 4.131 | 77.01%
2021-07-17 | 554 | 817 | 791 | 937 | 43.87 | 3142.87 | 2953.5 | 189.37 | 3143 | 2.871 | 106.7%
2021-07-18 | 373 | 509 | 494 | 575 | 21.28 | 1972.28 | 1845 | 127.28 | 1973 | 1.933 | 99.48%
2021-07-19 | 464 | 654 | 635 | 746 | 24.46 | 2523.46 | 2355 | 168.46 | 2524 | 2.824 | 87.11% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-1 & Row-A,B,C,D,E,F, inverter no-4 total module cleaning -1266 |  | 1266
2021-07-20 | 287 | 374 | 363 | 408 | 11.07 | 1443.07 | 1329.75 | 113.32 | 1444 | 1.585 | 88.8%
2021-07-21 | 418 | 569 | 550 | 630 | 20.84 | 2187.84 | 2020.5 | 167.34 | 2188 | 2.526 | 84.42% | Grid failure from-09:37 to 09:49
2021-07-22 | 600 | 857 | 831 | 978 | 39.71 | 3305.71 | 3129.75 | 175.96 | 3306 | 3.944 | 81.7% | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 total module cleaning - 790 |  | 790
2021-07-23 | 338 | 443 | 424 | 479 | 14.07 | 1698.07 | 1578 | 120.07 | 1699 | 1.855 | 89.27% | Module cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-R,S,T, inverter No-3 total module cleaning -1230 & Grid failure from-02:31 to 02:34 |  | 1230
2021-07-24 | 514 | 737 | 715 | 836 | 31.01 | 2833.01 | 2656.5 | 176.51 | 2834 | 3.393 | 81.41% | Module cleaning has been done in Row-M,N,O,P,Q, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1449 & Grid failure from-01:24 to 01:37 |  | 1449
2021-07-25 | 141 | 171 | 161 | 187 | 4.82 | 664.82 | 559.5 | 105.32 | 665 | 0.741 | 87.47% | Today U.P.S maintenanc from -09:28 to 10:12
2021-07-26 | 151 | 197 | 191 | 211 | 5.58 | 755.58 | 619.5 | 136.08 | 756 | 0.902 | 81.69% | Grid failure from -02:00 to 02:31
2021-07-27 | 343 | 463 | 454 | 525 | 15.71 | 1800.71 | 1656.75 | 143.96 | 1801 | 1.967 | 89.24%
2021-07-28 | 277 | 373 | 358 | 403 | 11.11 | 1422.11 | 1284.75 | 137.36 | 1423 | 1.556 | 89.13%
2021-07-29 | 172 | 222 | 217 | 237 | 6.23 | 854.23 | 714 | 140.23 | 855 | 0.945 | 88.18%
2021-07-30 | 302 | 403 | 388 | 438 | 12.84 | 1543.84 | 1408.5 | 135.34 | 1544 | 1.874 | 80.3% | Grid failure from -03:49 to 04:52 & 05:38 to 05:41
2021-07-31 | 393 | 524 | 524 | 610 | 19.44 | 2070.44 | 1910.25 | 160.19 | 2071 | 2.376 | 84.95% | Grid failure from -06:28 to 07:28 & 10:22 to 10:31
2021-08-01 | 414 | 560 | 559 | 660 | 20.94 | 2213.94 | 2067 | 146.94 | 2214 | 2.637 | 81.83% | Grid failure from -09:22 to 09:35
2021-08-02 | 232 | 277 | 283 | 333 | 10.16 | 1135.16 | 1018.5 | 116.66 | 1136 | 0.787 | 140.7%
2021-08-03 | 317 | 419 | 418 | 504 | 15.27 | 1673.27 | 1523.25 | 150.02 | 1674 | 1.953 | 83.54% | Today replace 3phase motor coil chang.
2021-08-04 | 388 | 509 | 514 | 620 | 21.94 | 2052.94 | 1903.5 | 149.44 | 2053 | 2.485 | 80.52% | Grid failure from -09:21 to 09:26
2021-08-05 | 479 | 659 | 645 | 791 | 31.47 | 2605.47 | 2467.5 | 137.97 | 2606 | 3.225 | 78.76% | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-F,G,H, inverter no-1 total module cleaning -1197 & Today we are found 1 MC4 connecter born Inverter No-2 AJB-112 string no-7 +tive & -tive site we replaced 2-MC4 connecter and started the string |  | 1197
2021-08-06 | 479 | 641 | 615 | 751 | 29.78 | 2515.78 | 2346 | 169.78 | 2516 | 3.065 | 80.01% | Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-1 & Row-Q,R,S,T, inverter no-3 total module cleaning -777 & Today we are clening all inverter door filters. |  | 777
2021-08-07 | 483 | 655 | 640 | 771 | 29.53 | 2578.53 | 2419.5 | 159.03 | 2579 | 3.243 | 77.51% | Module Cleaning has been done in Row-M,N,O,P, inverter no-3 total module cleaning -798 |  | 798
2021-08-08 | 530 | 756 | 736 | 867 | 34.18 | 2923.18 | 2744.25 | 178.93 | 2859 | 3.709 | 75.13%
2021-08-09 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-10 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-11 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-12 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-13 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-14 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-15 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-16 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-17 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-18 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-19 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-20 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-21 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-22 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-23 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-24 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-25 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-26 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-27 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-28 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-29 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-30 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
2021-08-31 | [5 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!
[6 empty] | 0 |  | 0 |  |  | #DIV/0!