## 2012
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2012-07-06 | 679 | 825 | 837 | 869 | 8 | 3218 | 3135 | 83 |  |  |  | Grid failure from 14.10 to 14.15 hours. Communication down, problem with SEEDS Gateway | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2012-07-07 | 882 | 899 | 910 | 924 | 18 | 3633 | 3540 | 93 |  |  |  | Grid failure from 13-37 to 13-42 hours. Communication down, problem with SEEDS Gateway | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2012-07-08 | 1051 | 1080 | 1091 | 1129 | 26 | 4377 | 4245 | 132 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2012-07-09 | 1114 | 1136 | 1148 | 1172 | 55 | 4625 | 4485 | 140 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2012-07-10 | 153 | 159 | 170 | 162 | 4 | 648 | 600 | 48 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2012-07-11 | 718 | 723 | 746 | 800 | 25 | 3012 | 2925 | 87 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2012-07-12 | 848 | 877 | 882 | 898 | 40 | 3545 | 3450 | 95 |  |  |  | Inverter 7802195 display not working. Communication down, problem with SEEDS Gateway | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2012-07-13 | 995 | 1017 | 1029 | 19.93 | 40 | 3100.93 | 2985 | 115.93 |  |  |  | Inverter 7802195 Break Down because of its S.M.P.S. found failed due to Moisture. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2012-07-14 | 927 | 944 | 955 | 72.03 | 42 | 2940.03 | 2850 | 90.03 | 2974 | 4.723 | 0.61373 | Inverter 7802195 started from 16.54, after replacing the S.M.P.S & Front panel Display unit | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2012-07-15 | 814 | 826 | 842 | 849 | 26 | 3357 | 3270 | 87 | 3402 | 3.942 | 0.84114 | Grid Supply Failure from- 08.42 am to 08.46 am. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2012-07-16 | 791 | 825 | 831 | 826 | 35 | 3308 | 3285 | 23 | 3203 | 3.84 | 0.81298 | Inverter 1104500527 was shut down from 15.24 to 15.26 & 15.29 to 15.31 for checking the Ethernet Adaptor (RETA-01) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2012-07-17 | 1114 | 1142 | 1154 | 1158 | 57 | 4625 | 4500 | 125 | 4654 | 5.546 | 0.8179 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2012-07-18 | 893 | 916 | 921 | 919 | 40 | 3689 | 3570 | 119 | 3695 | 4.337 | 0.8303 | M/s.Schneider has Came for Service The Inv-4,Then He Shut Downed The Inv From-17-25 to 21-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2012-07-19 | 826 | 842 | 860 | 735 | 37.01 | 3300.01 | 3240 | 60.01 | 3349 | 4.054 |  | M/s.Schneider has Came for Observation,Then he Shut-downed the INV-4 ,From 13-05 TO 13-25 for Data log in,,,,,,,Grid Also Failure From- 18-20 to 18-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2012-07-20 | 910 | 939 | 961 | 944 | 41 | 3795 | 3690 | 141 | 3831 | 4.48 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2012-07-21 | 870 | 899 | 944 | 941 | 44 | 3698 | 3630 | 123 | 3753 | 4.534 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2012-07-22 | 617 | 644 | 656 | 623 | 22.1 | 2562.1 | 2505 | 57.1 | 2617 | 3.009 | 84.76 | Grid Supply Failure From - 10-20 TO 10-26. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2012-07-23 | 435 | 458 | 458 | 435 | 13.21 | 1799.21 | 1755 | 44.21 | 1843 | 2.062 | 87.11 | Grid Supply Failure From - 14-28 TO 14-33. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2012-07-24 | 661 | 678 | 689 | 667 | 23.449 | 2718.44 | 2640 | 78.44 | 2745 | 3.155 | 84.79 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2012-07-25 | 843 | 860 | 865 | 862 | 34.61 | 3464.61 | 3375 | 89.61 | 3503 | 3.958 | 86.26 | Grid Supply Failure From- 15-39 To 15-44. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2012-07-26 | 933 | 950 | 950 | 937 | 38.76 | 3808.76 | 3705 | 103.76 | 3828 | 4.474 | 83.39 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2012-07-27 | 944 | 961 | 972 | 972 | 43.06 | 3892.06 | 3780 | 112.06 | 3917 | 4.604 | 82.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2012-07-28 | 429 | 435 | 441 | 485 | 13.41 | 1803.41 | 1710 | 93.41 | 1789 | 2.031 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2012-07-29 | 317 | 328 | 334 | 279 | 7.86 | 1265.86 | 1275 | 9.14 | 1359 | 1.519 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2012-07-30 | 407 | 418 | 435 | 419 | 12.55 | 1691.55 | 1635 | 56.55 | 1724 | 1.871 | 89.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2012-07-31 | 345 | 385 | 385 | 379 | 9.07 | 1503.07 | 1470 | 33.07 | 1542 | 1.875 | 80.15 | Inv-1 & 4 Break downed From 13-05 to 13-12 due High Grid Frquancy Fault. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2012-08-01 | 610 | 627 | 644 | 633 | 14.04 | 2528.04 | 2460 | 68.04 | 2564 | 2.302 | 108.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2012-08-02 | 973 | 990 | 989 | 965 | 2.53 | 3919.53 | 3810 | 109.53 |  |  |  | Because of Unbalanced Frequancy of GRID, Inv-4, went in F1.Hi Grid Freequancy fault mode 4th time.Tracker`s Inverters also Went in Grid fault mode severly. And Internet Radio link Also Failure from PDPU.From 11-00,O`Clock.-2-8-12 To 18-00,O`Clock Today -3-8-12 ,SEEDS data does not Available now. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
29 | 2012-08-03 | 531 | 542 | 554 | 541 | 6.04 | 2174.04 | 2130 | 44.04 | 2932 |  |  | Plant Shut Downed From -11-25 to 11-33, For Rectification of Sparking Problem in the D.O.Fuse Holder of `R`Phase,,,,,Grid Failure From-12-18 to 12-23 & 16-45 to 16-57. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2012-08-04 | 814 | 837 | 849 | 841 | 16.49 | 3357.49 | 3255 | 102.49 | 3399 | 3.945 | 83.97 | Internet Failure From- 12-30 to 13-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
31 | 2012-08-05 | 656 | 673 | 684 | 675 | 13.47 | 2701.47 | 2640 | 61.47 | 2753 | 3.183 | 84.29 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2012-08-06 | 995 | 1017 | 1023 | 1041 | 25.27 | 4101.27 | 3990 | 111.27 | 4133 | 4.625 | 87.09 | Plant Shut Downed From- 09-00 to 09-07 ,For Replaced The `R`,D.O.Fuse assembly . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2012-08-07 | 718 | 741 | 752 | 763 | 19.67 | 2993.61 | 2925 | 68.61 | 3049 | 3.473 | 85.56 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2012-08-08 | 475 | 492 | 492 | 495 | 5.31 | 1959.31 | 1890 | 69.31 | 2016 | 2.226 | 82.27 | Grid Supply Failure From- 17-18 to 18-30. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2012-08-09 | 543 | 559 | 571 | 552 | 2.47 | 2227.47 | 2160 | 67.47 | 2288 | 2.514 | 88.7 | Because of High Grid Voltages (256 V to 257 V) All 03,No`s fo Trackers SMA Inverters- Went to Fault ,Grid Disturbance From 12-15 to 00-00. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2012-08-10 | 870 | 854 | 825 | 902 | 0 | 3451 | 3345 | 106 | 3515 | 4.022 | 85.17 | Because of High Grid Voltages (260 V to 262 V) All 03,No`s fo Trackers SMA Inverters- Went to Fault ,Grid Disturbance From 00-00 to 19-30. And INV-2 & 3 Went to Fault-ID-2 Mode during 11-43 to 11-55 & 13-35 to 13-38, Inv-4 Also Went to Stand by Mode From -17-18 to 17-20. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2012-08-11 | 543 | 560 | 571 | 557 | 0.39 | 2231.39 | 2160 | 71.39 | 2279 | 2.549 | 87.14 | Because of High Grid Voltages (>252V) All o3,No`s of Trackers Inverters went to Fault Grid Diturbance From 00-00 to 11-15,,,,,,,11-30 to 16-30,,,,,,,,,17-00 to 18-00,,,,,,,, & 18-15 to 19-30. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2012-08-12 | 192 | 198 | 209 | 205 | 0.99 | 804.99 | 765 | 39.99 |  |  |  | Internet Failure From- 11-00 to 00-00……….. Grid Supply Failure From -16-13 to 16-33. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
39 | 2012-08-13 | 300 | 311 | 317 | 306 | 7.04 | 1241.04 | 1230 | 11.04 | 1251 |  |  | Internet Started From-10-30….Grid Supply Failure From-16-50 to 16-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
40 | 2012-08-14 | 277 | 288 | 294 | 281 | 6.06 | 1146.06 | 1095 | 51.06 | 1197 | 1.344 | 86.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2012-08-15 | 565 | 582 | 593 | 580 | 2.72 | 2322.72 | 2265 | 57.72 | 2382 | 2.836 | 81.86 | Plant Break Downed From -11-34 To 11-42 B`coz of Blown off The D.O.Fuse of `R` Phase. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2012-08-16 | 639 | 656 | 662 | 645 | 18.48 | 2620.48 | 2535 | 85.48 | 2664 | 3.032 | 85.63 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2012-08-17 | 752 | 775 | 786 | 780 | 21.01 | 3114.01 | 3030 | 84.01 | 3167 | 3.633 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2012-08-18 | 899 | 927 | 944 | 949 | 19.47 | 3738.47 | 3660 | 78.47 | 3806 | 4.299 |  | Grid Supply Failure From-15-02 To 15-22. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2012-08-19 | 1142 | 1170 | 1176 | 1167 | 0.2 | 4655.2 | 4515 | 140.2 | 4706 | 5.6356 | 81.39 | Out of Few Minutes All 03,No`s fo Trackers SMA Inverters- Went to Fault ,Grid Disturbance Because of High Grid Voltages (254 V to 260 V ) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2012-08-20 | 831 | 854 | 859 | 866 | 2.26 | 3412.26 | 3330 | 82.26 | 3471 | 4.121 | 82.09 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2012-08-21 | 927 | 944 | 944 | 986 | 25.3 | 3826.3 | 3735 | 91.3 | 3483 |  |  | Grid Supply Failure From- 08-25 to 08-30,,,,10-12 to 10-17,,,,,,10-27 to 10-32 & 11-07 to 11-51,,,,, Our CPU has Hanged From-13-17 then we Sent to PDPU server Room for Repaired it. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2012-08-22 | 452 | 469 | 475 | 463 | 7.55 | 1866.55 | 1815 | 51.55 | 2306 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2012-08-23 | 911 | 933 | 944 | 956 | 33.29 | 3777.29 | 3690 | 87.29 | 3812 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2012-08-24 | 910 | 927 | 933 | 957 | 33.41 | 3760.41 | 3660 | 100.41 | 3787 | 4.505 | 81.93 | All Inverters Went to Fault Mode From - 15-10 to 15-20 & 15-25 to 15-30 due to Law Grid Freequancy. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2012-08-25 | 650 | 673 | 684 | 666 | 15.02 | 2688.02 | 2625 | 63.02 | 2679 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2012-08-26 | 808 | 825 | 837 | 833 | 14.13 | 3317.13 | 3255 | 62.13 | 3427 |  |  | Grid Suplly Failure From - 08-35 to 08-40. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2012-08-27 | 1035 | 1057 | 1057 | 1086 | 34.84 | 4269.84 | 4140 | 129.84 | 4298 | 5.116 | 81.88 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2012-08-28 | 424 | 441 | 447 | 445 | 12.23 | 1769.23 | 1755 | 14.23 | 1824 | 2.076 | 85.63 | Grid Supply Failure From -13-30 13-35 & 14-06 to 14-16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2012-08-29 | 904 | 933 | 944 | 936 | 37.95 | 3754.95 | 3675 | 79.95 | 3792 | 4.36 | 84.76 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2012-08-30 | 922 | 950 | 949 | 955 | 35.94 | 3811.94 | 3720 | 91.94 | 3856 | 4.543 | 82.72 | Grid Supply Failure From -11-27 to 11-42. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2012-08-31 | 622 | 644 | 656 | 644 | 24.99 | 2590.99 | 2520 | 70.99 | 2627 | 3.078 |  | Grid Supply Failure From -14-54 to 15-00 & 15-05 to 15-10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2012-09-01 | 876 | 899 | 905 | 930 | 19.28 | 3629.28 | 3555 | 74.28 | 3684 | 4.313 |  | Grid supply Failure From -10-45 to 11-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2012-09-02 | 803 | 826 | 831 | 819 | 18.59 | 3297.59 | 3225 | 72.59 | 3343 | 3.895 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 2012-09-03 | 712 | 735 | 740 | 731 | 11.84 | 2929.84 | 2865 | 64.84 | 2963 | 3.415 | 84.56 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2012-09-04 | 905 | 932 | 944 | 930 | 18.09 | 3729.09 | 3645 | 84.09 | 3764 | 4.216 | 87.01 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2012-09-05 | 1040 | 1069 | 1080 | 1095 | 23.74 | 4307.74 | 4200 | 107.74 | 4347 | 5.06 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2012-09-06 | 283 | 294 | 300 | 291 | 5.04 | 1173.04 | 1140 | 33.04 | 1218 | 1.441 | 82.38 | Grid Supply Failure From - 10-20 to 10-25. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2012-09-07 | 226 | 237 | 243 | 237 | 4.21 | 947.21 | 915 | 32.21 | 966 | 1.195 | 78.78 | I shut downed the Plant From-12-45 to 12-55, For solved the chattering problem in Fuse Holder of-11-kv, `R` D.O.Fuse. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2012-09-08 | 757 | 780 | 786 | 772 | 15.87 | 3110.87 | 3030 | 80.87 | 3167 | 3.789 | 81.46 | Grid Supply Failure From- 11-06 to 11-22 & 11-25 to 11-28. And also Blown off The .D.O.Fuse of `R` Phase . | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2012-09-09 | 283 | 289 | 288 | 295 | 4.96 | 1159.96 | 1125 | 34.96 | 1217 | 1.417 | 83.7 | Grid Supply Failure From- 14-01 to14-05. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2012-09-10 | 396 | 407 | 413 | 401 | 11.66 | 1628.66 | 1605 | 23.66 | 1676 | 1.64 | 99.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2012-09-11 | 492 | 503 | 509 | 498 | 11.88 | 2013.88 | 1965 | 48.88 | 2060 | 2.297 |  | Grid Supply Failure From- 15-35 to 15-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2012-09-12 | 684 | 707 | 695 | 710 | 11.07 | 2807.07 | 2745 | 62.07 | 2834 | 3.221 | 85.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2012-09-13 | 610 | 627 | 611 | 618 | 10.76 | 2476.76 | 2430 | 46.76 | 2536 | 2.912 | 84.88 | Grid Supply Failure From -13-07 to 13-12. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2012-09-14 | 871 | 893 | 859 | 904 | 4.55 | 3531.55 | 3435 | 96.55 | 3570 | 4.363 | 79.75 | Because of Heavy Cloud All Inverters Went to Sleep mode Severaly during the Period of ,,,,,,,,,17-00 to 17-40. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2012-09-15 | 1080 | 1108 | 1080 | 1120 | 19.66 | 4407.66 | 4305 | 102.66 | 4469 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2012-09-16 | 1080 | 1114 | 1074 | 1118 | 8.2 | 4394.2 | 4290 | 104.2 | 4441 | 5.395 | 80.23 | Because Of High Grid Voltages >256V All SMA Inverters-No-5 Went to Grid Disturbance Mode for Sevral Time . | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2012-09-17 | 1226 | 1261 | 1215 | 1263 | 8.95 | 4973.95 | 4845 | 128.95 | 5010 | 6.15 | 0.794 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2012-09-18 | 1148 | 1187 | 1159 | 1172 | 21.26 | 4687.26 | 4575 | 112.26 | 4732 | 5.872 | 78.54 | Grid Supply Failure From -10-34 to 10-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2012-09-19 | 950 | 978 | 984 | 950 | 15.31 | 3877.31 | 3780 | 97.31 | 3903 | 4.736 | 80.32 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2012-09-20 | 1102 | 1137 | 1142 | 1136 | 27.05 | 4544.05 | 4440 | 104.05 | 4569 | 5.622 | 79.21 | Grid Supply Failure From - 17-38 to 17-43. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2012-09-21 | 809 | 836 | 848 | 814 | 24.23 | 3331.23 | 3240 | 91.23 | 3371 | 4.021 | 81.71 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2012-09-22 | 870 | 893 | 899 | 890 | 22.59 | 3574.59 | 3495 | 79.59 | 3614 | 4.392 | 80.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2012-09-23 | 905 | 933 | 944 | 931 | 11.41 | 3724.41 | 3630 | 94.41 | 3771 | 4.512 | 81.45 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2012-09-24 | 1068 | 1103 | 1108 | 1108 | 29.79 | 4416.79 | 4305 | 111.79 | 4458 | 4.856 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2012-09-25 | 1159 | 1193 | 1199 | 1227 | 20.42 | 4798.42 | 4695 | 103.42 | 4853 | 5.847 | 80.89 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2012-09-26 | 1193 | 1232 | 1243 | 1235 | 32.94 | 4935.94 | 4800 | 135.94 | 4973 | 5.848 | 82.88 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2012-09-27 | 1170 | 1210 | 1210 | 1220 | 30.84 | 4840.84 | 4710 | 130.84 | 4871 | 6.167 | 76.98 | Grid Supply Failure From - 17-31 to 17-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2012-09-28 | 1295 | 1334 | 1346 | 1351 | 25.34 | 5351.34 | 5220 | 131.34 | 5370 | 6.565 |  | Grid Supply Failure From -10-40- to 10-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2012-09-29 | 1328 | 1374 | 1390 | 1367 | 27.16 | 5486.16 | 5340 | 146.16 | 5366 |  |  | Grid Supply Failure From- 17-30 to 17-35 & 17-36 to 17-50, & Also Filure The Net From PDPU , Because of Shut Downed The Server for It`s Service Purpose. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2012-09-30 | 1301 | 1357 | 1363 | 1344 | ERROR | 5365 | 5235 | 130 |  |  |  | Plant Break Downed From -09-30 to 09-45, Due to Blown off The D.O.Fuse of `B` Phase. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2012-10-01 | 1266 | 1323 | 1317 | 1328 | 39 | 5273 | 5130 | 143 | 5304 | 6.646 | 77.78 | Plant Break Downed From -10-50 to 11-05,Because of Loose soldaring of ,D.,O.Fuselink it`s Blown off Again. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2012-10-02 | 1114 | 1158 | 1153 | 1155 | 14.46 | 4594.46 | 4485 | 109.46 | 4636 | 5.711 | 0.7912 | Grid failure from 16.11 to 16. 49 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2012-10-03 | 1147 | 1188 | 1182 | 1172 | 58.21 | 4747.21 | 4620 | 127.21 | 4777 | 6.089 | 76.46 | Plant Break Downed From -11-08 to 11-23,Because of Loose soldaring of ,D.,O.Fuselink it`s Blown off Again. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2012-10-04 | 1273 | 1283 | 1272 | 1283 | 55.47 | 5166.47 | 5025 | 141.47 | 5193 | 6.582 | 76.89 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2012-10-05 | 1294 | 1306 | 1289 | 1325 | 45.16 | 5259.16 | 5115 | 144.16 | 5296 | 6.67 | 77.38 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2012-10-06 | 1176 | 1181 | 1176 | 1183 | 36.77 | 4752.77 | 4635 | 117.77 | 4788 | 6.188 | 75.41 | Grid Supply Failure From - 11-45 to 11-50. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2012-10-07 | 769 | 781 | 769 | 801 | 27.65 | 3147.65 | 3060 | 87.65 | 3187 | 3.911 | 79.42 | Grid Supply Failure From - 10-57 to 11-24. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2012-10-08 | 1193 | 1204 | 1193 | 1254 | 47.31 | 4891.31 | 4770 | 121.31 | 4929 | 6.198 | 77.51 | Grid Supply Failure From -09-55 to 10-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2012-10-09 | 1215 | 1227 | 1221 | 1293 | 30.16 | 4986.16 | 4845 | 141.16 | 5000 | 6.364 | 76.57 | Grid Supply Failure From -11-28 to 11-33,,,,,,15-20 to 15-33,,,,,,,,,,16-53 to 16-58 & 17-14 to 17-19. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2012-10-10 | 1289 | 1328 | 1340 | 1379 | 61.56 | 5397.56 | 5250 | 147.56 | 5401 |  |  | Grid Supply Failure From- 11-18 to 11-23. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2012-10-11 | 1255 | 1295 | 1317 | 1338 | 48.21 | 5253.21 | 5115 | 138.21 | 5274 | 5.58 |  | Grid Supply Failure From- 16-52 to 17-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2012-10-12 | 1187 | 1227 | 1278 | 1102 | 53.12 | 4847.12 | 4710 | 137.12 | 4867 | 6.318 | 75.08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2012-10-13 | 1165 | 1249 | 1272 | 1212 | 54.79 | 4952.79 | 4800 | 152.79 | 4970 | 6.214 | 77.95 | Grid Supply Failure From- 10-03 to 10-08. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2012-10-14 | 1182 | 1283 | 1272 | 1246 | 49.54 | 5032.54 | 4905 | 127.54 | 5058 | 6.255 | 78.81 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2012-10-15 | 1198 | 1312 | 1300 | 1276 | 53.15 | 5139.15 | 4980 | 159.15 | 5151 | 6.432 | 78.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2012-10-16 | 1199 | 1317 | 1300 | 1305 | 55.21 | 5176.21 | 5025 | 151.21 | 5192 | 6.511 | 77.72 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2012-10-17 | 1170 | 1272 | 1261 | 1296 | 54 | 5053 | 4905 | 148 | 5077 | 6.484 | 76.31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2012-10-18 | 1136 | 1238 | 1221 | 1262 | 51.18 | 4908.18 | 4755 | 153.18 | 4915 | 6.128 | 78.17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2012-10-19 | 1080 | 1187 | 1170 | 1213 | 51.65 | 4701.65 | 4575 | 126.65 | 4727 | 5.96 | 77.3 | Plant Break Downed From- 11-47 to 12-00, Because of Blown off The D.O.Fuse of `R` Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2012-10-20 | 1131 | 1239 | 1204 | 1257 | 52.48 | 4883.48 | 4740 | 143.48 | 4913 | 6.287 | 76.16 | Internet Failure From- 17-32 to 18-45. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
110 | 2012-10-21 | 1091 | 1170 | 1137 | 1165 | 33.6 | 4596.6 | 4485 | 111.6 | 4631 | 5.883 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2012-10-22 | 1085 | 1142 | 1102 | 1132 | 39.26 | 4500.26 | 4365 | 135.26 | 4519 | 5.901 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2012-10-23 | 1108 | 1147 | 1108 | 1147 | 37.55 | 4547.55 | 4425 | 122.55 | 4583 | 5.871 | 76.08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2012-10-24 | 1199 | 1210 | 1170 | 1111 | 14 | 4704 | 4590 | 114 | 4739 | 5.997 | 77.02 | Grid Supply Failure From - 08-38 to 08-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2012-10-25 | 1238 | 1250 | 1199 | 1221 | 36.66 | 4944.66 | 4800 | 144.66 | 4972 | 6.348 | 76.33 | Grid Supply Failure From - 14-57 to 14-58. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2012-10-26 | 1266 | 1272 | 1227 | 1289 | 40.88 | 5094.88 | 4965 | 129.88 | 5129 | 6.527 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2012-10-27 | 1278 | 1289 | 1238 | 1313 | 50.94 | 5168.94 | 5025 | 143.94 | 5193 | 6.512 | 77.72 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2012-10-28 | 1249 | 1249 | 1204 | 1292 | 46.85 | 5040.85 | 4890 | 150.85 | 5066 | 6.256 | 78.92 | Grid supply Failure From -08-45 to 08-50,,,,,,16-01 to 16-05,,,,,&,,16-34 to 16-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2012-10-29 | 1261 | 1272 | 1216 | 1323 | 62.52 | 5134.52 | 4995 | 139.52 | 5152 | 6.435 | 78.03 | Grid Supply Failure From - 17-57 to 18-01. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2012-10-30 | 1227 | 1233 | 1192 | 1285 | 55.45 | 4992.45 | 4860 | 132.45 | 5021 | 6.249 | 78.31 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2012-10-31 | 1057 | 1062 | 1103 | 1081 | 44.97 | 4347.97 | 4230 | 117.97 | 4385 | 5.372 | 79.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2012-11-01 | 565 | 560 | 605 | 571 | 15.72 | 2316.72 | 2280 | 36.72 | 2382 |  |  | Grid Supply Failure From - 09-40 TO 09-45, And Plant Break Downed From - 09-50 TO 12-00, Because of Created The Fault in Aux-440,V,Supply. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 2012-11-02 | 1142 | 1170 | 1244 | 1168 | 47.55 | 4771.55 | 4635 | 136.55 | 4796 | 5.912 | 79.06 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2012-11-03 | 1148 | 1233 | 1243 | 1166 | 48.69 | 4838.69 | 4695 | 143.69 | 4864 | 5.44 |  | Grid Supply Failure From - 17-30 to 17-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2012-11-04 | 1080 | 1198 | 1170 | 1083 | 22.15 | 4553.15 | 4425 | 128.15 | 4590 | 5.555 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2012-11-05 | 1074 | 1165 | 1142 | 1042 | 38.39 | 4461.39 | 4350 | 111.39 | 4498 | 5.568 | 78.73 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2012-11-06 | 1108 | 1159 | 1126 | 1036 | 35.7 | 4464.7 | 4350 | 114.7 | 4502 | 5.399 | 81.27 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2012-11-07 | 1108 | 1153 | 1136 | 1070 | 33.44 | 4500.44 | 4380 | 120.44 | 4540 | 5.419 | 81.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2012-11-08 | 1063 | 1108 | 1080 | 1045 | 35.03 | 4331.03 | 4215 | 116.03 | 4374 | 5.452 | 78.19 | Grid Supply Failure From - 08-43 to 08-48. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2012-11-09 | 1136 | 1187 | 1159 | 1170 | 30.81 | 4682.81 | 4560 | 122.81 | 4714 | 5.801 | 79.2 | Grid Supply Failure From - 09-09 to 09-18. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2012-11-10 | 1171 | 1216 | 1181 | 1225 | 34.3 | 4827.3 | 4695 | 132.3 | 4858 | 6.047 | 78.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2012-11-11 | 1147 | 1198 | 1170 | 1214 | 30.31 | 4759.31 | 4635 | 124.31 |  |  |  | Grid Supply Failure From - 13-09 TO 13-10,,,,,Client Connect Prod.Graf has Not Updated From -6-30 to 00-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2012-11-12 | 1171 | 1222 | 1188 | 1260 | 35.55 | 4876.55 | 4740 | 136.55 |  |  |  | Grid Supply Failure From- 16-49 to 16-54,,,,,Client Connect Prod.Graf has Not Updated From -00-00 to 00-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2012-11-13 | 1108 | 1153 | 1153 | 1168 | 9.89 | 4591.89 | 4485 | 106.89 |  |  |  | Grid Supply Failur From - 10-27 to 10-32 & 11-25 to 11-30,,,,,,,,Cliend Connect Prod,Graf is Not Updated From -24-00 to 24-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2012-11-14 | 1028 | 1074 | 1074 | 1069 | 1.461 | 4246.461 | 4140 | 106.461 |  |  |  | Client Connect Prod.Graf Not Updated Properly. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2012-11-15 | 1029 | 1068 | 1074 | 1065 | 12.26 | 4248.26 | 4125 | 123.26 |  |  |  | Grid Supply Failure From - 17-38 to 17-41. Client Connect Prod.Graf Not Updated Properly. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2012-11-16 | 1120 | 1165 | 1170 | 1168 | 18.84 | 4641.84 | 4515 | 126.84 | 4471 |  |  | Grid Supply Failure From -12-41 to 12-46. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2012-11-17 | 1091 | 1142 | 1159 | 1123 | 24.01 | 4539.01 | 4410 | 129.01 | 4569 | 5.78 | 77.04 | Grid Supply Failure From - 09-08 to 09-30. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2012-11-18 | 1148 | 1204 | 1255 | 1205 | 18.37 | 4830.37 | 4710 | 120.37 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2012-11-19 | 1079 | 1165 | 1182 | 1128 | 33.75 | 4587.75 | 4470 | 117.75 |  |  |  | Grid Supply Failure From - 12-58 to 13-03,,,,18-10 to 20-30 & 20-35 to 00-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2012-11-20 | 797 | 882 | 865 | 996 | 12.8 | 3552.8 | 3390 | 162.8 |  |  |  | Grid Supply Failure From - 16-40 to 16-45 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2012-11-21 | 1080 | 1170 | 1148 | 1077 | 20.98 | 4495.98 | 4380 | 115.98 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2012-11-22 | 1097 | 1137 | 1130 | 1058 | 19.45 | 4441.45 | 4335 | 106.45 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2012-11-23 | 1108 | 1136 | 1137 | 1081 | 15.81 | 4477.81 | 4365 | 112.81 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2012-11-24 | 1148 | 1170 | 1170 | 1150 | 10.19 | 4648.19 | 4515 | 133.19 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2012-11-25 | 1176 | 1221 | 1198 | 1183 | 7.1 | 4785.1 | 4665 | 120.1 |  |  |  | Grid Supply Failure From - 11-05 to 11-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2012-11-26 | 1164 | 1216 | 1188 | 1194 | 17.37 | 4779.37 | 4635 | 144.37 |  |  |  | Grid Supply Failure From - 10-05 to 11-11. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2012-11-27 | 1142 | 1193 | 1164 | 1193 | 17.72 | 4709.72 | 4590 | 119.72 | 4755 | 6.067 | 76.38 | Grid Supply Failure From - 11-50 to 11-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2012-11-28 | 1148 | 1193 | 1193 | 1206 | 15.03 | 4755.03 | 4635 | 120.03 | 4799 | 5.901 | 79.26 | Grid Supply Failure From - 12-35 to 12-40 & 15-52 to 15-53. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2012-11-29 | 1176 | 1226 | 1255 | 1247 | 10.65 | 4914.65 | 4785 | 129.65 | 4965 | 5.845 | 82.79 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2012-11-30 | 1153 | 1227 | 1250 | 1198 | 17.11 | 4845.11 | 4710 | 135.11 | 4882 | 5.922 | 80.34 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2012-12-01 | 1108 | 1210 | 1198 | 1134 | 24.38 | 4674.38 | 4545 | 129.38 | 4712 | 5.678 | 80.88 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2012-12-02 | 1057 | 1136 | 1125 | 1060 | 1.67 | 4379.67 | 4260 | 119.67 | 4431 | 5.419 | 79.69 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 2012-12-03 | 888 | 961 | 944 | 872 | 7.15 | 3672.15 | 3585 | 87.15 | 3732 | 4.585 | 79.33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2012-12-04 | 1001 | 1063 | 1052 | 981 | 5.25 | 4102.25 | 3990 | 112.25 | 4156 | 5.152 | 78.62 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2012-12-05 | 949 | 978 | 967 | 927 | 37.63 | 3858.63 | 3750 | 108.63 | 3886 | 4.874 | 77.7 | Grid Supply Failure From - 08-51 to 10-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2012-12-06 | 1074 | 1114 | 1091 | 1073 | 47.91 | 4399.91 | 4275 | 124.91 | 4428 | 5.619 | 76.8 | Grid Supply Failure From - 13-31 to 13-34. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2012-12-07 | 1029 | 1063 | 1040 | 1051 | 49.37 | 4232.37 | 4110 | 122.37 | 4260 | 5.592 | 74.24 | Grid Supply Failure From - 09-28 to 09-33,,,,,,11-48 to 11-50, & 13-56 to 13-58. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2012-12-08 | 1075 | 1108 | 1091 | 1126 | 47.82 | 4447.82 | 4335 | 112.82 | 4475 | 5.61 | 77.74 | Grid Supply Failure From -09-00 to 09-17. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2012-12-09 | 1136 | 1176 | 1153 | 1200 | 40.82 | 4705.82 | 4575 | 130.82 | 4734 | 5.981 | 77.14 | Grid Supply Failure From - 09-00 to 09-17. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2012-12-10 | 1097 | 1131 | 1137 | 1171 | 49.77 | 4585.77 | 4455 | 130.77 | 4606 | 5.869 | 76.49 | Plant Break Downed From -10-32 to 10-42, Because of Blown off The D.O.Fuse of `Y` Phase …….Grid Supply Failure From -17-14 to 17-19. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2012-12-11 | 1102 | 1136 | 1175 | 1147 | 36.77 | 4596.77 | 4470 | 126.77 | 4631 | 5.799 | 77.83 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2012-12-12 | 1029 | 1040 | 1114 | 1068 | 35.52 | 4286.52 | 4155 | 131.52 | 4313 | 5.471 | 76.83 | Grid Supply Failure From -13-55 to 14-20.,,,,,,Inv -2 . Shut downed From - 10-05 to 10-20. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2012-12-13 | 950 | 1035 | 1029 | 938 | 23.84 | 3975.84 | 3870 | 105.84 | 4014 | 4.993 | 78.35 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2012-12-14 | 904 | 966 | 1016 | 909 | 26.25 | 3821.25 | 3660 | 161.25 | 3812 | 4.646 | 79.96 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2012-12-15 | 1097 | 1142 | 1042 | 1093 | 22.8 | 4396.8 | 4335 | 61.8 | 4500 | 5.721 | 76.66 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2012-12-16 | 1125 | 1171 | 1131 | 1119 | 19.08 | 4565.08 | 4440 | 125.08 | 4606 | 5.82 | 77.13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 2012-12-17 | 933 | 966 | 932 | 888 | 12.84 | 3731.84 | 3645 | 86.84 | 3788 | 4.724 | 78.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 2012-12-18 | 995 | 1029 | 1001 | 967 | 27.82 | 4019.82 | 3900 | 119.82 | 4061 | 5.127 | 77.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2012-12-19 | 1074 | 1120 | 1080 | 1078 | 23.21 | 4375.21 | 4260 | 115.21 | 4413 | 5.52 | 77.91 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 2012-12-20 | 1221 | 1272 | 1221 | 1277 | 23.37 | 5014.37 | 4860 | 154.37 | 5040 | 6.391 | 76.86 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 2012-12-21 | 1176 | 1221 | 1199 | 1130 | 36.32 | 4762.32 | 4635 | 127.32 | 4796 | 6.183 | 75.6 | Grid Supply Failure From -16-00 to 16-02. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 2012-12-22 | 1148 | 1193 | 1226 | 1199 | 31.93 | 4797.93 | 4665 | 132.93 | 4837 | 6.049 | 77.93 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 2012-12-23 | 995 | 1035 | 1086 | 1024 | 21.55 | 4161.55 | 4035 | 126.55 | 4198 | 5.831 | 70.17 | Plant Shut downed From -12-00 to 12-47 Because of Malted the `R`Phase Arc Rod of 11-kv Isolator. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2012-12-24 | 1176 | 1244 | 1272 | 1215 | 29.68 | 4936.68 | 4800 | 136.68 | 4960 | 6.206 | 77.89 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2012-12-25 | 1170 | 1283 | 1261 | 1211 | 19.49 | 4944.49 | 4800 | 144.49 | 4971 | 6.228 | 77.79 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 2012-12-26 | 1170 | 1231 | 1215 | 1186 | 24.6 | 4826.6 | 4695 | 131.6 | 4875 | 6.198 | 76.66 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 2012-12-27 | 1199 | 1217 | 1187 | 1149 | 23.6 | 4775.6 | 4650 | 125.6 | 4803 | 6.209 | 75.39 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2012-12-28 | 1147 | 1182 | 1125 | 1054 | 22.4 | 4530.4 | 4395 | 135.4 | 4569 | 5.846 | 76.17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2012-12-29 | 1074 | 1125 | 1057 | 1021 | 21.46 | 4298.46 | 4185 | 113.46 | 4337 | 5.334 | 79.24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2012-12-30 | 1029 | 1068 | 1007 | 973 | 22.09 | 4099.09 | 3990 | 109.09 | 4140 | 5.099 | 79.13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2012-12-31 | 1035 | 1080 | 1012 | 984 | 12.48 | 4123.48 | 4020 | 103.48 | 4170 | 5.165 | 78.69 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2013
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2013-01-01 | 955 | 1001 | 950 | 922 | 8.34 | 3836.34 | 3735 | 101.34 | 3893 | 4.867 | 77.96 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2013-01-02 | 1108 | 1159 | 1096 | 1113 | 14.52 | 4490.52 | 4380 | 110.52 | 4540 | 5.69 | 77.76 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2013-01-03 | 1058 | 1102 | 1091 | 1045 | 10.98 | 4306.98 | 4200 | 106.98 | 4356 | 5.351 | 79.34 | Plant Shut downed From 17-30 to 17-55 for Rectification of Oil Leakage Problem in Main X-mer (D-1168) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2013-01-04 | 1091 | 1154 | 1188 | 1092 | 10.99 | 4535.99 | 4395 | 140.99 | 4585 | 5.613 | 79.61 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2013-01-05 | 1125 | 1232 | 1226 | 1132 | 16.34 | 4731.34 | 4590 | 141.34 | 4773 | 5.771 | 80.61 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2013-01-06 | 746 | 814 | 809 | 740 | 13.05 | 3122.05 | 3030 | 92.05 | 3167 | 3.921 | 78.72 | Grid Supply Failure From -09-19 to 11-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2013-01-07 | 984 | 1091 | 1080 | 988 | 25.52 | 4168.52 | 4035 | 133.52 | 4194 | 5.098 | 80.18 | Gris Supply Failure From - 11-27 to 11-30 & 11-31 to 12-29. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2013-01-08 | 1243 | 1368 | 1351 | 1293 | 17.52 | 5272.52 | 5130 | 142.52 | 5308 | 6.413 | 80.67 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2013-01-09 | 1148 | 1255 | 1243 | 1196 | 31.09 | 4873.09 | 4740 | 133.09 | 4882 | 5.976 | 0.7662 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2013-01-10 | 1136 | 1250 | 1233 | 1200 | 22.28 | 4841.28 | 4710 | 131.28 | 4846 | 5.952 | 0.7935 | Grid Supply Failure From - 16-15 to 16-20. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2013-01-11 | 1120 | 1215 | 1198 | 1180 | 13.09 | 4726.09 | 4590 | 136.09 | 4763 | 5.887 | 0.7885 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2013-01-12 | 1142 | 1187 | 1171 | 1149 | 15 | 4664 | 4530 | 134 | 4700 | 5.966 | 0.7678 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2013-01-13 | 1136 | 1159 | 1142 | 1120 | 14.53 | 4571.53 | 4455 | 116.53 | 4612 | 5.832 | 0.7707 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2013-01-14 | 1074 | 1035 | 927 | 999 | 19.83 | 4054.83 | 3945 | 109.83 | 4111 | 5.491 | 72.97 | Every Inverters Intermittent went in Fault Moded during the Period of 13-00 to 16-05 Because of Kite Festivel High Grid Voltages problem Happened Severly for few second only | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2013-01-15 | 1086 | 1108 | 1091 | 1074 | 14.05 | 4373.05 | 4260 | 113.05 | 4418 | 5.266 | 81.77 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2013-01-16 | 995 | 1012 | 1001 | 989 | 17.67 | 4014.67 | 3900 | 114.67 | 4059 | 4.829 | 81.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2013-01-17 | 1080 | 1097 | 1079 | 1077 | 9.09 | 4342.09 | 4245 | 97.09 | 4392 | 5.501 | 77.81 | Grid Supply Failure From -15-30 to 15-35. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2013-01-18 | 1243 | 1255 | 1233 | 1187 | 11.48 | 4929.48 | 4785 | 144.48 | 4966 | 5.84 | 82.87 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2013-01-19 | 1301 | 1300 | 1283 | 1259 | 16.67 | 5159.67 | 5025 | 134.67 | 5188 | 6.417 | 78.79 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2013-01-20 | 1136 | 1136 | 1114 | 1097 | 13.45 | 4496.45 | 4365 | 131.45 | 4527 | 5.608 | 78.67 | Grid Supply Failure From - 11-37 to 12-30 & 18-00 to 18-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2013-01-21 | 1317 | 1329 | 1300 | 1307 | 9.4 | 5262.4 | 5100 | 162.4 | 5295 | 6.514 | 79.22 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2013-01-22 | 1267 | 1272 | 1255 | 1274 | 8.44 | 5076.44 | 4935 | 141.44 | 5110 | 6.165 | 80.78 | Grid Supply Failure From - 09-14 09-22 & 14-10 to 14-27. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2013-01-23 | 1328 | 1334 | 1312 | 1344 | 7.12 | 5325.12 | 5175 | 150.12 | 5365 | 6.653 | 78.59 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2013-01-24 | 1221 | 1233 | 1210 | 1216 | 9.52 | 4889.52 | 4755 | 134.52 | 4930 | 6.157 | 78.04 | Grid Supply From - 12-33 to 12-36 & 16-58 to 17-03. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2013-01-25 | 1261 | 1266 | 1272 | 1261 | 15.82 | 5075.82 | 4920 | 155.82 | 5121 | 6.256 | 79.78 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2013-01-26 | 1238 | 1249 | 1306 | 1234 | 33.97 | 5060.97 | 4920 | 140.97 | 5111 | 6.213 | 80.1784 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2013-01-27 | 1266 | 1278 | 1356 | 1293 | 35.71 | 5228.71 | 5085 | 143.71 | 5284 | 6.485 | 79.4155 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2013-01-28 | 1188 | 1227 | 1284 | 1194 | 4.57 | 4897.57 | 4755 | 142.57 | 4941 | 5.736 | 83.9573 | Grid Supply From - 09-59 to 09-03 & 17-09 to 17-14. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2013-01-29 | 1164 | 1255 | 1255 | 1172 |  | 4846 | 4710 | 136 | 4891 | 5.516 | 86.4223 | Grid Supply From - 14-31 to 15-04. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2013-01-30 | 933 | 1012 | 989 | 910 | 12.55 | 3856.55 | 3750 | 106.55 | 3898 | 4.554 | 83.426 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2013-01-31 | 1086 | 1131 | 1193 | 1020 | 26.93 | 4456.93 | 4245 | 211.93 | 4376 | 4.951 | 86.1464 | Grid Supply Failure From -11-41 to 11-45. & Internet Failure From 17-00 TO 00-00 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
32 | 2013-02-01 | 1192 | 1209 | 1187 | 1103 | 28.05 | 4719.05 | 4590 | 129.05 | 4778 | 5.801 | 80.2779 | Grid Supply Failure From - 15-19 to 15-24 & Internet Failure From - 00-00 to 17-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
33 | 2013-02-02 | 1057 | 1080 | 1051 | 994 | 27.11 | 4209.11 | 4095 | 114.11 | 4259 | 5.257 | 78.96 | Grid Supply Failure From - 09-02 to 09-06. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2013-02-03 | 1063 | 1080 | 1052 | 1003 | 25.3 | 4223.3 | 4110 | 113.3 | 4265 | 5.284 | 78.66 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2013-02-04 | 1086 | 1108 | 1080 | 1045 | 24.39 | 4343.39 | 4215 | 128.39 | 4372 | 5.377 | 79.24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2013-02-05 | 1311 | 1340 | 1306 | 1334 | 14.8 | 5305.8 | 5175 | 130.8 | 5340 | 6.414 | 81.14 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2013-02-06 | 1346 | 1374 | 1379 | 1339 | 17.54 | 5455.54 | 5295 | 160.54 | 5489 | 6.621 | 80.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2013-02-07 | 1391 | 1404 | 1470 | 1277 | 24.61 | 5566.61 | 5475 | 91.61 | 5607 | 6.727 | 81.23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2013-02-08 | 1396 | 1476 | 1487 | 1394 | 17.71 | 5770.71 | 5610 | 160.71 | 5792 | 6.883 | 82.01 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2013-02-09 | 1402 | 1487 | 1458 | 1376 | 16.27 | 5739.27 | 5585 | 154.27 | 5768 | 6.855 | 82.01 | Grid Supply Failure From - 10-39 to 10-42. There was An Error found in The UGVCL. Aggregate Metere Then I Informed to Mr.Booch (Ex.En. UGVCL ) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2013-02-10 | 1295 | 1356 | 1340 | 1233 | 12.65 | 5236.65 | 5085 | 151.65 | 5293 |  |  | Grid Supply Failure From - 16-14 to 16-18 & 16-35 to 16-45 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2013-02-11 | 1227 | 1267 | 1244 | 1161 | 24.46 | 4923.46 | 4800 | 123.46 | 4941 | 5.974 | 80.61 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2013-02-12 | 1249 | 1278 | 1255 | 1198 | 23.54 | 5003.54 | 4860 | 143.54 | 5039 | 5.634 |  | Grid Supply Failure From 14-04 to 14-09. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2013-02-13 | 1272 | 1300 | 1283 | 1257 | 25.24 | 5137.24 | 4995 | 142.24 | 5171 | 6.405 | 78.68 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2013-02-14 | 1108 | 1125 | 1108 | 1098 | 24.88 | 4463.88 | 4350 | 113.88 | 4498 | 5.556 | 78.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2013-02-15 | 560 | 576 | 583 | 562 | 7.61 | 2288.61 | 2220 | 68.61 | 2326 | 2.722 | 83.28 | Grid Supply Failure From -07-30 to 07-35. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2013-02-16 | 1464 | 1521 | 1515 | 1467 | 8.9 | 5975.9 | 5805 | 170.9 | 6005 | 6.947 | 84.24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2013-02-17 | 1385 | 1436 | 1424 | 1358 | 11.49 | 5614.49 | 5475 | 139.49 | 5637 | 6.831 | 80.42 | There was An Error found in The UGVCL. Aggregate Metere Then I Informed to Mr.Bhavsar (JE. UGVCL ) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2013-02-18 | 1368 | 1408 | 1403 | 1374 | 10.99 | 5563.99 | 5410 | 153.99 | 5596 | 6.855 | 79.56 | Grid Supply Failure From - 10-49 to 10-53. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2013-02-19 | 1153 | 1199 | 1192 | 1156 | 12.57 | 4712.57 | 4590 | 122.57 | 4746 | 5.811 | 79.6 | Grid Supply Failure From 10-47 to 11-37 & 14-12 to 14-17. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2013-02-20 | 1351 | 1401 | 1391 | 1363 | 21.66 | 5527.66 | 5430 | 97.66 | 5563 | 6.532 | 83 | Grid Supply Failure From - 07-10 to 07-20 & 10-29 to 10-33 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2013-02-21 | 1318 | 1352 | 1346 | 1315 | 26.68 | 5357.68 | 5205 | 152.68 | 5392 | 6.643 | 79.11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2013-02-22 | 1232 | 1277 | 1277 | 1256 | 30.43 | 5072.43 | 5040 | 32.43 | 5104 | 6.268 |  | Grid Supply Failure From - 10-50 to 10-55 & 13-01 to 13-06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2013-02-23 | 1351 | 1402 | 1431 | 1245 | 34.21 | 5463.21 | 5295 | 168.21 | 5483 |  |  | Internet Failure From - 11-35 to 11-55. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
55 | 2013-02-24 | 1459 | 1504 | 1543 | 1400 | 30.67 | 5936.67 | 5805 | 131.67 | 5952 | 7.238 | 80.14 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2013-02-25 | 1379 | 1442 | 1464 | 1395 | 35.19 | 5715.19 | 5575 | 140 | 5739 | 6.951 | 80.47 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2013-02-26 | 1222 | 1300 | 1289 | 1213 | 23.52 | 5047.52 | 4900 | 147.52 | 5078 | 6.262 | 79.03 | Grid Supply Failure From - 09-55 to 10-10,,11-32 to 11-35,, & 17-13 to 17-20. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2013-02-27 | 1452 | 1538 | 1515 | 1460 | 25.38 | 5990.38 | 5850 | 140.38 | 6022 | 7.249 | 80.96 | Grid Supply Failure From - 09-39 to 09-44. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2013-02-28 | 1516 | 1560 | 1532 | 1463 | 26.2 | 6097.2 | 5940 | 157.2 | 6119 | 7.541 | 79.08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 2013-03-01 | 1487 | 1521 | 1499 | 1452 | 0.91 | 5959.91 | 5810 | 149.91 | 5981 | 7.519 | 77.5294 | Grid Supply Failure From - 06-45 to 07-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2013-03-02 | 1531 | 1566 | 1537 | 1279 | 21.85 | 5934.85 | 5795 | 149.85 | 5979 | 7.727 | 75.4172 | Grid Supply Failure From - 07-35 to 07-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2013-03-03 | 1487 | 1515 | 1493 | 1468 | 8.72 | 5971.72 | 5825 | 146.72 | 6019 | 7.568 | 77.51 | Grid Supply Failure From- 08-50 to 08-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2013-03-04 | 1363 | 1396 | 1368 | 1352 | 11.91 | 5490.91 | 5345 | 145.91 | 5526 | 7.141 | 75.42 | Grid Supply Failure From - 10-16 to 10-21. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2013-03-05 | 1402 | 1431 | 1408 | 1412 | 27.81 | 5680.81 | 5530 | 150.81 | 5698 | 6.593 | 84.23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2013-03-06 | 1362 | 1390 | 1390 | 1385 | 40.89 | 5567.89 | 5415 | 152.89 | 5556 | 6.871 | 78.81 | Grid Supply Failure From - 13-46 to 13-52. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2013-03-07 | 1357 | 1386 | 1425 | 1293 | 36.48 | 5497.48 | 5355 | 142.48 | 5479 | 7.01 | 76.17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2013-03-08 | 1301 | 1362 | 1379 | 1319 | 41.64 | 5402.64 | 5260 | 142.64 | 5400 | 6.846 | 76.87 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2013-03-09 | 1339 | 1436 | 1419 | 1348 | 36.07 | 5578.07 | 5430 | 148.7 | 5593 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2013-03-10 | 1329 | 1402 | 1386 | 1320 | 8.45 | 5445.45 | 5310 | 135.45 | 5461 | 6.65 | 80.0393 | Grid Supply Failure From - 11-35 to 11-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2013-03-11 | 1142 | 1210 | 1198 | 1104 | 37.52 | 4691.52 | 4537 | 154.52 | 4739 | 5.767 | 80.092 | Grid Supply Failure From - 09-30 to 09-36. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2013-03-12 | 1396 | 1436 | 1419 | 1369 | 35.35 | 5655.35 | 5510 | 145.35 | 5680 | 6.51 | 85.0394 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2013-03-13 | 1357 | 1374 | 1357 | 1317 | 37.33 | 5442.33 | 5310 | 132.33 | 5474 | 6.912 | 77.18 | Aggregate Meter Replaced by UGVCL Between - 09 to 10-00. Grid Supply Failure From - 09-17 to 09-21. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2013-03-14 | 1351 | 1379 | 1362 | 1316 | 33.08 | 5441.08 | 5310 | 131.08 | 5453 | 6.789 | 78.28 | Grid Supply Failure From - 09-17 to 09-21. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2013-03-15 | 1251 | 1374 | 1357 | 1349 | 28.22 | 5359.22 | 5230 | 129.22 | 5470 | 6.915 | 77.0988 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2013-03-16 | 1250 | 1272 | 1278 | 1199 | 23.56 | 5022.56 | 4900 | 122.56 | 5060 | 6.377 | 77.33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2013-03-17 | 1362 | 1379 | 1413 | 1387 | 15.02 | 5556.02 | 5410 | 146.02 | 5587 | 6.906 | 78.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2013-03-18 | 1318 | 1340 | 1391 | 1320 | 24.92 | 5393.92 | 5250 | 143.92 | 5406 | 6.378 | 82.61 | Grid Supply Failure From - 10-03 to 10-08 & 13-07 to 13-12. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2013-03-19 | 1260 | 1329 | 1345 | 1310 | 37 | 5281 | 5140 | 141 | 5316 | 6.695 | 77.39 | Grid Supply Failure From - 09-55 to 09-57. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2013-03-20 | 1380 | 1481 | 1453 | 1376 | 40.84 | 5730.84 | 5590 | 140.84 | 5744 | 6.937 | 80.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2013-03-21 | 1413 | 1464 | 1442 | 1384 | 57.02 | 5760.02 | 5635 | 125.02 | 5783 | 6.98 | 80.7515 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2013-03-22 | 984 | 1001 | 989 | 951 | 21.71 | 3946.71 | 3834.25 | 112.46 | 3969 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2013-03-23 | 1374 | 1407 | 1380 | 1360 | 21.89 | 5542.89 | 5375.25 | 167.64 | 5544 | 6.916 | 78.1305 | Plant Shut Downed From- 10-31 to 10-41 ,For Replaced The `R`,D.O.Fuse Link . Grid Supply Failure From - 16-50 to 16-53. | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
84 | 2013-03-24 | 1447 | 1482 | 1458 | 1456 | 13.11 | 5856.11 | 5676.75 | 179.36 | 5886 | 7.293 | 78.6623 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2013-03-25 | 1407 | 1436 | 1408 | 1410 | 17.17 | 5678.17 | 5508.75 | 169.42 | 5711 | 6.856 | 81.18 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2013-03-26 | 1142 | 1164 | 1148 | 1168 | 17.36 | 4639.36 | 4507.5 | 131.86 | 4684 | 5.805 | 78.64 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2013-03-27 | 1125 | 1148 | 1125 | 1138 | 0.59 | 4536.59 | 4393.5 | 143.09 | 4573 | 5.574 | 79.96 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2013-03-28 | 1380 | 1413 | 1385 | 1383 | 23.89 | 5584.89 | 5420.25 | 164.64 | 5611 | 6.943 | 78.76 | Grid Supply Failure From - 14-05 to 14-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2013-03-29 | 1402 | 1436 | 1458 | 1434 | 27.88 | 5757.88 | 5575.5 | 182.38 | 5789 | 7.021 | 80.36 | Grid Supply Failure From - 15-15 to 15-20. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2013-03-30 | 1362 | 1402 | 1442 | 1358 | 18.28 | 5582.28 | 5402.25 | 180.03 | 5616 | 7.263 | 75.36 | Plant Break Downed From - 13-12 to 13-25 Because of Blown of The D.O.Fuse of `R` Phase. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2013-03-31 | 1284 | 1312 | 1351 | 1291 | 15.19 | 5253.19 | 5091 | 162.19 | 5296 | 6.839 | 0.7547 | Plnt Break Downed From 09-50 to 10-04 Because of Blown off The D.O.Fuse of `R` Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2013-04-01 | 1368 | 1413 | 1459 | 1374 | 9.65 | 5623.65 | 5446.5 | 177.15 |  |  |  | Internet Failure From -12-30 to 00-00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
94 | 2013-04-02 | 1374 | 1464 | 1475 | 1409 | 13.6 | 5735.6 | 5556.75 | 178.85 | 5897 |  |  | Grid Supply Failure From - 07-57 to 08-01. Internet Failure From - 00-00 to 16-00 and after also Failure for Intermittent Period Till to 19- 00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
95 | 2013-04-03 | 1317 | 1425 | 1408 | 1360 | 12.11 | 5522.11 | 5345.25 | 176.86 | 5564 | 6.869 | 78.94 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2013-04-04 | 1345 | 1442 | 1413 | 1379 | 17.82 | 5596.82 | 5421.75 | 175.07 | 5634 |  |  | Grid Supply Failure From - 14-42 to 14-46. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2013-04-05 | 1391 | 1447 | 1419 | 1362 | 18.59 | 5637.59 | 5465.25 | 172.34 | 5679 | 7.204 | 76.83 | Grid Supply Failure From - 18-11 to 18-16. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2013-04-06 | 1397 | 1413 | 1385 | 1338 | 19.64 | 5552.64 | 5373.75 | 178.89 | 5596 | 7.109 | 76.22 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2013-04-07 | 1407 | 1431 | 1402 | 1397 | 10.04 | 5647.04 | 5476.5 | 170.54 | 5687 | 7.2 |  | Grid Supply Failure From - 8-10 to 8-20. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2013-04-08 | 1216 | 1232 | 1210 | 1213 | 30.22 | 4901.22 | 4743.75 | 157.47 | 4940 | 5.799 | 83.02 | Grid SUPPLY Failure From - 07-35 to 07-40,,,09-38 to 09-40 & 10-38 to 10-42. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2013-04-09 | 1198 | 1215 | 1199 | 1228 | 16.77 | 4856.77 | 4683.75 | 173.02 | 4899 | 6.029 | 79.19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2013-04-10 | 1278 | 1301 | 1289 | 1332 | 44.99 | 5244.99 | 5076.75 | 168.24 | 5272 | 6.464 | 79.49 | Grid Supply Failure From - 09-33 to 09-38. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2013-04-11 | 1306 | 1328 | 1357 | 1361 | 30.48 | 5382.48 | 5217.75 | 164.73 | 5417 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2013-04-12 | 1317 | 1357 | 1385 | 1302 | 39.72 | 5400.72 | 5234.25 | 166.47 | 5441 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2013-04-13 | 1340 | 1430 | 1419 | 1381 | 31.63 | 5601.63 | 5425.5 | 176.13 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2013-04-14 | 1323 | 1425 | 1396 | 1392 | 9.84 | 5545.84 | 5368.5 | 177.34 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2013-04-15 | 1311 | 1413 | 1374 | 1366 | 23.77 | 5487.77 | 5338.5 | 149.27 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2013-04-16 | 1380 | 1453 | 1408 | 1418 | 23.07 | 5682.07 | 5496 | 186.07 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2013-04-17 | 1294 | 1318 | 1283 | 1286 | 34.96 | 5215.96 | 5051.25 | 164.71 | 5241 | 6.563 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2013-04-18 | 1092 | 1102 | 1068 | 1078 | 28.61 | 4368.61 | 4248 | 120.61 | 4384 | 5.309 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2013-04-19 | 1266 | 1283 | 1250 | 1265 | 24.86 | 5088.86 | 4945.5 | 143.36 | 5130 | 6.512 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2013-04-20 | 1286 | 1312 | 1283 | 1322 | 13.86 | 5216.86 | 5049 | 167.86 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2013-04-21 | 1137 | 1165 | 1153 | 1186 | 2.83 | 4643.83 | 4496.25 | 147.58 | 5176 |  |  | Grid Supply From 11-15 to 11-56 & 16-55 to 17-00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2013-04-22 | 932 | 966 | 950 | 956 | 16.81 | 3820.81 | 3680.25 | 140.56 | 3858 | 4.774 | 78.76 | Internet Failure From -10-45 to 13-30. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
115 | 2013-04-23 | 1312 | 1346 | 1340 | 1362 | 22.92 | 5382.92 | 5198.25 | 184.67 | 5418 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2013-04-24 | 1261 | 1311 | 1300 | 1304 | 12.1 | 5188.1 | 5024.25 | 163.85 |  |  |  | Internet Failure From - 13-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
117 | 2013-04-25 | 1368 | 1436 | 1419 | 1416 | 12.08 | 5651.08 | 5448.75 | 202.33 |  |  |  | Internet Failure From -00-00 to 10-30. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
118 | 2013-04-26 | 1385 | 1470 | 1436 | 1422 | 5.6 | 5718.6 | 5517 | 201.6 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2013-04-27 | 1362 | 1448 | 1408 | 1431 | 7.03 | 5656.03 | 5466.75 | 189.28 | 5702 |  |  | Grid Supply Failure From - 10-32 to 10-35,,,,Internet Disconnectivity Problem From - 08-15 to 17-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
120 | 2013-04-28 | 1312 | 1385 | 1357 | 1368 | 2.99 | 5424.99 | 5230.5 | 194.49 | 5463 | 6.802 | 78.27 | Grid Supply Failure From - 08-35 to 08-38. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2013-04-29 | 1345 | 1419 | 1379 | 1403 | 17.34 | 5563.34 | 5377.5 | 185.84 | 5610 | 6.954 | 78.62 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2013-04-30 | 1386 | 1424 | 1385 | 1406 | 30 | 5631 | 5439 | 192 | 5664 | 7.11 | 77.64 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2013-05-01 | 1396 | 1414 | 1368 | 1353 | 16.63 | 5547.63 | 5363.25 | 184.38 | 5586 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2013-05-02 | 1425 | 1441 | 1402 | 1453 | 27.95 | 5748.95 | 5550 | 198.95 | 5781 |  |  | Grid Supply Failure From - 17-08 to 17-12. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2013-05-03 | 1390 | 1408 | 1374 | 1467 | 13.53 | 5652.53 | 5453.25 | 199.28 | 5690 | 7.119 | 77.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2013-05-04 | 1369 | 1391 | 1351 | 1469 | 24.2 | 5604.2 | 5407.5 | 196.7 | 5642 | 7.077 | 77.7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2013-05-05 | 1385 | 1402 | 1374 | 1485 | 11.48 | 5657.48 | 5460 | 197.48 | 4158 |  |  | Grid Supply Failure From - 17-49 to 17-54,,,,Internet Failure From - 09-30 to 00-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
129 | 2013-05-06 | 1317 | 1345 | 1306 | 1427 |  | 5395 | 5241 | 154 | 5832 |  |  | Internet Failure From -00-00 to 09-45. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
130 | 2013-05-07 | 1266 | 1284 | 1249 | 1362 |  | 5161 | 5004.75 | 156.25 | 5226 |  |  | Internet Failure From -05-00 to 11-45. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
131 | 2013-05-08 | 1346 | 1373 | 1369 | 1442 | 27.01 | 5557.01 | 5357.2 | 199.76 | 5597 | 7.028 | 77.6205 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2013-05-09 | 1334 | 1357 | 1396 | 1422 | 21 | 5530 | 5352.75 | 177.25 | 5562 |  |  | Grid Supply Failure From - 10-18 to 10-23,,,, Internet Failure From -06-00 to 09-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
133 | 2013-05-10 | 1232 | 1289 | 1306 | 1303 | 17.07 | 5147.07 | 4974 | 173.07 | 5186 | 6.628 | 76.26 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2013-05-11 | 1255 | 1346 | 1340 | 1333 | 8.5 | 5282.5 | 5085.75 | 196.75 | 5325 | 6.703 | 77.42 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2013-05-12 | 1261 | 1356 | 1334 | 1336 | 2.98 | 5289.98 | 5095.5 | 194.48 | 5336 |  |  | Internet Failure From - 12-30 to 13-30. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
136 | 2013-05-13 | 1249 | 1352 | 1317 | 1328 | 20.41 | 5266.41 | 5076 | 190.41 | 5299 | 6.766 | 76.33 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2013-05-14 | 1244 | 1323 | 1289 | 1298 | 27.74 | 5181.74 | 4993.5 | 188.24 | 5227 |  |  | Internet Failure From 11-30 to 11-45. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
138 | 2013-05-15 | 1306 | 1339 | 1295 | 1310 | 15.83 | 5265.83 | 5081.25 | 184.58 | 5308 |  |  | Internet Failure From - 10-30 to 11-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
139 | 2013-05-16 | 1351 | 1352 | 1317 | 1343 | 13.52 | 5376.52 | 5189.25 | 187.27 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2013-05-17 | 1306 | 1322 | 1283 | 1349 | 15.64 | 5275.64 | 5090.25 | 185.39 | 5285 | 6.86 | 75.0885 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2013-05-18 | 1329 | 1340 | 1306 | 1413 | 8.59 | 5396.59 | 5198.25 | 198.34 |  |  |  | Internet Failure From 00-00 to 21-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
142 | 2013-05-19 | 1294 | 1312 | 1272 | 1389 | 6.45 | 5273.45 | 5081.25 | 192.2 | 5317 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2013-05-20 | 1244 | 1266 | 1244 | 1353 | 22.93 | 5129.93 | 4932 | 197.93 |  |  |  | Grid Supply Failure From - 07-21 to 07-26,,,,, 09-59 to 10-02,,,10-05 to 10-07 & 10-38 to 10-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2013-05-21 | 1278 | 1295 | 1289 | 1380 | 16.82 | 5258.82 | 5071.5 | 187.32 | 5300 | 6.622 | 78 | Grid Supply Failure From - 11-25 to 11-30. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2013-05-22 | 1289 | 1300 | 1278 | 1399 | 20.92 | 5286.92 | 5130 | 156.92 | 5370 | 6.946 | 75.35 | Grid Supply Failure From - 08-11 to 08-15,,,13-00 to 13-04 & 18-36 to 18-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2013-05-23 | 1295 | 1317 | 1368 | 1408 | 24.38 | 5412.38 | 5223.75 | 188.63 | 5460 | 6.902 | 77.1 | Grid Supply Failure From - 18-33 to 18-37. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2013-05-24 | 1277 | 1323 | 1363 | 1390 | 20.92 | 5373.92 | 5181.75 | 192.17 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2013-05-25 | 1170 | 1255 | 1243 | 1266 | 23.79 | 4957.79 | 4771.5 | 186.29 | 5080 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2013-05-26 | 1052 | 1142 | 1137 | 1142 | 14.17 | 4487.17 | 4319.25 | 167.92 |  |  |  | Internet Failure From - 7-30 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
150 | 2013-05-27 | 1097 | 1182 | 1147 | 1168 | 13.21 | 4607.21 | 4432.5 | 174.71 | 4937 |  |  | Internet Failure From 00-00 to 11-15. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
151 | 2013-05-28 | 1193 | 1244 | 1205 | 1221 | 19.42 | 4882.42 | 4702.5 | 179.92 | 4924 | 5.917 | 81.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2013-05-29 | 1334 | 1368 | 1334 | 1364 | 22.13 | 5422.13 | 5220 | 202.13 | 5456 | 6.573 | 80.9 | Grid Supply Failure From - 07-17 to 07-23,,,14-46 to 14-50 & 18-35 to 18-38. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2013-05-30 | 1311 | 1340 | 1000 | 1369 | 28.87 | 5048.87 | 4854.75 | 194.12 | 5086 | 6.587 | 75.25 | Grd Supply Failure From - 07-55 to 08-10,,,Inverter-3 Not Auto.started after Returned the GRID, Restarted From - 10-50. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2013-05-31 | 1295 | 1328 | 1312 | 1382 | 43.44 | 5360.44 | 5160 | 200.44 | 5391 | 6.5 | 80.83 | Grid Supply Failure From - 07-30 to 07-33. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2013-06-01 | 1261 | 1295 | 1278 | 1378 | 35.31 | 5247.31 | 5061.75 | 185.56 | 5287 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2013-06-02 | 1193 | 1221 | 1209 | 1297 | 9.37 | 4929.37 | 4771.5 | 157.87 | 4976 | 6.121 | 79.23 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2013-06-03 | 859 | 882 | 877 | 927 | 35.42 | 3580.42 | 3475.5 | 104.92 | 3619 | 4.353 | 80.03 | Grid Supply Failure From - 18-43 to 20-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2013-06-04 | 1017 | 1040 | 1051 | 1094 | 21.94 | 4223.94 | 4095.75 | 128.19 | 4261 | 5.235 | 79.33 | Grid Supply Failure From - 09-38 to 09-43 & 21-15 to 00-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2013-06-05 | 1063 | 1102 | 1108 | 1125 | 31.94 | 4429.94 | 4302 | 127.94 | 4455 |  |  | Grid Supply From - 00-00 to 05-15 & 15-14 to 15-22. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2013-06-06 | 1074 | 1109 | 1120 | 1139 | 28.35 | 4470.35 | 4306.5 | 163.85 | 4513 |  |  | Grid Supply From -16-10 to 16-25. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2013-06-07 | 979 | 1006 | 1006 | 1025 | 30.34 | 4046.34 | 3884.25 | 162.09 | 4081 |  |  | Grid Supply Failure From - 07-10 to 07-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2013-06-08 | 1096 | 1125 | 1136 | 1161 | 16.05 | 4534.05 | 4397.25 | 136.8 | 4589 |  |  | Grid Supply Failure From - 08-09 to 08-14. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2013-06-09 | 990 | 1023 | 1035 | 1049 | 7.27 | 4104.27 | 3977.25 | 127.02 | 4142 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2013-06-10 | 650 | 667 | 678 | 678 | 8.25 | 2681.25 | 2550.75 | 130.5 | 2720 |  |  | Grid Supply Failure From -10-13 to 10-27,,11-11 to 12-01,,13-53 to 13-56,,17-22 to 17-28,,17-57 to 18-07 & 19-03 to 19-08 and Because of Heavy Cloud Inv-1 & Inv-4 Went to Sleep mode From - 11-02 to 11-09. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2013-06-11 | 752 | 780 | 792 | 784 | 4.68 | 3112.68 | 2972.25 | 140.43 | 3150 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2013-06-12 | 966 | 996 | 1006 | 1020 | 12.08 | 4000.08 | 3868.5 | 131.58 | 3919 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2013-06-13 | 916 | 944 | 956 | 941 | 7.98 | 3764.98 | 3630.75 | 134.23 | 2903 |  |  | Grid Supply Failure From - 09-11 to 09-14,,,09-19 to 09-22,,,09-26 to 09-28,,,09-34 to 09-36,,,09-56 to 09-58. Internet Failure From - 09-58 to 12-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
169 | 2013-06-14 | 1069 | 1091 | 1096 | 1131 | 21.28 | 4408.28 | 4254.75 | 153.53 | 5479 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 2013-06-15 | 1113 | 1147 | 1142 | 1180 | 4.04 | 4586.04 | 4462.5 | 123.54 | 4605 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2013-06-16 | 1097 | 1125 | 1131 | 1148 | 0.32 | 4501.32 | 4365.75 | 135.57 | 4541 |  |  | Because of Cyclone Grid Supply Failure From - 18-50 to 22-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 2013-06-17 | 577 | 594 | 599 | 598 | 17.82 | 2385.82 | 2325.75 | 60.07 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 2013-06-18 | 605 | 628 | 639 | 623 | 19.36 | 2514.36 | 2445.75 | 68.61 |  |  |  | Grid Supply Failure From - 14-40 to 14-50. Internet Failure From 00-00 to 13-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
174 | 2013-06-19 | 983 | 1000 | 995 | 1034 | 37.42 | 4049.42 | 3928.5 | 120.92 |  |  |  | Grid Supply Failure From - 18-35 to 18-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 2013-06-20 | 1080 | 1097 | 1073 | 1108 | 41.17 | 4399.17 | 4239 | 160.17 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2013-06-21 | 1148 | 1159 | 1177 | 1155 | 50.98 | 4689.98 | 4509 | 180.98 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2013-06-22 | 1023 | 1034 | 1125 | 1071 | 26.57 | 4279.57 | 4113.75 | 165.82 |  |  |  | Grid Supply Failure From - 14-11 to 14-17. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 2013-06-23 | 1035 | 1052 | 1153 | 1059 | 21.09 | 4320.09 | 4156.5 | 163.59 |  |  |  | Grid SUPPLY Failure From - 12-06 to 12-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 2013-06-24 | 961 | 1001 | 1052 | 1006 | 38.75 | 4058.75 | 3894 | 164.75 |  |  |  | Grid Supply Failure From - 13-00 to 13-05,,,13-24 to 13-27 & 17-10 to 17-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2013-06-25 | 853 | 938 | 927 | 900 | 10.01 | 3628.01 | 3510 | 118.01 | 3674 |  |  | Grid Supply Failure From - 09-25 to 09-55,,,11-24 to 11-29 & 18-08 to 18-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2013-06-26 | 555 | 599 | 588 | 526 | 15.45 | 2283.45 | 2194.5 | 88.95 | 2330 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2013-06-27 | 921 | 950 | 939 | 917 | 23.97 | 3750.97 | 3597 | 153.97 | 3787 |  |  | Grid Supply Failure From - 10-24 to 10-29. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2013-06-28 | 1057 | 1086 | 1085 | 1111 | 14.17 | 4353.17 | 4182 | 171.17 | 4390 |  |  | Grid Supply Failure From - 11-34 to 11-39. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2013-06-29 | 922 | 944 | 938 | 962 | 12.72 | 3778.72 | 3614.25 | 164.47 | 3824 |  |  | Grid Supply Failure From - 14-03 to 14-08,,,15-36 to 15-42,,,16-06 to 16-10 & 16-58 to 17-02 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 2013-06-30 | 825 | 848 | 843 | 834 | 18.4 | 3368.4 | 3225 | 143.4 | 3410 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 2013-07-01 | 944 | 966 | 961 | 916 | 41.44 | 3828.44 | 3669.75 | 158.69 | 3869 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2013-07-02 | 854 | 882 | 870 | 898 | 28.73 | 3532.73 | 3382.5 | 150.23 | 3581 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2013-07-03 | 452 | 470 | 475 | 476 | 10.81 | 1883.81 | 1799.25 | 84.56 |  |  |  | Grid Supply Failure From - 08-38 to 08-42. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2013-07-04 | 62 | 62 | 63 | 62 | 0.9 | 249.9 | 209.25 | 40.65 |  |  |  | Grid Supply Failure From - 07-16 to 08-30, Because of Heavy Cloud All Inverters Intermittent went to Sleep Mode. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2013-07-05 | 735 | 752 | 763 | 782 | 13.1 | 3045.1 | 2928 | 117.1 | 3161 |  |  | Grid Supply Failure From - 08-23 to 08-27 & 11-35 to 11-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2013-07-06 | 814 | 848 | 848 | 850 | 11.95 | 3371.95 | 3238.5 | 133.45 | 3416 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 2013-07-07 | 877 | 899 | 904 | 924 | 4.99 | 3608.99 | 3497.25 | 111.74 | 3655 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2013-07-08 | 978 | 1017 | 1024 | 1042 | 8.82 | 4069.82 | 3936.75 | 133.07 | 4068 |  |  | Grid Supply Failure From - 09-17 to 09-22. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 2013-07-09 | 786 | 809 | 814 | 836 | 8.45 | 3253.45 | 3129.75 | 123.7 | 3353 |  |  | Grid Supply Failure From - 10-52 to 10-57,,,14-47 to 14-54 & 16-38 to 16-46. Internet failure from - 00-00 to 10-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
196 | 2013-07-10 | 978 | 1012 | 1017 | 1031 | 14.22 | 4052.22 | 3886.5 | 165.72 | 4095 |  |  | Grid Supply Failure From - 12-34 to 12-42, Internet Failure From - 15-15 to 17-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
197 | 2013-07-11 | 582 | 605 | 611 | 598 | 11.71 | 2407.71 | 2343 | 64.71 | 2459 |  |  | Grid Supply Failure From - 07-47 to 07-51 & 15-30 to 15-35. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2013-07-12 | 724 | 751 | 757 | 758 | 13.33 | 3003.33 | 2902.5 | 100.83 | 3057 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 2013-07-13 | 452 | 464 | 475 | 459 | 6.17 | 1856.17 | 1789.5 | 66.67 | 1909 | 2.185 | 85.15 | Grid Supply Failure From - 10-48 to 10-52 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 2013-07-14 | 429 | 441 | 453 | 446 | 7.01 | 1776.01 | 1692 | 84.01 | 1830 | 3.189 | 55.93 | Grid Supply Failure From - 12-42 to 14-49. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 2013-07-15 | 905 | 944 | 944 | 959 | 13.81 | 3765.81 | 3643.5 | 122.31 | 3810 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 2013-07-16 | 763 | 786 | 791 | 786 | 13.82 | 3139.82 | 3033.75 | 106.07 | 3181 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 2013-07-17 | 520 | 537 | 549 | 534 | 13.31 | 2153.31 | 2061.75 | 91.56 | 2200 |  |  | Grid Supply Failure From - 13-37 to 13-42 & 15-29 to 15-39. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 2013-07-18 | 696 | 724 | 723 | 724 | 12.73 | 2879.73 | 2743.5 | 136.23 | 2925 |  |  | Grid Supply Failure From - 11-37 to 12-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2013-07-19 | 797 | 819 | 820 | 825 | 13.56 | 3274.56 | 3128.25 | 146.31 | 3322 | 4.039 | 80.16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 2013-07-20 | 916 | 944 | 950 | 952 | 10.33 | 3772.33 | 3632.25 | 140.08 | 3807 |  |  | Seeds Box Shutdowned From -11-40 to 19-45 for it`s Mantainace. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 2013-07-21 | 1113 | 1148 | 1159 | 1162 | 2.58 | 4584.58 | 4428.75 | 155.83 | 4631 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 2013-07-22 | 775 | 797 | 797 | 805 | 16.02 | 3190.02 | 3078 | 112.02 | 3238 |  |  | Grid Supply Failure From - 17-28 to 17-36. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 2013-07-23 | 582 | 605 | 610 | 601 | 14.01 | 2412.01 | 2317.5 | 94.51 | 2465 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 2013-07-24 | 175 | 192 | 198 | 185 | 3.18 | 753.18 | 702.75 | 50.43 | 811 | 1.019 | 77.571 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 2013-07-25 | 331 | 351 | 351 | 342 | 6.42 | 1381.42 | 1335 | 46.42 | 1438 | 1.667 | 84.0768 | Grid Supply Failure From - 17-48 to 17-49. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 2013-07-26 | 655 | 678 | 684 | 685 | 9.09 | 2711.09 | 2619 | 92.09 | 2759 | 3.3 | 81.48 | Grid Supply Failure From - 13-12 to 13-19 & 18-06 to 18-11. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 2013-07-27 | 628 | 651 | 661 | 641 | 8.81 | 2589.81 | 2496 | 93.81 | 2610 |  |  | Internet Failure From - 11-15 to 15-15. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
214 | 2013-07-28 | 396 | 412 | 413 | 405 | 7.43 | 1633.43 | 1569.75 | 63.68 |  |  |  | Grid Supply Failure From - 9-22 to 9-27. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 2013-07-29 | 458 | 475 | 486 | 474 | 11.12 | 1904.12 | 1849.5 | 54.62 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2013-07-30 | 576 | 599 | 605 | 592 | 13.06 | 2385.06 | 2305.5 | 79.56 |  |  |  | Grid Supply Failure From - 16-05 to 16-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 2013-07-31 | 611 | 633 | 633 | 625 | 10.73 | 2512.73 | 2406.75 | 105.98 |  |  |  | Grid Supply Failure From - 8-25 to 8-30 & 9-11 to 9-16 & 19-21 to 19-25. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 2013-08-01 | 316 | 328 | 339 | 322 | 6.06 | 1311.06 | 1248.75 | 62.31 |  |  |  | Grid Supply Failure From 16-31 to 16-36. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 2013-08-02 | 526 | 549 | 549 | 544 | 7.06 | 2175.06 | 2068.5 | 106.56 |  |  |  | Grid Supply Failure From - 13-32 to 13-40 & 14-20 to 14-25, Because of Heavy Cloud and Rain all Inverters Intermittent went to Sleep mode. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 2013-08-03 | 419 | 429 | 435 | 430 | 5.6 | 1718.6 | 1662 | 56.6 | 1631 | 2.099 | 75.73 | Because of Heavy Cloud and Rain All Inverters Intermittent Went to Sleep mode During Up to 09-17. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 2013-08-04 | 650 | 673 | 679 | 686 | 9.34 | 2697.34 | 2601.75 | 95.59 | 2763 | 3.186 | 84.52 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 2013-08-05 | 1147 | 1187 | 1192 | 1142 | 14.69 | 4682.69 | 4605 | 77.69 | 4793 | 5.878 | 79.47 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 2013-08-06 | 775 | 798 | 792 | 801 | 6.64 | 3172.64 | 3066 | 106.64 | 3214 | 3.935 | 79.6 | Grid Supply Failure From - 14-17 to 14-24 & 19-00 to 19-03. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 2013-08-07 | 893 | 921 | 927 | 929 | 21.49 | 3691.49 | 3582 | 109.49 | 3737 | 4.516 | 80.65 | Grid Supply Failure From - 10-42 to 10-47. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 2013-08-08 | 826 | 842 | 842 | 859 | 16.16 | 3385.16 | 3259.5 | 125.66 | 3429 | 4.143 | 80.66 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 2013-08-09 | 661 | 679 | 684 | 686 | 3.83 | 2713.83 | 2636.25 | 77.58 | 2755 | 3.277 | 81.84 | Grid Supply Failure From - 06-20 to 06-25,,,Inv 1,2,3 Started From - 07-35 After Reset it Manually. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 2013-08-10 | 339 | 356 | 362 | 349 | 7.53 | 1413.53 | 1359.75 | 53.78 | 1449 | 1.698 | 83.17 | Grid Supply Failure From - 08-25 to 08-30. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 2013-08-11 | 990 | 1023 | 1023 | 1044 | 5.54 | 4085.54 | 3947.25 | 138.29 | 4125 | 5.006 | 80.31 | Grid Supply Failure From - 13-44 to 13-49. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 2013-08-12 | 785 | 814 | 826 | 816 | 12.29 | 3253.29 | 3139.5 | 113.79 | 3292 | 3.97 | 80.82 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 2013-08-13 | 390 | 407 | 413 | 402 | 6.25 | 1618.25 | 1565.25 | 53 | 1660 | 1.935 | 83.61 | Because of Cloud Inv- 2 & 3 Started From - 7-43 and Inv -1 & 4 Started From - 8-37. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 2013-08-14 | 809 | 826 | 831 | 847 | 13.74 | 3326.74 | 3242.25 | 84.49 | 3372 | 3.902 | 84.22 | Internet Failure From -08-30 to 13-00,,,,Grid Supply Failure From - 17-16 to 17-21. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
233 | 2013-08-15 | 786 | 819 | 819 | 825 | 0.13 | 3249.13 | 3103.5 | 145.63 | 3289 | 3.943 | 81.29 | Internet Failure From -11-00 to 11-15,,,, Grid Supply Failure From - 09-19 to 09-23. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
234 | 2013-08-16 | 509 | 532 | 526 | 523 | 7.75 | 2097.75 | 2040.75 | 57 | 2141 | 2.571 | 81.16 | Grid Supply Failure From - 16-57 to 17-03. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 2013-08-17 | 797 | 820 | 814 | 830 | 21.38 | 3282.38 | 3170 | 112.38 | 3321 | 3.976 | 81.4 | Grid Supply Failure From - 12-37 to 12-42. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 2013-08-18 | 769 | 802 | 792 | 792 | 11.67 | 3166.67 | 3069.75 | 96.92 | 3204 | 3.833 | 81.47 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 2013-08-19 | 915 | 944 | 927 | 945 | 25.63 | 3756.63 | 3603.75 | 152.88 | 3797 | 4.432 | 83.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 2013-08-20 | 1074 | 1109 | 1091 | 1119 | 1.24 | 4394.24 | 4230.75 | 163.49 | 4434 |  |  | Grid Supply Failure From - 08-39 to 08-44 & 11 - 28 to 11-33. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 2013-08-21 | 741 | 768 | 758 | 754 | 19.4 | 3040.4 | 2932.5 | 107.9 | 3083 | 3.649 | 82.34 | Plnt Break Downed From 10-50 to 10-02 Because of Blown off The D.O.Fuse of 'B' Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 2013-08-22 | 1069 | 1103 | 1074 | 1119 | 25.96 | 4390.96 | 4245 | 145.96 | 4424 | 5.466 | 78.88 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 2013-08-23 | 978 | 1006 | 989 | 1025 | 28.56 | 4026.56 | 3895 | 131.56 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 2013-08-24 | 548 | 577 | 565 | 567 | 9.4 | 2266.4 | 2202.75 | 63.65 |  |  |  | Grid Supply Failure From - 13-25 to 13-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 2013-08-25 | 452 | 469 | 475 | 457 | 9.38 | 1862.38 | 1787.25 | 75.13 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 2013-08-26 | 611 | 633 | 566 | 630 | 9.25 | 2449.25 | 2348.25 | 101 |  |  |  | Grid Supply Failure From - 13-32 to 14-30 & 14 - 33 to 15-25. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 2013-08-27 | 1198 | 1238 | 887 | 1258 | 14.17 | 4595.17 | 4426.5 | 168.67 |  |  |  | Inv-3 Intermittent went to Sleep mode During the Period of 11-10 to 12-00 .Because of It`s High Temp due to Cooling fan Problem. Then I Switch off it`s 1-AJB( out of 6-AJB ) From 12-00 to 16-00 For Temp solution. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 2013-08-28 | 1103 | 1137 | 916 | 1156 | 9.8 | 4321.8 | 4140 | 181.8 |  |  |  | I switch off The AJB-114 of The Inv-3 From - 10-52 to 15-02 For stabilize it`s High Voltage Problem during The Period. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 2013-08-29 | 1187 | 1227 | 916 | 1222 | 25.34 | 4577.34 | 4423.5 | 153.84 |  |  |  | I switch off The AJB-117 of The Inv-3 From - 10-37 to 16-00 For stabilize it`s High Voltage Problem during The Period. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 2013-08-30 | 854 | 881 | 486 | 865 | 16.39 | 3102.39 | 2986 | 116.39 |  |  |  | Inv-3 Shut Downed From - 12-05 to 15-35 For Checked The Cooling Fan problem & Also it`s AJB-112 Switch Off From - 11-34 to 15-35. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 2013-08-31 | 944 | 803 | 984 | 965 | 15.43 | 3711.43 | 3576.75 | 134.68 | 3643 | 4.896 | 72.52 | Inv-2 has Went to Sleep mode From -13-58 to 13-59 Due to Colling fan Problem Then I switch off It`s AJB-112 From - 13-58 to 14-12. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | 2013-09-01 | 1113 | 1154 | 1147 | 1133 | 5.33 | 4552.33 | 4398.75 | 153.58 | 4699 | 5.883 | 77.8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 2013-09-02 | 866 | 893 | 905 | 871 | 12.88 | 3547.88 | 3431.25 | 116.63 | 3576 | 4.438 | 78.53 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 2013-09-03 | 1079 | 1114 | 1119 | 1107 | 16.03 | 4435.03 | 4284 | 151.03 | 4479 | 5.643 | 77.36 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 2013-09-04 | 1023 | 1062 | 1063 | 1036 | 24.45 | 4208.45 | 4038.75 | 169.7 | 3064 |  |  | Grid Failure From - 12-15 to 12-20 with High Voltages Than D.O.Fuse of `B` Phase also Blown off , Plant Started From 12-28. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 2013-09-05 | 1001 | 1029 | 1024 | 1027 | 20.88 | 4101.88 | 3930.75 | 171.13 | 4240 | 4240 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 2013-09-06 | 1018 | 1046 | 1051 | 1047 | 18.86 | 4180.86 | 4015.5 | 165.36 | 4229 | 5.529 | 74.54 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 2013-09-07 | 1057 | 1091 | 1091 | 1108 | 14.69 | 4361.69 | 4227.75 | 133.94 | 4370 | 5.813 | 73.27 | Grid Failure From - 07-38 to 07-45. & Plnt Break Downed From 11-42 to 12-00. Because of Blown off The D.O.Fuse of 'Y' Phase | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 2013-09-08 | 1198 | 1250 | 1250 | 1238 | 15.8 | 4951.8 | 4765.5 | 186.3 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2013-09-09 | 1329 | 836 | 1345 | 1375 | 14.12 | 4899.12 | 4749.75 | 149.37 | 4942 | 6.983 | 68.97 | Inv-2 Shut Downed From - 18-22 to 19-00 For Checked The Cooling Fan problem & Grid Failure From - 18-22 to 18-29. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 2013-09-10 | 1323 | 1380 | 1385 | 1387 | 33.02 | 5508.02 | 5305.5 | 202.52 | 5550 | 6.968 | 77.63 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 2013-09-11 | 1317 | 1362 | 1374 | 1383 | 41.69 | 5477.69 | 5271 | 206.69 | 5510 | 6.918 | 77.62 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | 2013-09-12 | 1024 | 1074 | 1074 | 1075 | 20.85 | 4267.85 | 4128.75 | 139.1 | 4316 | 5.213 | 80.6 | Internet Failure From -12:45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
263 | 2013-09-13 | 1113 | 1165 | 1170 | 1174 | 17.3 | 4639.3 | 4483.5 | 155.8 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 2013-09-14 | 1063 | 1114 | 1114 | 1117 | 16.03 | 4424.03 | 4278.75 | 145.28 |  |  |  | Plant Break Downed From 09-48 to 09-58 Because of Blown of The D.O.Fuse of `Y` Phase,,,,Grid Failure From - 15-35 to 15-42,,,Internet Failure From - 15-30 to 00-00 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
265 | 2013-09-15 | 1232 | 1289 | 1300 | 1286 | 11.48 | 5118.48 | 4929.75 | 188.73 |  |  |  | Internet Failure From - 00-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
266 | 2013-09-16 | 1227 | 1272 | 1289 | 1273 | 17.64 | 5078.64 | 4876.5 | 202.14 |  |  |  | Internet Failure From - 00-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
267 | 2013-09-17 | 1284 | 1306 | 1340 | 1335 | 9.88 | 5274.88 | 5097.75 | 177.13 |  |  |  | Internet Failure From - 00-00 to 18-30. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
268 | 2013-09-18 | 1277 | 1345 | 1351 | 1334 | 10.79 | 5317.79 | 5113.5 | 204.29 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 2013-09-19 | 1306 | 1396 | 1380 | 1374 | 20.16 | 5476.16 | 5241.75 | 234.41 | 5516 | 6.963 | 77.21 | Internet Failure From - 17-30 to 18-15. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
270 | 2013-09-20 | 1334 | 1425 | 1391 | 1347 | 24.29 | 5521.29 | 5324.25 | 197.04 | 5560 | 7.054 | 76.82 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 2013-09-21 | 1018 | 1069 | 1045 | 1042 | 7.35 | 4181.35 | 4021.5 | 159.85 | 4204 | 5.331 | 76.86 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 2013-09-22 | 639 | 672 | 673 | 676 | 5.15 | 2665.15 | 2589.75 | 75.4 | 2735 |  |  | Internet Failure From - 13-00 to 16-30. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
273 | 2013-09-23 | 379 | 396 | 401 | 386 | 6.11 | 1568.11 | 1501.5 | 66.61 | 1633 | 1.864 | 85.38 | All Inverters Went to Sleep Mode Early From - 15-45. Because of Heavy Cloud and Rain. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 2013-09-24 | 469 | 498 | 504 | 494 | 4.3 | 1969.3 | 1885.5 | 83.8 | 2024 | 2.316 | 85.17 | Grid Failure From - 12-43 to 12-51,,,Internet Failure From - 11-45 to 14-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
275 | 2013-09-25 | 203 | 220 | 220 | 209 | 2.72 | 854.72 | 818.25 | 36.47 | 915 | 1.105 | 80.7 | Grid Failure From - 07-50 to 10-51, | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 2013-09-26 | 323 | 339 | 351 | 326 | 7.5 | 1346.5 | 1287 | 59.5 | 1401 | 1.74 | 78.47 | Grid Failure From - 11-55 to 12-00 & 12-31 to 12-36. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2013-09-27 | 751 | 780 | 780 | 782 | 16.16 | 3109.16 | 2976 | 133.16 |  |  |  | Internet Failure From - 13-00 to 00-00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
278 | 2013-09-28 | 470 | 498 | 503 | 491 | 8.51 | 1970.51 | 1906.5 | 64.01 |  |  |  | Internet Failure From - 00-00 to 00-00. Grid Failure From - 11-48 to 11-53 Because of Shorte The Jumper of `Y`Phase oF The Grid. Then our D.O.Fuse of `Y`Phase Also Blown off and Plant started From 12-02. And 2nd Time Grid Failure From - 12-36 to 13-45 For Replaced The Jumper. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
279 | 2013-09-29 | 887 | 927 | 927 | 938 | 5.47 | 3684.47 | 3585 | 99.47 |  |  |  | Internet Failure From - 00-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
280 | 2013-09-30 | 950 | 995 | 995 | 981 | 21.88 | 3942.88 | 3831 | 111.88 |  |  |  | Internet Failure From - 00-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
282 | 2013-10-01 | 792 | 826 | 831 | 816 | 16.99 | 3281.99 | 3182.25 | 99.74 |  |  |  | Internet Failure From - 00-00 to 19-45. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
283 | 2013-10-02 | 1068 | 1119 | 1120 | 1116 | 11.96 | 4434.96 | 4300.5 | 134.46 | 4487 | 5.722 | 76.42 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 2013-10-03 | 1176 | 1215 | 1215 | 1259 | 27.84 | 4892.84 | 4714 | 178.84 | 4944 | 6.324 | 76.19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2013-10-04 | 1125 | 1171 | 1182 | 1174 | 14.95 | 4666.95 | 4490.25 | 176.7 | 4707 | 6.358 | 72.15 | Plant Break Downed From - 10-27 to 10-47 Because of Blown off The D.O.Fuse of `Y` Phase | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2013-10-05 | 797 | 836 | 831 | 829 | 14.83 | 3307.83 | 3185.25 | 122.58 | 3336 | 4.411 | 73.71 | Because of Rain and Cyclone Grid Failure From - 16-00 to 18-00 due to Single Pasing Problem in Distribution Line. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2013-10-06 | 656 | 690 | 695 | 659 | 5.7 | 2705.7 | 2625.75 | 79.95 | 2730 | 3.377 | 78.79 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2013-10-07 | 978 | 1023 | 1023 | 1012 | 18.35 | 4054.35 | 3924.75 | 129.6 | 4101 | 5.239 | 76.29 | Grid Failure From - 09-20 to 09-48. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 2013-10-08 | 360 | 289 | 283 | 257 | 4.79 | 1193.79 | 1030.5 | 163.29 | 1200 |  |  | Because of Cloud and Rain Every Inverters Intermittent Went to Sleep mode Durin The Period of 11-00 to 14-45. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 2013-10-09 | 494 | 622 | 622 | 586 | 11.14 | 2335.14 | 2355 | -19.86 | 2498 | 2.985 | 81.59 | Grid Failure From -13-03 to 13-08. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2013-10-10 | 1096 | 1147 | 1153 | 1104 | 17.16 | 4517.16 | 4388.25 | 128.91 | 4579 | 5.885 | 75.83 | Grid Failure From - 15-14 to 15-19. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 2013-10-11 | 1091 | 1148 | 1142 | 1146 | 6.71 | 4533.71 | 4395.75 | 137.96 | 4584 | 5.843 | 76.46 | Grid Failure From - 14-00 to 14-38. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 2013-10-12 | 1199 | 1255 | 1250 | 1252 | 10.93 | 4966.93 | 4791.5 | 175.43 | 5015 | 6.258 | 78.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 2013-10-13 | 1063 | 1119 | 1113 | 1081 | 0.13 | 4376.13 | 4254 | 122.13 | 4447 | 5.297 | 81.82 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 2013-10-14 | 1193 | 1250 | 1244 | 1237 | 13.46 | 4937.46 | 4758 | 179.46 | 4986 | 6.297 | 77.17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2013-10-15 | 1176 | 1238 | 1227 | 1225 | 22.77 | 4888.77 | 4710 | 178.77 | 4932 |  |  | Internet Intermittent Failure From - 10-30 to 15-00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
297 | 2013-10-16 | 1226 | 1266 | 1266 | 1282 | 23.24 | 5063.24 | 4906.5 | 156.74 | 5122 | 6.546 | 76.26 | Grid Failure From - 07-54 to 07-59. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2013-10-17 | 1261 | 1323 | 1306 | 1316 | 13.93 | 5219.93 | 5085 | 134.93 | 5268 | 6.746 | 76.11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2013-10-18 | 927 | 972 | 961 | 952 | 15.03 | 3827.03 | 3692.25 | 134.78 | 3877 | 5.016 | 75.33 | Grid Failure From - 11-35 to 13-10 & 16-02 to 16-26. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 2013-10-19 | 1182 | 1244 | 1227 | 1253 | 25.93 | 4931.93 | 4754.25 | 177.68 | 4961 | 6.269 | 77.13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2013-10-20 | 1227 | 1312 | 1289 | 1321 | 13.24 | 5162.24 | 4969.5 | 192.74 | 5196 | 6.683 | 75.77 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2013-10-21 | 1238 | 1300 | 1289 | 1334 | 30.95 | 5191.95 | 5010 | 181.95 | 5231 | 6.707 | 76.01 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2013-10-22 | 1210 | 1272 | 1261 | 1273 | 22.13 | 5038.13 | 4871.25 | 166.88 | 5071 | 6.708 | 73.68 | Grid Failure From - 09-26 to 09-29 & 13-38 to 13-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2013-10-23 | 1238 | 1289 | 1323 | 1306 | 22.96 | 5178.96 | 5001.75 | 177.21 | 5222 | 5.976 |  | Internet Failure From 15-15 to 18-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
305 | 2013-10-24 | 1159 | 1238 | 1260 | 1208 | 35.01 | 4900.01 | 4731.75 | 168.26 | 4935 | 6.186 | 77.75 | Grid Failure From - 08-57 to 09-00 , 10-02 to 10-05 & 10-37 to 10-40. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2013-10-25 | 1147 | 1255 | 1238 | 1217 | 28.55 | 4885.55 | 4706.25 | 179.3 | 4913 | 6.188 | 77.38 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2013-10-26 | 1188 | 1283 | 1255 | 1309 | 23.31 | 5058.31 | 4832 | 226.31 | 5040 | 6.245 | 78.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2013-10-27 | 1181 | 1255 | 1221 | 1187 | 17.69 | 4861.69 | 4695 | 166.69 | 4909 | 6.026 | 79.39 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2013-10-28 | 1131 | 1193 | 1165 | 1119 | 32.81 | 4640.81 | 4473 | 167.81 | 4676 | 5.802 | 78.55 | Grid Supply Failure From - 15-35 to 15-39 , 15-48 to 15-51 & 16-10 to 16-14. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2013-10-29 | 1147 | 1193 | 1165 | 1129 | 24.8 | 4658.8 | 4496.25 | 162.55 | 4700 | 5.764 | 79.47 | Grid Supply Failure From - 14-46 to 14-51. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2013-10-30 | 1154 | 1193 | 1164 | 1156 | 26.02 | 4693.02 | 4545.75 | 147.27 | 4727 | 5.389 | 85.49 | Internet Failure From 04-15 to 10-45. Grid Supply Failure From - 10-24 to 10-29. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
312 | 2013-10-31 | 1176 | 1221 | 1159 | 1195 | 20.91 | 4771.91 | 4609.5 | 162.41 |  |  |  | Internet Failure From - 00-00 to 00-00 For Changed IP Address From PDPU. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
314 | 2013-11-01 | 1175 | 1227 | 1165 | 1224 | 12.97 | 4803.97 | 4647 | 156.97 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2013-11-02 | 1143 | 1204 | 1148 | 1214 | 7.45 | 4716.45 | 4565.25 | 151.2 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2013-11-03 | 1147 | 1199 | 1153 | 1199 | 4.56 | 4702.56 | 4566 | 136.56 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2013-11-04 | 1097 | 1136 | 1097 | 1128 | 9.01 | 4467.01 | 4325.25 | 141.76 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2013-11-05 | 1125 | 1159 | 1113 | 1157 | 21.1 | 4575.1 | 4422.75 | 152.35 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 2013-11-06 | 967 | 995 | 961 | 987 | 32.14 | 3942.14 | 3824.25 | 117.89 |  |  |  | Grid Failure From - 08-04 to 08-07 & 12-32 to 12-35. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2013-11-07 | 966 | 1001 | 978 | 994 | 22.65 | 3961.65 | 3834.75 | 126.9 |  |  |  | Grid Failure From - 08-35 to 08-43 & 15-56 to 16-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2013-11-08 | 1029 | 1051 | 1080 | 1058 | 13.7 | 4231.7 | 4089.75 | 141.95 |  |  |  | Grid Failure From - 09-40 to 09-43. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2013-11-09 | 990 | 1035 | 1057 | 1011 | 25.88 | 4118.88 | 3986.25 | 132.63 |  |  |  | Inv-4 Shut Down From 17-15 to 17-24 For Rectified The Oil Leakage Problem of Aux.X`mer-4 (Sr.no-C1169). | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2013-11-10 | 1068 | 1125 | 1148 | 1084 | 16.9 | 4441.9 | 4298.25 | 143.65 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2013-11-11 | 1086 | 1164 | 1170 | 1110 | 28.54 | 4558.54 | 4410 | 148.54 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2013-11-12 | 1068 | 1171 | 1148 | 1084 | 21.48 | 4492.48 | 4349.25 | 143.23 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2013-11-13 | 1029 | 1096 | 1074 | 1010 | 22.34 | 4231.34 | 4095.75 | 135.59 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2013-11-14 | 1001 | 1046 | 1023 | 950 | 22.01 | 4042.01 | 3919.5 | 122.51 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2013-11-15 | 1063 | 1108 | 1086 | 1007 | 24.26 | 4288.26 | 4155 | 133.26 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2013-11-16 | 1209 | 1261 | 1227 | 1165 | 24.75 | 4886.75 | 4726.5 | 160.25 |  |  |  | Grid Failure From - 07-05 to 07-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2013-11-17 | 1148 | 1193 | 1164 | 1091 | 18.92 | 4614.92 | 4470.75 | 144.17 |  |  |  | Inv-4 Late Started From - 07-30 Because of Fault of Emergency Stop | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2013-11-18 | 1119 | 1170 | 1125 | 1074 | 22.71 | 4510.71 | 4368 | 142.71 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2013-11-19 | 1176 | 1227 | 1176 | 1155 | 24.08 | 4758.08 | 4612.5 | 145.58 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2013-11-20 | 1159 | 1182 | 1182 | 1179 | 28.09 | 4730.09 | 4572 | 158.09 |  |  |  | Grid Supply Failure From - 15-24 to 15-31. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2013-11-21 | 1176 | 1232 | 1210 | 1223 | 19.11 | 4860.11 | 4713.75 | 146.36 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2013-11-22 | 1170 | 1221 | 1226 | 1197 | 23.67 | 4837.67 | 4686 | 151.67 | 4877 | 6.156 | 77.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2013-11-23 | 1125 | 1159 | 1216 | 1160 | 29.06 | 4689.06 | 4533.75 | 155.31 | 4722 | 6.018 | 76.47 | Grid Supply Failure From - 16-00 to 16-05. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2013-11-24 | 1086 | 1131 | 1176 | 1110 | 19.87 | 4522.87 | 4371.75 | 151.12 | 4570 | 5.778 | 77.08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2013-11-25 | 1000 | 1051 | 1079 | 1026 | 26.4 | 4182.4 | 4059.75 | 122.65 | 4233 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2013-11-26 | 1063 | 1148 | 1142 | 1099 | 25.13 | 4477.13 | 4332.75 | 144.38 | 4516 | 5.674 | 77.57 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2013-11-27 | 978 | 1085 | 1058 | 1022 | 26.71 | 4169.71 | 4029 | 140.71 | 4209 | 5.193 | 78.99 | Grid Supply Failure From - 17-23 to 17-29. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2013-11-28 | 1108 | 1205 | 1159 | 1128 | 27 | 4627 | 4487.25 | 139.75 | 4670 | 5.811 | 78.32 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2013-11-29 | 1086 | 1119 | 1113 | 1046 | 33.03 | 4397.03 | 4260 | 137.03 | 4435 | 5.741 | 75.29 | Grid Supply Failure From - 11-28 to 11-36. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2013-11-30 | 1114 | 1159 | 1125 | 1054 | 30.56 | 4482.56 | 4336.5 | 146.06 | 4514 | 5.826 | 75.51 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 2013-12-01 | 1040 | 1085 | 1052 | 1008 | 22.52 | 4207.52 | 4083.75 | 123.77 | 4255 | 5.61 | 73.92 | Grid Supply Failure From - 16-20 to 16-57. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2013-12-02 | 1097 | 1080 | 1085 | 1089 | 32.49 | 4383.49 | 4252.5 | 130.99 | 4424 | 5.812 | 74.18 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 2013-12-03 | 1170 | 1216 | 1182 | 1189 | 27.95 | 4784.95 | 4627.5 | 157.45 |  |  |  | Grid Supply Failure From -10-47 to 10-50. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2013-12-04 | 1085 | 1136 | 1092 | 1113 | 20.35 | 4446.35 | 4320 | 126.35 | 4496 | 5.792 | 75.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2013-12-05 | 1069 | 1108 | 1079 | 1103 | 28.24 | 4387.24 | 4248 | 139.24 | 4422 | 5.678 | 75.9 | Grid Supply Failure From - 09-14 to 09-18. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 2013-12-06 | 1125 | 1170 | 1170 | 1179 | 32.62 | 4676.62 | 4518 | 158.62 | 4709 | 6.059 | 75.74 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2013-12-07 | 1130 | 1176 | 1204 | 1178 | 30.24 | 4718.24 | 4563.75 | 154.49 | 4757 | 6.119 | 75.77 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2013-12-08 | 1097 | 1142 | 1182 | 1132 | 21.75 | 4574.75 | 4431.75 | 143 | 4618 | 5.982 | 75.24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2013-12-09 | 1097 | 1125 | 1182 | 1134 | 27.72 | 4565.72 | 4395 | 170.72 | 4578 | 6.009 | 74.25 | Inv-3 Shut down From - 16-31 to 18-00 For Replaced The Control card of The Cooling Fan. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2013-12-10 | 1091 | 905 | 870 | 1128 | 36.24 | 4030.24 | 3895.5 | 134.74 | 4094 | 6.043 | 66.03 | Grid Failure From - 11-20 to 11-28 , Inv-3 Shut down From - 09-40 to 11-17 & 16-00 to 17-26 and Inv-2 Shut down From - 11-18 to 12-25 & 16-00 to 17-26 For Replaced The Control card of The Cooling Fan. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2013-12-11 | 1074 | 1170 | 1142 | 1100 | 31.14 | 4517.14 | 4375.5 | 141.64 | 4549 | 5.867 | 75.57 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2013-12-12 | 1080 | 1148 | 1120 | 1071 | 31.4 | 4450.4 | 4308 | 142.4 | 4491 | 5.717 | 76.56 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2013-12-13 | 1131 | 1187 | 1130 | 1102 | 26.81 | 4576.81 | 4438.5 | 138.31 | 4622 | 6.048 | 74.48 | Grid Failure From- 17-30 to 17-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2013-12-14 | 1159 | 1210 | 1154 | 1127 | 24.57 | 4674.57 | 4522.5 | 152.07 | 4710 | 6.241 | 73.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2013-12-15 | 1142 | 1164 | 1131 | 1102 | 18.64 | 4557.64 | 4424.25 | 133.39 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2013-12-16 | 1170 | 1216 | 1153 | 1146 | 27.06 | 4712.06 | 4570.5 | 141.56 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2013-12-17 | 1165 | 1204 | 1125 | 1157 | 20.71 | 4671.71 | 4520.25 | 151.46 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2013-12-18 | 1051 | 1080 | 1023 | 1073 | 27.03 | 4254.03 | 4137.75 | 116.28 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2013-12-19 | 1097 | 1136 | 1080 | 1128 | 22.38 | 4463.38 | 4329.75 | 133.63 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2013-12-20 | 1159 | 1199 | 1181 | 1194 | 29.67 | 4762.67 | 4608 | 154.67 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2013-12-21 | 1029 | 1063 | 1092 | 1033 | 18.36 | 4235.36 | 4105.5 | 129.86 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 2013-12-22 | 1012 | 1045 | 1085 | 1018 | 18.2 | 4178.2 | 4045.5 | 132.7 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 2013-12-23 | 1034 | 1092 | 1108 | 1053 | 26.94 | 4313.94 | 4184.25 | 129.69 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 2013-12-24 | 741 | 808 | 797 | 708 | 22.08 | 3076.08 | 2979 | 97.08 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 2013-12-25 | 836 | 916 | 876 | 811 | 19.71 | 3458.71 | 3362.25 | 96.46 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 2013-12-26 | 820 | 865 | 831 | 769 | 21.47 | 3306.47 | 3210.75 | 95.72 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 2013-12-27 | 956 | 989 | 945 | 885 | 16.58 | 3791.58 | 3666.75 | 124.83 | 3680 | 5.724 | 62.6615 | Grid Supply Failure From - 14-57 to 15-01. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 2013-12-28 | 1040 | 1075 | 1023 | 969 | 15.98 | 4122.98 | 3994.5 | 128.48 | 4010 | 5.312 | 73.5765 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 2013-12-29 | 961 | 989 | 944 | 908 | 9.85 | 3811.85 | 3700.5 | 111.35 | 3721 | 5.02 | 72.2451 | Grid Supply Failure From - 12-58 to 13-07. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 2013-12-30 | 848 | 876 | 831 | 798 | 19.14 | 3372.14 | 3274.5 | 97.64 | 3290 | 4.367 | 73.4286 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 2013-12-31 | 1091 | 1125 | 1069 | 1079 | 13.67 | 4377.67 | 4239.75 | 137.92 | 4250 | 5.64 | 73.445 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2014
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2014-01-01 | 695 | 712 | 689 | 676 | 17.62 | 2789.62 | 2712 | 77.62 | 2795 | 3.53 | 77.172 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2014-01-02 | 470 | 492 | 498 | 465 | 11.35 | 1936.35 | 1869.75 | 66.6 | 1950 | 2.393 | 79.4227 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2014-01-03 | 893 | 927 | 944 | 896 | 21.16 | 3681.16 | 3568.5 | 112.66 | 3698 | 4.707 | 76.5729 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2014-01-04 | 910 | 956 | 972 | 912 | 21.15 | 3771.15 | 3656.25 | 114.9 | 3782 | 4.681 | 78.7473 | Grid Failure From - 17-40 to 17-55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2014-01-05 | 1119 | 1198 | 1199 | 1124 | 19.55 | 4659.55 | 4518 | 141.55 | 4675 | 5.943 | 76.6705 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2014-01-06 | 1165 | 1250 | 1238 | 1164 | 25.94 | 4842.94 | 4689 | 153.94 | 4854 | 6.18 | 76.5533 | Grid Failure From - 11-31 to 11-34. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2014-01-07 | 1136 | 1260 | 1204 | 1146 | 24.09 | 4770.09 | 4625.25 | 144.84 | 4775 | 5.928 | 78.5087 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2014-01-08 | 1007 | 1080 | 1035 | 952 | 30.96 | 4104.96 | 3972 | 132.96 | 4115 | 5.171 | 77.5618 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2014-01-09 | 1046 | 1097 | 1045 | 979 | 24.62 | 4191.62 | 4064.25 | 127.37 | 4195 | 5.593 | 73.1038 | Grid Failure From - 14-21 to 14-51. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2014-01-10 | 1023 | 1046 | 1018 | 914 | 21.84 | 4022.84 | 3897.75 | 125.09 | 4028 | 5.291 | 74.2001 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2014-01-11 | 871 | 899 | 859 | 772 | 13.58 | 3414.58 | 3312.75 | 101.83 | 3421 | 4.394 | 75.8832 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2014-01-12 | 1102 | 1147 | 1097 | 1026 | 14.1 | 4386.1 | 4247.25 | 138.85 | 4390 | 5.61 | 76.2701 | Grid Failure From - 16-33 to 16-52 & 17-25 to 17-35. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2014-01-13 | 995 | 1035 | 995 | 883 | 22.08 | 3930.08 | 3806.25 | 123.83 | 3935 | 5.09 | 75.3494 | Inv-4 Shut-down From 15-45 to 17-29. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2014-01-14 | 1006 | 1046 | 1006 | 969 | 0.94 | 4027.94 | 3901.5 | 126.44 | 4032 | 5.208 | 75.4575 | Grid Supply Failure From - 17-53 to 17-58. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2014-01-15 | 1131 | 1198 | 1148 | 1108 | 3.14 | 4588.14 | 4446 | 142.14 | 4592 | 5.953 | 75.1828 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2014-01-16 | 1136 | 1188 | 1137 | 1123 | 6.43 | 4590.43 | 4447.5 | 142.93 | 4594 | 5.872 | 76.2531 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2014-01-17 | 933 | 966 | 955 | 911 | 16.97 | 3781.97 | 3603 | 178.97 | 3785 | 4.814 | 76.6324 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2014-01-18 | 1210 | 1261 | 1283 | 1213 | 30.84 | 4997.84 | 4776 | 221.84 | 5002 | 6.303 | 77.348 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2014-01-19 | 1187 | 1238 | 1267 | 1177 | 71.38 | 4940.38 | 4725 | 215.38 | 4943 | 6.053 | 79.5926 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2014-01-20 | 961 | 1018 | 1029 | 943 | 50.91 | 4001.91 | 3813.75 | 188.16 | 4005 | 5.043 | 77.4045 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2014-01-21 | 611 | 638 | 633 | 591 | 26.06 | 2499.06 | 2350.5 | 148.56 |  |  |  | Grid Failure From - 09-53 to 10-59. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2014-01-22 | 876 | 928 | 916 | 864 | 42.11 | 3626.11 | 3447.75 | 178.36 |  |  |  | Internet Failure From - 05-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
22 | 2014-01-23 | 1114 | 1170 | 1158 | 1113 | 60.83 | 4615.83 | 4407 | 208.83 |  |  |  | Internet Started From-13-00 but 8 Pot Switch Failure Then My CPU is not connected With Net only Seeds Gate Way is Connected now. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
23 | 2014-01-24 | 1074 | 1131 | 1109 | 1092 | 54.24 | 4460.24 | 4274.25 | 185.99 |  |  |  | Grid Failure From- 08-00 to 08-05 , 08-25 to 08-30 & 10-04 to 10-35 , All Inverters Started From 09-07 Because It`s Aux.MCB Tripped With Grid Failure at 08-00 Then I Manually Reset it And Stared The Plant. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2014-01-25 | 1153 | 1209 | 1192 | 1149 | 63 | 4766 | 4569.75 | 196.25 | 4770 | 6.029 | 77.1127 | Grid Failure From - 12-35 to 12-43. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2014-01-26 | 1001 | 1063 | 1041 | 995 | 52.68 | 4152.68 | 3966 | 186.68 | 4156 | 5.134 | 78.8991 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2014-01-27 | 1187 | 1250 | 1232 | 1106 | 69.64 | 4844.64 | 4631.25 | 213.39 | 4850 | 6.112 | 77.3412 | Inv-4 Shut Down From 16-10 to 19-10 by M/s.Schneider for Rectify The Comm.Error Problem. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2014-01-28 | 1170 | 1232 | 1216 | 1186 | 73.8 | 4877.8 | 4671.75 | 206.05 | 4881 | 6.286 | 75.681 | Grid Failure From - 13-32 to 13-39 & 15-56 to 16-32. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2014-01-29 | 1222 | 1289 | 1266 | 1229 | 73.88 | 5079.88 | 4869 | 210.88 | 5083 | 6.555 | 75.5788 | Grid Failure From - 15-29 to 15-34. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2014-01-30 | 1255 | 1323 | 1306 | 1306 | 77.82 | 5267.82 | 5022 | 245.82 | 5271 | 6.657 | 77.1733 | Grid failure From - 14-01 to 14-04. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2014-01-31 | 1260 | 1329 | 1317 | 1292 | 82.08 | 5280.08 | 5066.25 | 213.83 | 5284 | 6.585 | 78.2095 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2014-02-01 | 1210 | 1277 | 1295 | 1230 | 76.54 | 5088.54 | 4871.25 | 217.29 | 5092 | 6.324 | 78.4782 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2014-02-02 | 939 | 995 | 1000 | 932 | 49.56 | 3915.56 | 3743.25 | 172.31 | 3919 | 4.814 | 79.3454 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2014-02-03 | 1028 | 1091 | 1103 | 1019 | 60.27 | 4301.27 | 4124.25 | 177.02 | 4305 | 5.543 | 75.6974 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2014-02-04 | 1160 | 1255 | 1232 | 1170 | 71.66 | 4888.66 | 4685.25 | 203.41 | 4892 | 6.157 | 77.4408 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2014-02-05 | 1170 | 1272 | 1227 | 1189 | 71.22 | 4929.22 | 4723.5 | 205.72 | 4933 | 6.168 | 77.9506 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2014-02-06 | 1204 | 1272 | 1221 | 1173 | 72.18 | 4942.18 | 4737 | 205.18 | 4948 | 6.242 | 77.2607 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2014-02-07 | 1249 | 1295 | 1261 | 1236 | 74.55 | 5115.55 | 4908.75 | 206.8 | 5119 | 6.32 | 78.9443 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2014-02-08 | 1363 | 1385 | 1368 | 1357 | 86.28 | 5559.28 | 5331 | 228.28 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2014-02-09 | 1374 | 1436 | 1379 | 1355 | 86.74 | 5630.74 | 5389.5 | 241.24 | 5635 | 6.878 | 79.8517 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2014-02-10 | 1243 | 1306 | 1255 | 1250 | 79.06 | 5133.06 | 4926 | 207.06 | 5137 | 6.469 | 77.3972 | Grid Failure From - 13-17 to 13-31. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2014-02-11 | 1267 | 1323 | 1273 | 1276 | 79.26 | 5218.26 | 5014.5 | 203.76 |  |  |  | Grid Failure From - 11-40 to 11-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2014-02-12 | 1023 | 1068 | 1051 | 1033 | 63.17 | 4238.17 | 4055.25 | 182.92 | 4244 | 5.213 | 79.3488 | Grid Failure From - 12-28 to 13-58. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2014-02-13 | 1249 | 1306 | 1323 | 1267 | 73.71 | 5218.71 | 5001.75 | 216.96 | 5225 | 6.305 | 80.7707 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2014-02-14 | 1063 | 1131 | 1136 | 1065 | 55.97 | 4450.97 | 4265.25 | 185.72 | 4455 | 4.966 | 87.4367 | Inv-5.1 Shut down from-11-10 to 12-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2014-02-15 | 854 | 933 | 913 | 839 | 40.75 | 3579.75 | 3417 | 162.75 | 3583 | 4.329 | 80.67 | Because of Cloud Inv-4 went to Sleep mode From - 9-58 to 9-59 , 10-31 to 10-32 & 13-29 to 13-30. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2014-02-16 | 1170 | 1294 | 1253 | 1166 | 67.16 | 4950.16 | 4757.25 | 192.91 | 4955 | 6.083 | 79.3923 | Grid Failure From - 10-54 to 10-59. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2014-02-17 | 1312 | 1420 | 1368 | 1304 | 79.14 | 5483.14 | 5127 | 356.14 | 5488 | 6.572 | 81.3897 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2014-02-18 | 1413 | 1475 | 1419 | 1304 | 87.52 | 5698.52 | 5472.75 | 225.77 | 5705 | 7.067 | 78.6816 | Inv-4 Shut-down From 16-15 to 17-20 by M/s.Schneider. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2014-02-19 | 1283 | 1323 | 1277 | 1237 | 78.78 | 5198.78 | 5004 | 194.78 | 5204 | 6.572 | 77.1778 | Plnt Shut-down From - 17-33 to 17-35 & 17-40 to 18-00 By M/s.Suk-kam UPS. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2014-02-20 | 1114 | 1159 | 1120 | 1091 | 61.67 | 4545.67 | 4367.25 | 178.42 | 4549 | 5.723 | 77.472 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2014-02-21 | 701 | 723 | 695 | 695 | 26.93 | 2840.93 | 2704.5 | 136.43 | 2844 | 3.395 | 81.6474 | Fully Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
53 | 2014-02-22 | 1255 | 1301 | 1249 | 1275 | 74.35 | 5154.35 | 4947.75 | 206.6 | 5161 | 6.458 | 77.8912 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2014-02-23 | 1244 | 1300 | 1255 | 1258 | 72.81 | 5129.81 | 4929.75 | 200.06 | 5134 | 6.283 | 79.6419 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2014-02-24 | 984 | 1029 | 1012 | 986 | 48.45 | 4059.45 | 3883.5 | 175.95 | 4064 | 4.807 | 82.4009 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2014-02-25 | 1029 | 1091 | 1114 | 1059 | 56.26 | 4349.26 | 4174.5 | 174.76 | 4355 | 5.576 | 76.1234 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2014-02-26 | 780 | 837 | 860 | 795 | 39.25 | 3311.25 | 3180 | 131.25 | 3316 | 4.441 | 72.7757 | Grid Failure From - 11-18 to 11-30 & 16-19 to 16-26. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2014-02-27 | 1006 | 1108 | 1108 | 986 | 57.14 | 4265.14 | 4067.25 | 197.89 | 4270 | 5.26 | 79.1215 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2014-02-28 | 1227 | 1374 | 1345 | 1262 | 73.9 | 5281.9 | 5065.5 | 216.4 | 5285 | 6.375 | 80.8011 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 2014-03-01 | 1396 | 1385 | 1470 | 1388 | 85.81 | 5724.81 | 5492.25 | 232.56 | 5496 | 6.968 | 76.8761 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2014-03-02 | 1374 | 1470 | 1419 | 1345 | 81.8 | 5689.8 | 5452.5 | 237.3 | 5693 | 6.779 | 81.8518 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2014-03-03 | 1261 | 1323 | 1272 | 1197 | 70.96 | 5123.96 | 4912.5 | 211.46 | 5128 | 6.364 | 78.5363 | Grid Failure From - 16-27 to 16-32. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2014-03-04 | 1356 | 1413 | 1368 | 1325 | 82.82 | 5544.82 | 5319 | 225.82 | 5549 | 6.94 | 77.9306 | Grid Failure From - 15-37 to 15-41. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2014-03-05 | 1233 | 1277 | 1238 | 1254 | 73.58 | 5075.58 | 4863.75 | 211.83 | 5080 | 6.412 | 77.2188 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2014-03-06 | 1266 | 1318 | 1272 | 1303 | 76.93 | 5235.93 | 5023.5 | 212.43 | 5240 | 6.523 | 78.2955 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2014-03-07 | 1318 | 1368 | 1340 | 1381 | 80.87 | 5487.87 | 5264.25 | 223.62 | 5492 | 6.749 | 79.3129 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2014-03-08 | 1288 | 1345 | 1346 | 1384 | 81.47 | 5444.47 | 5216.25 | 228.22 | 5450 | 6.825 | 77.8299 | Grid Failure From - 08-30 to 08-35 , Inv- 1 , 2 , 3 Restarted From - 08-58. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2014-03-09 | 1210 | 1272 | 1283 | 1261 | 71.48 | 5097.48 | 4924.5 | 172.98 | 5101 | 6.568 | 75.6963 | Grid Failure From - 02-02 to 02-15 ( But VCB Tripped Then Plant Started From -08-20) Also Grid Failure From - 11-22 to 11-27. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2014-03-10 | 1131 | 1188 | 1198 | 1155 | 65.37 | 4737.37 | 4536.75 | 200.62 | 4742 | 6.023 | 76.7364 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2014-03-11 | 1165 | 1255 | 1233 | 1189 | 68.87 | 4910.87 | 4713.75 | 197.12 | 4916 | 6.28 | 76.2965 | Grid Failure From - 12-01 to 12-10. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2014-03-12 | 927 | 1006 | 967 | 932 | 50.73 | 3882.73 | 3724.5 | 158.23 | 3885 | 4.764 | 79.4826 | Grid Failure From - 12-07 to 13-36. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2014-03-13 | 1345 | 1430 | 1373 | 1355 | 78.49 | 5581.49 | 5361.75 | 219.74 | 5586 | 6.831 | 79.702 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2014-03-14 | 1340 | 1391 | 1329 | 1321 | 82.56 | 5463.56 | 5248.5 | 215.06 | 5467 | 6.821 | 78.1185 | Grid Failure From - 12-35 to 12-39. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2014-03-15 | 1329 | 1385 | 1329 | 1358 | 84.12 | 5485.12 | 5259.75 | 225.37 | 5489 | 6.938 | 77.1102 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2014-03-16 | 1238 | 1283 | 1232 | 1250 | 79.05 | 5082.05 | 4883.25 | 198.8 | 5088 | 6.463 | 76.7301 | Grid Failure From - 10-34 to 10-39. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2014-03-17 | 1385 | 1448 | 1391 | 1483 | 89.76 | 5796.76 | 5568 | 228.76 | 5803 | 7.083 | 79.8524 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2014-03-18 | 1453 | 1509 | 1498 | 1529 | 94.13 | 6083.13 | 5844 | 239.13 | 5089 | 7.435 | 66.712 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2014-03-19 | 1385 | 1447 | 1470 | 1458 | 88.85 | 5848.85 | 5626.5 | 222.35 | 5854 | 7.242 | 78.7856 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2014-03-20 | 1357 | 1431 | 1458 | 1412 | 88.69 | 5746.69 | 5513.25 | 233.44 | 5752 | 7.132 | 78.6068 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2014-03-21 | 1436 | 1549 | 1544 | 1524 | 94.74 | 6147.74 | 5902.5 | 245.24 | 6153 | 7.325 | 81.8713 | Grid Failure From - 16-53 to 16-57. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2014-03-22 | 1328 | 1447 | 1407 | 1399 | 82.69 | 5663.69 | 5442.75 | 220.94 | 5667 | 6.834 | 80.8222 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2014-03-23 | 1284 | 1368 | 1335 | 1321 | 76.54 | 5384.54 | 5175.75 | 208.79 | 5390 | 6.528 | 80.4751 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2014-03-24 | 1385 | 1459 | 1419 | 1411 | 84.66 | 5758.66 | 5532.75 | 225.91 | 5540 | 7.013 | 76.9943 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2014-03-25 | 1368 | 1407 | 1390 | 1400 | 86.07 | 5651.07 | 5434.5 | 216.57 | 5659 | 7.073 | 77.981 | Grid Failure From - 17-55 to 18-02. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2014-03-26 | 1317 | 1386 | 1340 | 1385 | 81.65 | 5509.65 | 5301.75 | 207.9 | 5515 | 6.912 | 77.7668 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2014-03-27 | 1170 | 1215 | 1182 | 1226 | 68.28 | 4861.28 | 4672.5 | 188.78 | 4869 | 6.067 | 78.2201 | Grid Failure From - 07-40 to 07-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2014-03-28 | 1306 | 1368 | 1357 | 1390 | 83.33 | 5504.33 | 5289 | 215.33 | 5512 | 6.872 | 78.1769 | Grid Failure From - 10-51 to 10-53. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2014-03-29 | 1351 | 1413 | 1430 | 1441 | 85.31 | 5720.31 | 5501.25 | 219.06 | 5726 | 6.981 | 79.9441 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2014-03-30 | 1295 | 1363 | 1391 | 1390 | 77.87 | 5516.87 | 5299.5 | 217.37 | 5521 | 6.706 | 80.2429 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2014-03-31 | 1317 | 1396 | 1424 | 1421 | 82.88 | 5640.88 | 5424.75 | 216.13 | 5647 | 6.905 | 79.7089 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2014-04-01 | 1368 | 1504 | 1482 | 1470 | 88.45 | 5912.45 | 5678.25 | 234.2 | 5918 | 7.159 | 80.5703 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2014-04-02 | 1351 | 1464 | 1424 | 1408 | 83.46 | 5730.46 | 5504.2 | 226.26 | 5736 | 6.941 | 80.5452 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2014-04-03 | 1227 | 1284 | 1255 | 1236 | 65.42 | 5067.42 | 4893 | 174.42 | 5072 | 7.097 | 69.6558 | I observed Switch off The Main ACB at Morning 09-00 , Then I Started The Plant From - 09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2014-04-04 | 1346 | 1407 | 1363 | 1364 | 85.56 | 5565.56 | 5349 | 216.56 | 5571 | 7.145 | 75.9947 | Replaced D.C.12Amp.Fuse Link of The String.04 --tive in AJB-105 ( Inv-4) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
97 | 2014-04-05 | 1227 | 1233 | 1243 | 1269 | 80.88 | 5052.88 | 4865.25 | 187.63 |  |  |  | Grid Failure From - 13-26 to 13-31 & 14-24 to 14-50,,,Inv-2 Shut-Down From 17-00 to 18-00 and Replaced The AFPS Card of Cooling Fan By M/s.ABB. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2014-04-06 | 1368 | 1419 | 1386 | 1358 | 88.87 | 5619.87 | 5403.75 | 216.12 | 5628 | 7.221 | 75.9643 | At.14-07 I Observed Tripped The Q11.MCB of MJB-4 ( INV-4 ) Then I Reset it and Retight it`s Termination. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2014-04-07 | 1210 | 1261 | 1232 | 1283 | 70.4 | 5056.4 | 4870.5 | 185.9 | 5060 | 6.416 | 76.8668 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2014-04-08 | 1288 | 1339 | 1306 | 1389 | 80.47 | 5402.47 | 5190.75 | 211.72 | 5409 | 6.85 | 76.9625 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2014-04-09 | 1318 | 1369 | 1362 | 1428 | 86.36 | 5563.36 | 5364 | 199.36 | 5569 | 7.083 | 76.6324 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2014-04-10 | 1187 | 1226 | 1267 | 1258 | 76.82 | 5014.82 | 4828.5 | 186.32 | 5021 | 6.41 | 76.3457 | Grid Failure From - 09-48 to 09-53 & 13-43 to 13-58. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2014-04-11 | 1300 | 1368 | 1430 | 1418 | 86.61 | 5602.61 | 5388.75 | 213.86 | 5609 | 7.029 | 77.7758 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2014-04-12 | 1261 | 1380 | 1391 | 1377 | 82.72 | 5491.72 | 5287.5 | 204.22 | 5501 | 6.786 | 79.0097 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2014-04-13 | 1221 | 1357 | 1344 | 1323 | 80.79 | 5325.79 | 5111.25 | 214.54 | 5330 | 6.621 | 78.4614 | Grid Failure From - 09-29 to 09-37. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2014-04-14 | 1221 | 1368 | 1334 | 1323 | 79.02 | 5325.02 | 5122.5 | 202.52 | 5331 | 6.592 | 78.8214 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2014-04-15 | 1199 | 1294 | 1255 | 1249 | 70.96 | 5067.96 | 4880.25 | 187.71 | 5072 | 6.323 | 78.1823 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2014-04-16 | 1283 | 1340 | 1306 | 1307 | 76.72 | 5312.72 | 5116.5 | 196.22 | 5320 | 6.649 | 77.9844 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2014-04-17 | 1249 | 1284 | 1244 | 1254 | 77.23 | 5108.23 | 4915.5 | 192.73 | 5115 | 6.435 | 77.4729 | Grid Failure From - 16-08 to 16-13. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2014-04-18 | 1284 | 1317 | 1283 | 1323 | 81.61 | 5288.61 | 5086.5 | 202.11 | 5292 | 6.596 | 78.1973 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2014-04-19 | 1232 | 1272 | 1227 | 1307 | 74.31 | 5112.31 | 4920.75 | 191.56 | 5118 | 6.4 | 77.9423 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2014-04-20 | 1137 | 1164 | 1131 | 1203 | 65.52 | 4700.52 | 4520.25 | 180.27 |  |  |  | Because Cloud Inv-4 Went to Sleep mode From - 17-25 & Inv-1,2,3 Went to Sleep mode From -17-44 and Due to Cyclone and Rain Grid Failure From 18-15 to Late Night. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2014-04-21 | 1266 | 1329 | 1328 | 1377 | 70.57 | 5370.57 | 5228.25 | 142.32 |  |  |  | Because of GRID Failure From Yesterday Evening to Late Night .VCB Also Switch off Due to Failure The Battery Back-Up, Then I started The Plant From - 08-48, Grid Failure From - 09-23 TO 09-28. Internet Failure From Yesterday 18-15 to 00-00 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0
114 | 2014-04-22 | 1295 | 1362 | 1357 | 1391 | 83.49 | 5488.49 | 5284.5 | 203.99 |  |  |  | Grid Failure From - 09-17 to 09-36 & 16-04 to 16-06. Internet Failure From 00-00 to 00-00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
115 | 2014-04-23 | 1283 | 1357 | 1351 | 1376 | 85.04 | 5452.04 | 5253.75 | 198.29 |  |  |  | Grid Failure From - 09-34 to 09-37 , 10-24 to 10-29 & 11-09 to 11-12 , Internet Failure From 00-00 to 00-00 . | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
116 | 2014-04-24 | 1334 | 1402 | 1402 | 1431 | 79.69 | 5648.69 | 5445 | 203.69 |  |  |  | Internet Failure From 00-00 to 00-00. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
117 | 2014-04-25 | 1261 | 1329 | 1323 | 1365 | 82.33 | 5360.33 | 5156.25 | 204.08 |  |  |  | Grid Failure From - 08-55 to 09-35. Internet Failure From 00-00 to 14-45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
118 | 2014-04-26 | 1243 | 1312 | 1306 | 1361 | 76.22 | 5298.22 | 5100.75 | 197.47 | 5305 | 6.726 | 76.8743 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2014-04-27 | 1018 | 1068 | 1063 | 1090 | 65.39 | 4304.39 | 4134 | 170.39 | 4310 | 5.75 | 73.057 | Grid Failure From - 8:30 to 8:35 & 10:40 to 11:55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2014-04-28 | 1233 | 1295 | 1289 | 1332 | 79.74 | 5228.74 | 5031 | 197.74 | 5235 | 6.726 | 75.8599 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2014-04-29 | 1226 | 1289 | 1283 | 1345 | 79.6 | 5222.6 | 5037.75 | 184.85 |  |  |  | Grid Failure From -17:48 to 17:50 , Rahul Mohan Shut-down The SEEDS During The Period of 13:45 to 16-15. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2014-04-30 | 1261 | 1328 | 1312 | 1382 | 83.91 | 5366.91 | 5166 | 200.91 | 5370 | 6.866 | 76.2295 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2014-05-01 | 1227 | 1295 | 1323 | 1403 | 86.34 | 5334.34 | 5126.25 | 208.09 | 5440 | 6.948 | 76.3118 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2014-05-02 | 1272 | 1328 | 1334 | 1414 | 84.38 | 5432.38 | 5232 | 200.38 | 5439 | 6.952 | 76.2539 | Grid Failure From - 17:44 to 17:49. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2014-05-03 | 1148 | 1204 | 1210 | 1269 | 65.56 | 4896.56 | 4702.5 | 194.06 | 4903 | 6.232 | 76.6809 | Grid Failure From - 16-27 to 19-29. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2014-05-04 | 1175 | 1227 | 1243 | 1317 | 69.07 | 5031.07 | 4852.5 | 178.57 | 5038 | 6.326 | 77.6214 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2014-05-05 | 1120 | 1154 | 1216 | 1238 | 67.15 | 4795.15 | 4602 | 193.15 | 4800 | 6.079 | 76.9594 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2014-05-06 | 1085 | 1147 | 1193 | 1225 | 66.05 | 4716.05 | 4542 | 174.05 | 4720 | 5.983 | 76.891 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2014-05-07 | 1205 | 1301 | 1340 | 1248 | 78.39 | 5172.39 | 5063.25 | 109.14 | 5179 | 6.43 | 78.5032 | Grid Failure From - 08:16 to 08:20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2014-05-08 | 1215 | 1334 | 1345 | 1353 | 77.77 | 5324.77 | 5136.75 | 188.02 | 5330 | 6.594 | 78.7827 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2014-05-09 | 1300 | 1390 | 1391 | 1391 | 85.97 | 5557.97 | 5348.25 | 209.72 | 5600 | 6.957 | 78.4546 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2014-05-10 | 1187 | 1205 | 1216 | 1232 | 69.93 | 4909.93 | 4721.25 | 188.68 | 4938 | 6.338 | 75.93 | Grid Failure From - 11:27 to 11:48 & 17:49 to 17:55. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2014-05-11 | 1267 | 1306 | 1294 | 1349 | 80.29 | 5296.29 | 5084.25 | 212.04 | 5316 | 6.681 | 77.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2014-05-12 | 1244 | 1322 | 1312 | 1372 | 82.38 | 5332.38 | 5129.25 | 203.13 | 5357 | 6.663 | 78.36 | Grid Failure from 16:10 to 16:14 & 18:47 to 18:51 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2014-05-13 | 1119 | 1193 | 1170 | 1244 | 68.94 | 4794.94 | 4602 | 192.94 | 4817 | 6.13 | 76.58 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2014-05-14 | 1142 | 1217 | 1215 | 1272 | 69.19 | 4915.19 | 4722.75 | 192.44 | 4940 | 6.102 | 78.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2014-05-15 | 1227 | 1288 | 1295 | 1362 | 79.36 | 5251.36 | 5050.5 | 200.86 | 5275 | 6.469 | 79.47 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2014-05-16 | 1102 | 1147 | 1159 | 1212 | 67.36 | 4687.36 | 4504.5 | 182.86 | 4715 | 5.745 | 79.99 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2014-05-17 | 1216 | 1273 | 1306 | 1347 | 77.42 | 5219.42 | 5025 | 194.42 | 5249 | 6.43 | 79.56 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2014-05-18 | 1158 | 1215 | 1244 | 1345 | 79.43 | 5041.43 | 4844.25 | 197.18 | 5066 | 6.587 | 74.96 | Grid Failure From -08:00 to 08:05 But Inverter - 1 , 2 & 3 Reset at 08:50. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2014-05-19 | 1058 | 1119 | 1125 | 1164 | 69.38 | 4535.38 | 4360.5 | 174.88 | 4569 | 5.729 | 77.73 | Grid Failure From - 09:05 to 09:10 & 12:05 to 12:18. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2014-05-20 | 1227 | 1329 | 1294 | 1343 | 59.57 | 5252.57 | 5073 | 179.57 | 5300 | 6.477 | 79.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2014-05-21 | 1288 | 1396 | 1346 | 1414 | 91.07 | 5535.07 | 5328 | 207.07 | 5561 | 6.81 | 79.58 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2014-05-22 | 1306 | 1368 | 1323 | 1396 | 90.68 | 5483.68 | 5281.5 | 202.18 | 5513 | 7.001 | 76.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2014-05-23 | 1306 | 1357 | 1311 | 1390 | 90.99 | 5454.99 | 5252.25 | 202.74 | 5476 | 6.979 | 76.47 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2014-05-24 | 1267 | 1317 | 1280 | 1354 | 87.16 | 5305.16 | 5108.25 | 196.91 | 5330 | 6.797 | 76.42 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2014-05-25 | 1176 | 1216 | 1182 | 1279 | 75.87 | 4928.87 | 4752.9 | 175.97 | 4967 | 6.391 | 75.67 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2014-05-26 | 1113 | 1153 | 1125 | 1197 | 69.83 | 4657.83 | 4482.75 | 175.08 | 4674 | 6.007 | 75.83 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2014-05-27 | 577 | 605 | 593 | 617 | 34.55 | 2426.55 | 2309.25 | 117.3 | 2458 | 3.272 | 73.21 | Grid failure from 9:14 am to 13:04 pm. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2014-05-28 | 1153 | 1216 | 1187 | 1284 | 68.6 | 4908.6 | 4735.5 | 173.1 | 4938 | 6.326 | 76.08 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2014-05-29 | 1193 | 1243 | 1221 | 1335 | 79.56 | 5071.56 | 4881 | 190.56 | 5092 | 6.361 | 78.0217 | Internet Failure From - 02:15 to 09:50. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
153 | 2014-05-30 | 1210 | 1267 | 1267 | 1361 | 83.09 | 5188.09 | 5000.25 | 187.84 | 5215 | 6.639 | 76.56 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2014-05-31 | 1193 | 1244 | 1278 | 1337 | 76.57 | 5128.57 | 4931.25 | 197.32 | 5144 | 6.554 | 76.49 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2014-06-01 | 1136 | 1187 | 1232 | 1268 | 70.32 | 4893.32 | 4713.75 | 179.57 | 4927 | 6.295 | 76.28 | Grid Failure From - 09:06 to 09:09 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2014-06-02 | 1120 | 1198 | 1210 | 1259 | 70.38 | 4857.38 | 4668.75 | 188.63 | 4881 | 6.18 | 76.9791 | Internet Failure From - 11:00 to 16:45 & Grid Failure From - 17:15 to 17:27. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
158 | 2014-06-03 | 1147 | 1233 | 1227 | 1271 | 76.74 | 4954.74 | 4767.75 | 186.99 | 4981 | 6.361 | 76.32 | Grid Failure From - 12:03 to 12:11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2014-06-04 | 990 | 1057 | 1057 | 1102 | 69.75 | 4275.75 | 4118.25 | 157.5 | 4339 | 5.955 | 71.01 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2014-06-05 | 1192 | 1238 | 1238 | 1251 | 74.72 | 4993.72 | 4813.5 | 180.22 | 5054 | 6.4 | 76.96 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2014-06-06 | 1227 | 1283 | 1272 | 1278 | 82.96 | 5142.96 | 4949.95 | 193.01 | 5173 | 6.596 | 76.43 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2014-06-07 | 1171 | 1210 | 1210 | 1231 | 77.45 | 4899.45 | 4703.2 | 196.25 | 4953 | 6.478 | 74.52 | Grid Failure From - 09:43 to 09:46 & D.O.Fuse of `Y` Phase also Blown of With Grid Failure ,Then Plant Started From - 10:02 After Returned The GRID. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2014-06-08 | 1221 | 1272 | 1266 | 1308 | 85.47 | 5152.47 | 4953.75 | 198.72 | 5182 | 6.601 | 76.51 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2014-06-09 | 1221 | 1267 | 1272 | 1309 | 84.03 | 5153.03 | 4955.25 | 197.78 | 5197 | 6.559 | 77.22 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2014-06-10 | 1142 | 1192 | 1204 | 1248 | 76.18 | 4862.18 | 4671.8 | 190.38 | 4885 | 6.215 | 76.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2014-06-11 | 1102 | 1142 | 1159 | 1198 | 65.85 | 4666.85 | 4482.7 | 184.15 | 4693 | 5.841 | 78.3 | Grid Failure From - 17:55 to 18:00. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2014-06-12 | 1001 | 1046 | 1063 | 1067 | 57.25 | 4234.25 | 4063.5 | 170.75 | 4264 | 5.263 | 78.96 | Grid Failure From - 14:33 to 14:38 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2014-06-13 | 1051 | 1091 | 1119 | 1131 | 68.73 | 4460.73 | 4275.75 | 184.98 | 4474 | 5.589 | 78.02 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 2014-06-14 | 1097 | 1148 | 1123 | 1160 | 69.11 | 4597.11 | 4439.25 | 157.86 | 4649 | 5.848 | 77.48 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 2014-06-15 | 1074 | 1125 | 1178 | 1139 | 72.03 | 4588.03 | 4370.25 | 217.78 | 4587 | 5.702 | 78.4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2014-06-16 | 848 | 893 | 888 | 900 | 41.96 | 3570.96 | 3408.75 | 162.21 | 3601 | 4.529 | 77.49 | Grid Failure From -17:42 to 17:45. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 2014-06-17 | 916 | 967 | 972 | 993 | 49.8 | 3897.8 | 3725.25 | 172.55 | 3938 | 4.843 | 79.25 | Grid Failure From - 13:42 to 14:03 & 18:25 to 18:27. | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 2014-06-18 | 1063 | 1114 | 1120 | 1128 | 66.67 | 4491.67 | 4317 | 174.67 | 4525 | 5.611 | 78.6 | Inverter-1-Shut-Down From 18:05 & Grid Failure From - 18:19 to 18:21. | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 2014-06-19 | 1102 | 1153 | 1164 | 1162 | 64.11 | 4645.11 | 4482.7 | 162.41 | 4709 | 5.786 | 79.3237 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 2014-06-20 | 1069 | 1125 | 1125 | 1128 | 60.01 | 4507.01 | 4332.8 | 174.21 | 4527 | 5.698 | 77.43 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2014-06-21 | 1023 | 1074 | 1080 | 1087 | 52.33 | 4316.33 | 4132.5 | 183.83 | 4333 | 5.522 | 76.44 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2014-06-22 | 944 | 995 | 1007 | 1018 | 46.16 | 4010.16 | 3843 | 167.16 | 4034 | 5.017 | 78.36 | Grid Failure From - 17:34 to 17:42 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 2014-06-23 | 1007 | 1063 | 1068 | 1073 | 54.25 | 4265.25 | 4101 | 164.25 | 4293 | 5.476 | 76.4 | Grid Failure From -11:11 to 11:14 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 2014-06-24 | 1077 | 1136 | 1148 | 1153 | 61.33 | 4575.33 | 4395 | 180.33 | 4595 | 5.866 | 76.34 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2014-06-25 | 995 | 1052 | 1074 | 1068 | 54.58 | 4243.58 | 4078.5 | 165.08 | 4284 | 5.49 | 76.05 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2014-06-26 | 1040 | 1102 | 1136 | 1117 | 61.77 | 4456.77 | 4281.75 | 175.02 | 4502 | 5.709 | 76.85 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2014-06-27 | 1080 | 1176 | 1187 | 1179 | 67.82 | 4689.82 | 4511.25 | 178.57 | 4743 | 6.003 | 77 | Grid Failure From - 17:40 to 17:48 & 18:13 to 18:28. & Inveter No -1 D C vollage low so not start | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2014-06-28 | 1085 | 1193 | 1182 | 1172 | 66.25 | 4698.25 | 4510.5 | 187.75 | 4747 | 5.964 | 77.57 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2014-06-29 | 1080 | 1165 | 1136 | 1133 | 60.29 | 4574.29 | 4393.5 | 180.79 | 4601 | 5.89 | 76.13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 2014-06-30 | 1023 | 1079 | 1052 | 1058 | 53.8 | 4265.8 | 4125 | 140.8 | 4276 | 5.56 | 74.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 2014-07-01 | 1040 | 1080 | 1057 | 1060 | 60.66 | 4297.66 | 4119 | 178.66 | 4342 | 5.44 | 77.79 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2014-07-02 | 1001 | 1046 | 1023 | 1037 | 58.28 | 4165.28 | 3991.5 | 173.78 | 4188 | 5.34 | 76.43 | Grid Failure From - 15:19 to 15:21 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2014-07-03 | 984 | 1024 | 1001 | 1038 | 53.63 | 4100.63 | 3933.75 | 166.88 | 4135 | 5.153 | 78.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2014-07-04 | 984 | 1028 | 1006 | 1055 | 54.59 | 4127.59 | 3952.5 | 175.09 | 4177 | 5.25 | 77.54 | Grid Failure From - 16:26 to 16:47 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2014-07-05 | 1006 | 1046 | 1035 | 1092 | 60.58 | 4239.58 | 4058.25 | 181.33 | 4266 | 5.693 | 73.03 | Grid Failure From - 16:26 to 11:11 to 11:34 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2014-07-06 | 1017 | 1074 | 1063 | 1110 | 62.32 | 4326.32 | 4167 | 159.32 | 4352 | 5.621 | 75.46 | Grid Failure From - 16:26 to 15:39 to 15:57 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 2014-07-07 | 961 | 1001 | 1017 | 1038 | 52.73 | 4069.73 | 3896.25 | 173.48 | 4092 | 5.18 | 76.99 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2014-07-08 | 1069 | 1148 | 1142 | 1146 | 65.36 | 4570.36 | 4390.5 | 179.86 | 4602 | 5.58 | 80.38 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 2014-07-09 | 1046 | 1136 | 1102 | 1124 | 61.52 | 4469.52 | 4277.25 | 192.27 | 4489 | 6.128 | 71.39 | Grid Failure From - 9:06 to 9:16 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 2014-07-10 | 1057 | 1279 | 1063 | 1115 | 62.19 | 4576.19 | 4219.5 | 356.69 | 4433 | 5.783 | 74.71 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 2014-07-11 | 1114 | 950 | 1126 | 1176 | 70.3 | 4436.3 | 4258.5 | 177.8 | 4478 | 6.103 | 71.51 | ABB Inverter no-2 did not wake up in the morning reset it @ 10:00 o clock & Grid failure from - 13:58 to 14:00 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2014-07-12 | 944 | 989 | 961 | 998 | 46.86 | 3938.86 | 3777.75 | 161.11 | 3968 | 5.016 | 77.1 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
199 | 2014-07-13 | 938 | 978 | 949 | 993 | 49.36 | 3907.36 | 3745.5 | 161.86 |  | 5.139 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 2014-07-14 | 605 | 633 | 628 | 634 | 23.35 | 2523.35 | 2392.5 | 130.85 | 2563 | 2.958 | 84.45 | Fully Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
201 | 2014-07-15 | 730 | 758 | 752 | 770 | 29.73 | 3039.73 | 2895 | 144.73 |  | 3.719 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 2014-07-16 | 441 | 458 | 463 | 476 | 15.26 | 1853.26 | 1739.25 | 114.01 | 1892 | 2.231 | 82.65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 2014-07-17 | 650 | 684 | 679 | 718 | 26.64 | 2757.64 | 2631 | 126.64 | 2791 | 3.232 | 84.16 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 ++tive in AJB-100 of The Inverter-4 during The Period of 10:15 To 10:20. Battery water Fileed in 03 no`s of Compund Light ( 02 Back side Light & 01 Front side Light ) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
204 | 2014-07-18 | 401 | 407 | 413 | 428 | 12.57 | 1661.57 | 1549.5 | 112.07 | 1695 | 1.973 | 83.73 | Grid Failure From - 10:32 to 10:42 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2014-07-19 | 729 | 752 | 751 | 794 | 28.09 | 3054.09 | 2916 | 138.09 | 3081 | 3.589 | 83.67 | Fully Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
206 | 2014-07-20 | 990 | 1023 | 1029 | 1078 | 47.71 | 4167.71 | 4002 | 165.71 | 4189 | 5.016 | 81.39 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 2014-07-21 | 1017 | 1052 | 1057 | 1106 | 55.94 | 4287.94 | 4110 | 177.94 | 4301 | 5.32 | 78.79 | Grid Failure From - 14:05 to 14:43 & D.O.Fuse of `R` Phase also Blown of With Grid Failure ,Then Plant Started From - 14:43 After Returned The GRID.WO # 791503 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 2014-07-22 | 945 | 975 | 978 | 1020 | 44.89 | 3962.89 | 3810 | 152.89 | 3986 | 4.757 | 81.66 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 2014-07-23 | 344 | 356 | 357 | 363 | 10.39 | 1430.39 | 1312.5 | 117.89 | 1442 | 1.665 | 84.41 | Fully Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
210 | 2014-07-24 | 113 | 119 | 124 | 124 | 2.41 | 482.41 | 388 | 94.41 | 509 | 685 | 72.42 | Heavy Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 2014-07-25 | 571 | 594 | 594 | 616 | 17.92 | 2392.92 | 2259 | 133.92 | 2412 | 2.754 | 85.36 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 2014-07-26 | 911 | 932 | 938 | 999 | 41.76 | 3821.76 | 3658.5 | 163.26 | 3866 | 4.7 | 80.17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 2014-07-27 | 898 | 928 | 933 | 980 | 41.65 | 3780.65 | 3626.25 | 154.4 | 3806 | 4.513 | 82.19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 2014-07-28 | 730 | 752 | 757 | 788 | 30.07 | 3057.07 | 2922.75 | 134.32 | 3077 | 3.615 | 82.96 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 2014-07-29 | 559 | 582 | 583 | 598 | 18.98 | 2340.98 | 2218.5 | 122.48 | 2367 | 2.72 | 84.81 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2014-07-30 | 684 | 706 | 712 | 748 | 26.98 | 2876.98 | 2731.5 | 145.48 | 2907 | 3.412 | 83.04 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 2014-07-31 | 945 | 973 | 978 | 1051 | 48.81 | 3995.81 | 3836.25 | 159.56 | 4026 | 4.998 | 78.51 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
219 | 2014-08-01 | 966 | 989 | 989 | 1070 | 47.28 | 4061.28 | 3899.25 | 162.03 | 4086 | 5.046 | 78.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 2014-08-02 | 662 | 690 | 690 | 718 | 26.83 | 2786.83 | 2646 | 140.83 | 2808 | 3.321 | 82.41 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 2014-08-03 | 650 | 667 | 673 | 711 | 27.14 | 2728.14 | 2584.5 | 143.64 | 2745 | 3.359 | 79.64 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 2014-08-04 | 752 | 775 | 780 | 812 | 27.61 | 3146.61 | 3000 | 146.61 | 3176 | 3.845 | 80.5 | Grid Failure From - 10:15 to 10:24 WO#980264 & Cloudy Day | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
223 | 2014-08-05 | 599 | 616 | 622 | 637 | 21.31 | 2495.31 | 2388.75 | 106.56 | 2530 | 2.966 | 83.13 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 2014-08-06 | 328 | 339 | 339 | 341 | 9.06 | 1356.06 | 1243.5 | 112.56 | 1375 | 1.566 | 85.57 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 2014-08-07 | 701 | 724 | 729 | 754 | 25.43 | 2933.43 | 2805 | 128.43 | 2967 | 3.463 | 83.5 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
226 | 2014-08-08 | 967 | 989 | 979 | 1054 | 53.53 | 4042.53 | 3879 | 163.53 | 4067 | 5.112 | 77.54 | Grid Failure From - 17:58 to 18:25 WO#1058270 & Cloudy Day | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
227 | 2014-08-09 | 1091 | 1125 | 1130 | 1173 | 59.04 | 4578.04 | 4404.75 | 173.29 | 4626 | 5.698 | 79.12 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 2014-08-10 | 927 | 961 | 967 | 1002 | 52.42 | 3909.42 | 3748.5 | 160.92 | 3937 | 4.799 | 79.95 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
229 | 2014-08-11 | 905 | 922 | 921 | 973 | 48.35 | 3769.35 | 3615 | 154.35 | 3798 | 4.647 | 79.65 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
230 | 2014-08-12 | 1079 | 1119 | 1097 | 1178 | 58.65 | 4531.65 | 4353.75 | 177.9 | 4555 | 5.82 | 76.28 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 2014-08-13 | 826 | 848 | 842 | 907 | 43.38 | 3466.38 | 3318.75 | 147.63 | 3474 | 4.3 | 78.74 | Grid Failure From - 9:13 to 9:25(WO#1113328) & second time Grid Failure From - 11:12 to 11:15 & D.O.Fuse of `Y` Phase also Blown of With Grid Failure ,Then Plant Started From - 11:27 After Returned The GRID.(WO#1114096) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 2014-08-14 | 752 | 774 | 758 | 803 | 32.61 | 3119.61 | 2981.25 | 138.36 | 3148 | 3.769 | 81.4 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 2014-08-15 | 881 | 911 | 905 | 951 | 38.63 | 3686.63 | 3522 | 164.63 | 3710 | 4.476 | 80.78 | Cloud and Rain | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 2014-08-16 | 809 | 836 | 814 | 877 | 36.72 | 3372.72 | 3216.75 | 155.97 | 3401 | 4.304 | 77.01 | Grid Failure From - 14:30 to 15:40 WO#1153598 & Rain & Cloudy | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
235 | 2014-08-17 | 995 | 1029 | 1017 | 1050 | 39.65 | 4130.65 | 3965.25 | 165.4 | 4161 | 5.119 | 79.22 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
236 | 2014-08-18 | 1102 | 1137 | 1131 | 1192 | 47.81 | 4609.81 | 4434 | 175.81 | 4645 | 5.83 | 77.65 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07 --tive in AJB-116 of The Inverter-3 during The Period of 10:20 To 10:25.WO#(1174948) & Rain & Cloudy | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
237 | 2014-08-19 | 1080 | 1119 | 1114 | 1180 | 49.15 | 4542.15 | 4363.5 | 178.65 | 4562 | 5.763 | 77.15 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
238 | 2014-08-20 | 1165 | 1221 | 1204 | 1245 | 54.27 | 4889.27 | 4703.25 | 186.02 | 4909 | 6.228 | 76.82 | Today I Replaced The 1 D.C.12Amp Fuse Link of The String- 07 ++tive in AJB-109 of The Inverter-2 during The Period of 10:50 To 10:55.WO#(1220529) & 2, D.C.12Amp Fuse Link of The String- 08 --tive in AJB-112 of The Inverter-2 during The Period of 16:35 To 16:40.WO#(1223722) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
239 | 2014-08-21 | 1193 | 1255 | 1244 | 1310 | 53.96 | 5055.96 | 4864.5 | 191.46 | 5084 | 6.439 | 76.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 2014-08-22 | 1057 | 1114 | 1108 | 1142 | 56.82 | 4477.82 | 4307.25 | 170.57 | 4501 | 6.085 | 72.09 | Grid Failure From 12:33 to12:47 for D.O Fuse of "Y" Phase blown after replace fuse and plant start | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 2014-08-23 | 554 | 582 | 576 | 601 | 28.05 | 2341.05 | 2217 | 124.05 | 2367 | 2.848 | 81 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
242 | 2014-08-24 | 707 | 752 | 747 | 778 | 32.1 | 3016.1 | 2858.25 | 157.85 | 3069 | 4.731 | 63.22 | D.O Fuse of "Y" phase blown at 10:30 Am, Fuse was replaced and plant started at 11:35 Am. & Rain & Cloudy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
243 | 2014-08-25 | 780 | 820 | 820 | 851 | 36.31 | 3307.31 | 3152.25 | 155.06 | 3347 | 4.045 | 80.64 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
244 | 2014-08-26 | 1170 | 1238 | 1238 | 1307 | 74.22 | 5027.22 | 4830 | 197.22 | 5055 |  |  | D.O Fuse of "Y" phase blown at 10:10 Am, Fuse was replaced and plant started at 11:24 (WO#1306835) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 2014-08-27 | 978 | 1040 | 1040 | 1084 | 59.11 | 4201.11 | 4027.5 | 173.61 | 4224 |  |  | D.O Fuse of "R"Y"B" phase blown at 12:10 Am, Fuse was replaced and plant started at 13:08 Pm. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 2014-08-28 | 1102 | 1165 | 1175 | 1187 | 58.56 | 4687.56 | 4502.25 | 185.31 | 4714 |  |  | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
247 | 2014-08-29 | 1024 | 1091 | 1092 | 1125 | 55.25 | 4387.25 | 4224 | 163.25 | 4421 |  |  | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
248 | 2014-08-30 | 384 | 407 | 412 | 403 | 12.41 | 1618.41 | 1499.25 | 119.16 | 1640 |  |  | Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
249 | 2014-08-31 | 939 | 995 | 995 | 1063 | 48.44 | 4040.44 | 3877.5 | 162.94 | 4083 |  |  | D.O Fuse of "Y" phase blown at 12:50 Am, Fuse was replaced and plant started at 13:08 (WO#1383416) Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
251 | 2014-09-01 | 548 | 588 | 588 | 603 | 18.43 | 2345.43 | 2223 | 122.43 | 2378 |  |  | D.O Fuse of "R" phase blown at 13:30 Am, Fuse was replaced and plant started at 13:48 (WO#) Rain & Cloudy Day & 2 time Grid Failure from-8:10 to 10:46 wo#(1395963) & 11:30 to 12:25wo#(1397012) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
252 | 2014-09-02 | 837 | 882 | 894 | 900 | 28.6 | 3541.6 | 3407.25 | 134.35 | 3580 |  |  | Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
253 | 2014-09-03 | 672 | 712 | 712 | 733 | 21.16 | 2850.16 | 2709.75 | 140.41 | 2883 |  |  | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
254 | 2014-09-04 | 221 | 237 | 243 | 230 | 6.3 | 937.3 | 841 | 96.3 | 999 |  |  | Grid Failure From - 14:08 to 14:54 WO#1437911 & Rain & Cloudy & Inv-No:-4 Filter & inveter cleaning | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
255 | 2014-09-05 | 910 | 962 | 967 | 970 | 24.83 | 3833.83 | 3668.25 | 165.58 | 3862 |  |  | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
256 | 2014-09-06 | 1074 | 1136 | 1142 | 1176 | 29.96 | 4557.96 | 4385.25 | 172.71 | 4591 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 2014-09-07 | 961 | 1023 | 1029 | 1034 | 28.51 | 4075.51 | 3901 | 174.51 | 4097 |  |  | D.O Fuse of "R'&'Y" phase blown at 10:47 Am, Fuse was replaced and plant started at 11:20 (WO#1486006) Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
258 | 2014-09-08 | 204 | 221 | 220 | 212 | 5.99 | 862.99 | 759 | 103.99 | 921 |  |  | Grid Failure From - 15:34 to 15:44 WO#1501674 & Grid Failure From - 17:02 to 17:37 & Grid Failure From - 17:54 to 18:16 & Fully Rain | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2014-09-09 | 170 | 186 | 187 | 178 | 4.62 | 725.62 | 619.5 | 106.12 | 767 |  |  | Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
260 | 2014-09-10 | 152 | 159 | 164 | 153 | 3.82 | 631.82 | 525 | 106.82 | 668 | 816 | 79.79 | Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
261 | 2014-09-11 | 452 | 480 | 486 | 463 | 13.27 | 1894.27 | 1791 | 103.27 | 1941 | 2.15 | 87.99 | Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
262 | 2014-09-12 | 685 | 729 | 729 | 738 | 25.74 | 2906.74 | 2772.75 | 133.99 | 2947 | 3.507 | 81.9 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
263 | 2014-09-13 | 678 | 724 | 729 | 724 | 27.22 | 2882.22 | 2750.25 | 131.97 | 2924 | 3.427 | 83.16 | Grid Failure From - 16:50 to 16:54 & Cloudy Day | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
264 | 2014-09-14 | 786 | 831 | 831 | 841 | 34.18 | 3323.18 | 3180 | 143.18 | 3357 | 4.019 | 81.41 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
265 | 2014-09-15 | 740 | 774 | 781 | 787 | 34.26 | 3116.26 | 2978.25 | 138.01 | 3148 | 3.837 | 79.96 | Rain & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
266 | 2014-09-16 | 1074 | 1142 | 1142 | 1172 | 52.04 | 4582.04 | 4416.75 | 165.29 | 4619 |  |  | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
267 | 2014-09-17 | 962 | 1024 | 1017 | 1038 | 49.41 | 4090.41 | 3917.25 | 173.16 | 4105 | 5.617 | 71.22 | Grid Failure From - 13:02 to 14:20 WO#1631677 & Cloudy Day | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
268 | 2014-09-18 | 1170 | 1226 | 1233 | 1246 | 69.4 | 4944.4 | 4755 | 189.4 | 4971 | 6.588 | 73.54 | D.O Fuse of "R" phase blown at 12:12 pm, Fuse was replaced and plant started at 12:34 (WO#1644643) & Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
269 | 2014-09-19 | 1260 | 1312 | 1322 | 1353 | 73.65 | 5320.65 | 5111.25 | 209.4 | 5334 | 6.765 | 76.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 2014-09-20 | 1272 | 1329 | 1335 | 1393 | 74 | 5403 | 5191.5 | 211.5 | 5424 | 6.819 | 77.52 | Today I Replaced The 1 D.C.12Amp Fuse Link of The String-NO- 02 ++tive in AJB-101 of The Inverter-4 during The Period of 10:40 To 10:45.WO#(1671005) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
271 | 2014-09-21 | 1222 | 1266 | 1266 | 1316 | 70.68 | 5140.68 | 4939.5 | 201.18 | 5167 | 6.58 | 76.53 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 2014-09-22 | 938 | 973 | 967 | 1011 | 51.04 | 3940.04 | 3774.75 | 165.29 | 3963 | 5.131 | 75.27 | Grid Failure From - 10:12 to 10:35 WO#1697916 & Cloudy Day | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
273 | 2014-09-23 | 1176 | 1215 | 1215 | 1299 | 67.97 | 4972.97 | 4784.25 | 188.72 | 4998 | 6.43 | 75.75 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
274 | 2014-09-24 | 1125 | 1165 | 1188 | 1265 | 64.04 | 4807.04 | 4620.75 | 186.29 | 4832 | 6.224 | 75.66 | Grid Failure From - 8:28 to 8:37 WO#1724239 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | 2014-09-25 | 882 | 927 | 955 | 969 | 29.07 | 3762.07 | 3607.5 | 154.57 | 3796 | 5.404 | 68.46 | Today I Replaced The D.C.12Amp Fuse Link of The String- 08 --tive in AJB-110 of The Inverter-2 during The Period of 12:10 To 12:15.WO#(1737960) & Grid Failure From - 07:29 to 07:55 & our vcb trip After reset vcb plant started 9:32 WO#1736380 & Cloudy | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
276 | 2014-09-26 | 1140 | 1198 | 1238 | 1245 | 39.44 | 4860.44 | 4656 | 204.44 | 4870 | 6.282 | 75.55 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2014-09-27 | 1192 | 1261 | 1306 | 1321 | 39.78 | 5119.78 | 4924.5 | 195.28 | 5148 | 6.678 | 75.15 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 2014-09-28 | 1126 | 1182 | 1216 | 1257 | 38.25 | 4819.25 | 4625.25 | 194 | 4840 | 6.369 | 74.06 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2014-09-29 | 994 | 1051 | 1079 | 1111 | 34.33 | 4269.33 | 4090.5 | 178.83 | 4292 | 5.623 | 74.39 | Cloudy Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
280 | 2014-09-30 | 996 | 1046 | 1075 | 1114 | 34.08 | 4265.08 | 4095 | 170.08 | 4294 | 5.629 | 74.35 | Grid Failure From - 10:12 to 10:35 WO#1822946 & Cloudy Day | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
282 | 2014-10-01 | 1096 | 1165 | 1187 | 1230 | 35.6 | 4713.6 | 4522.5 | 191.1 | 4739 | 6.174 | 74.81 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2014-10-02 | 1131 | 1198 | 1221 | 1279 | 36.23 | 4865.23 | 4683 | 182.23 | 4894 | 6.364 | 74.95 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 2014-10-03 | 1153 | 1221 | 1272 | 1294 | 36.51 | 4976.51 | 4785.75 | 190.76 | 5024 | 6.493 | 75.41 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2014-10-04 | 1148 | 1210 | 1277 | 1278 | 37.31 | 4950.31 | 4756.5 | 193.81 | 4973 | 6.414 | 75.56 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2014-10-05 | 918 | 972 | 1012 | 1035 | 30.02 | 3967.02 | 3792.75 | 174.27 | 3981 | 5.159 | 75.21 | Grid Failure From - 14:17 to 16:53 WO#1888096 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2014-10-06 | 882 | 924 | 984 | 974 | 37.77 | 3801.77 | 3647.25 | 154.52 | 3856 | 4.855 | 77.41 | Grid Failure From - 16:32 to 16:34 WO#1697916 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2014-10-07 | 1159 | 1227 | 1295 | 1323 | 52.03 | 5056.03 | 4857 | 199.03 | 5076 | 6.497 | 76.14 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 --tive in AJB-105 of The Inverter-4 during The Period of 10:45 To 10:50.WO#1914138 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
289 | 2014-10-08 | 40 | 1152 | 1176 | 1222 | 44.4 | 3634.4 | 3439.5 | 194.9 | 3627 |  |  | Grid Failure From - 8:10 to 8:25 WO#1926295 & 8:50 Inverter 1 is down, informed ABB. They will be working to resolve this issue WO#1926581 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2014-10-09 |  | 1199 | 1193 | 1212 | 44.14 | 3648.14 | 3490.5 | 157.64 | 3685 | 6.057 | 5929 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 2014-10-10 |  | 1232 | 1198 | 1210 | 44.52 | 3684.52 | 3535.5 | 149.02 | 3715 | 6.172 | 58.66 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 2014-10-11 |  | 1091 | 1057 | 1066 | 30.15 | 3244.15 | 3108 | 136.15 | 3260 | 6.284 | 50.56 | Grid Failure From - 8:47 to 9:25 & D.O.Fuse of `B` Phase also Blown of With High Frequncy & Fuse link sport also Blown ,Then Plant Started From - 9:42 .WO # 1972636 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
294 | 2014-10-12 |  | 1148 | 1227 | 1239 | 34.77 | 3648.77 | 3514.5 | 134.27 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 2014-10-13 |  | 1266 | 1221 | 1207 | 34.84 | 3728.84 | 3570.75 | 158.09 | 3764 | 6.439 | 56.97 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2014-10-14 |  | 1222 | 1165 | 1166 | 34 | 3587 | 3429.75 | 157.25 | 3621 | 6.362 | 55.47 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2014-10-15 |  | 1125 | 1080 | 1094 | 32.36 | 3331.36 | 3183 | 148.36 | 3371 | 5.931 | 55.39 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & cleaning & tietnece L.T panel | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2014-10-16 |  | 1063 | 1017 | 1072 | 26.56 | 3178.56 | 3029.25 | 149.31 | 3222 | 6.268 | 50.1 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & cleaning & tietnece L.T panel & Grid Failure From - 8:27 to 9:43 WO#2043269 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2014-10-17 |  | 1209 | 1148 | 1277 | 30.23 | 3664.23 | 3507.75 | 156.48 | 3708 | 6.361 | 56.81 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581, & Today I Replaced The D.C.12Amp Fuse Link of The String- 04 --tive in AJB-105 of The Inverter-4 during The Period of 10:50 To 10:55.WO#2057851 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
300 | 2014-10-18 |  | 1204 | 1181 | 1271 | 29.99 | 3685.99 | 3530.25 | 155.74 | 3719 | 6.385 | 56.76 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2014-10-19 |  | 1160 | 1171 | 1197 | 30.33 | 3558.33 | 3405 | 153.33 | 3599 | 6.129 | 57.23 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2014-10-20 |  | 1124 | 1158 | 1197 | 29.62 | 3508.62 | 3354.75 | 153.87 | 3547 | 5.976 | 57.84 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 17:15 to 17:42 WO#2101384 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2014-10-21 |  | 1171 | 1205 | 1221 | 29.69 | 3626.69 | 3489 | 137.69 | 3691 | 5.094 | 70.62 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 11:03 to 11:11 WO#2110541 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2014-10-22 |  | 1187 | 1181 | 1136 | 29.47 | 3533.47 | 3384.75 | 148.72 | 3585 | 6.017 | 58.07 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 8:44 to 8:54 WO#2122704 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 2014-10-23 |  | 1159 | 1131 | 316 | 27.9 | 2633.9 | 2490.75 | 143.15 | 2694 | 5.928 | 44.29 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 11:05 to 11:10 WO#2138394 & inverter 4 producing low due to cybro controler faulty WO#2138162 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2014-10-24 |  | 1051 | 1029 | 1002 | 33.39 | 3115.39 | 2977.5 | 137.89 | 3186 | 5.155 | 60.23 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2014-10-25 |  | 1171 | 1142 | 1128 | 38.03 | 3479.03 | 3328.5 | 150.53 | 3547 | 5.73 | 60.33 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 16:39 to 16:44 WO#2175271 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2014-10-26 |  | 933 | 910 | 880 | 30.35 | 2753.35 | 2611.5 | 141.85 | 2793 | 4.498 | 60.52 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2014-10-27 |  | 1023 | 995 | 985 | 33.97 | 3036.97 | 2895 | 141.97 | 3082 | 5.008 | 59.98 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure From - 15:06 to 16:13 WO# | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2014-10-28 |  | 96 | 91 | 85 | 3.84 | 275.84 | 209.25 | 66.59 | 317 |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Grid Failure & Government side 11kv H Poll "R" Phase L.A Failure From - 8:17 to 15:55 WO#2212818 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2014-10-29 |  | 204 | 197 |  | 6.18 | 407.18 | 396 | 11.18 |  |  |  | inverter 1 & 4 is down iformed ABB & Schneider & Grid Failure with High voltage than our plant sort circuit than plant(inverter 1&2) started 11:55 & U.P.S & Battery charger Blown | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
312 | 2014-10-30 |  | 480 | 470 |  | 15.99 | 965.99 | 899.25 | 66.74 |  |  |  | inverter 1 & 4 is down iformed ABB & Schneider & Grid Failure with High voltage than our plant sort circuit than plant(inverter 1&2) started 11:55 & U.P.S & Battery charger Blown & our side visit schneider engineer & resolve issue inverter no-4 started | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
313 | 2014-10-31 |  | 758 | 740 | 734 | 24.58 | 2256.58 | 2142 | 114.58 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & U.P.S & Battery charger Blown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
315 | 2014-11-01 |  | 1000 | 978 | 964 | 33.64 | 2975.64 | 2849.25 | 126.39 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & U.P.S & Battery charger Blown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
316 | 2014-11-02 |  | 1035 | 1008 | 980 | 36 | 3059 | 2928.75 | 130.25 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & U.P.S & Battery charger Blown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
317 | 2014-11-03 |  | 972 | 927 | 1034 | 36.96 | 2969.96 | 2853.75 | 116.21 |  |  |  | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown & U.P.S rectified | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
318 | 2014-11-04 |  | 1052 | 1006 | 1033 | 36.32 | 3127.32 | 2996.25 | 131.07 | 3147 | 5.381 | 57 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
319 | 2014-11-05 |  | 1198 | 1131 | 1244 | 39.8 | 3612.8 | 3468.75 | 144.05 | 3623 | 5.793 | 60.95 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
320 | 2014-11-06 |  | 1216 | 1159 | 1300 | 40.56 | 3715.56 | 3567 | 148.56 | 3739 | 6.237 | 58.42 | Inverter 1 is down, informed ABB.They will be working resolve this issue WO#1926581 & Battery charger Blown & Grid failure from 16:21 to 16:25 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
321 | 2014-11-07 | 6 | 1170 | 1108 | 1247 | 56.77 | 3587.77 | 3450 | 137.77 | 3624 | 6.146 | 57.47 | Grid Failure From - 9:50 to 9:55 WO#2369551 & ABB Service engineer Mr. Salim has come to site. He has rectified the problem by replacing faulty ACB. Inverter starte at 16:20 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2014-11-08 | 1046 | 1097 | 1040 | 1087 | 65.07 | 4335.07 | 4150.5 | 184.57 | 4355 | 5.763 | 73.65 | Grid Failure From 9:18 to 9:30 & inverter no 4 down due to auxiliary supply MCB tripped and it was not able to reset for 30 minutes after that reset @ 10:00 AM. WO #2387806 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2014-11-09 | 1040 | 1102 | 1052 | 1169 | 66.25 | 4429.25 | 4255.5 | 173.75 | 4458 | 5.723 | 75.92 | Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
324 | 2014-11-10 | 950 | 1001 | 989 | 1035 | 57.55 | 4032.55 | 3867 | 165.55 | 4058 | 5.201 | 76.04 | Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
325 | 2014-11-11 | 899 | 950 | 1006 | 967 | 52.43 | 3874.43 | 3708 | 166.43 | 3894 | 4.926 | 77.04 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07 ++tive in AJB-116 of The Inverter-3 during The Period of 10:35 To 10:40.WO#(2435089) & Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
326 | 2014-11-12 | 910 | 1017 | 1035 | 1015 | 54.88 | 4031.88 | 3864 | 167.88 | 4057 | 5.1 | 77.53 | Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
327 | 2014-11-13 | 905 | 1023 | 1000 | 990 | 51.65 | 3969.65 | 3801 | 168.65 | 3991 | 4.986 | 78.01 | Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
328 | 2014-11-14 | 842 | 905 | 882 | 861 | 42.65 | 3532.65 | 3389.25 | 143.4 | 3579 | 4.646 | 75.08 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 ++tive in AJB-102 of The Inverter-1 during The Period of 11:55 To 12:00.WO#(2480488) & Battery charger Blown & Grid Failure From - 15:54 to 16:03 WO#2482657 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0
329 | 2014-11-15 | 695 | 729 | 713 | 690 | 28.43 | 2855.43 | 2739 | 116.43 | 2851 | 3.764 | 73.82 | Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
330 | 2014-11-16 | 792 | 837 | 819 | 825 | 37.41 | 3310.41 | 3165.75 | 144.66 | 3366 | 4.314 | 76.04 | Battery charger Blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
331 | 2014-11-17 | 887 | 950 | 916 | 972 | 37.37 | 3762.37 | 3612.75 | 149.62 | 3802 | 5.035 | 73.59 | Battery charger Blown & Grid Failure From - 8:00 to 9:20 WO#2541824 & 9:59 to 10:05 WO#2542101 & 17:32 to 17:46 WO#2546487 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
332 | 2014-11-18 | 877 | 927 | 882 | 936 | 47.83 | 3669.83 | 3522 | 147.83 | 3711 | 5.049 | 71.63 | Battery charger Blown Grid & Failure From - 8:31 to 9:09 WO#2556092 & inverter no-3 morning time note wake up so reset (3 time inverter on off) to inverter so started 9:10 WO#2555238 & Array /balance of system | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
333 | 2014-11-19 | 1017 | 1079 | 1074 | 1105 | 61.98 | 4336.98 | 4165.5 | 171.48 | 4370 | 5.64 | 75.51 | Battery charger Blown & Tracker P.M | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
334 | 2014-11-20 | 1074 | 1143 | 1142 | 1172 | 68.94 | 4599.94 | 4428 | 171.94 | 4636 | 6.053 | 74.64 | Battery charger Blown &Combiner & Grid Failure From- 15:31 to 15:43 WO#2589251 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
335 | 2014-11-21 | 995 | 1057 | 1086 | 1078 | 60.32 | 4276.32 | 4108.5 | 167.82 | 4334 | 5.496 | 76.85 | Seeds (Das) meteorological (MET) station p.m & Battery charger blown | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
336 | 2014-11-22 | 1029 | 1108 | 1131 | 1111 | 62.61 | 4441.61 | 4267.5 | 174.11 | 4471 | 5.753 | 75.74 | Battery charger Blown & Grid Failure From- 16:59 to 17:09 WO# 2627748 & 17:25 to 17:30 WO# 2627992 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
337 | 2014-11-23 | 1006 | 1102 | 1102 | 826 | 61.33 | 4097.33 | 3942 | 155.33 | 4141 | 5.741 | 70.3 | Battery charger blown & Grid failure from- 9:48 to 9:53 WO# 2639096 & Inverter #4 due to auto tripped it was not able to reset 1:35 hour after that reset @2:35 WO# 2640754 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
338 | 2014-11-24 | 996 | 1114 | 1091 | 367 | 59.29 | 3627.29 | 3456 | 171.29 | 3648 | 5.608 | 63.4 | Inverter #4 is down 11:12 AM informed Schneider WO#2656601 & Transformer No-4 (P.M R,B,N,)Oil Lickege gass kitt failure | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2014-11-25 | 1006 | 1102 | 1063 | 1035 | 58.03 | 4264.03 | 4095 | 169.03 | 4291 | 5.529 | 75.64 | Grid failure from- 13:18 to 13:30 WO#2671705 & Module visual Inspection P.M | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2014-11-26 | 1057 | 1125 | 1085 | 1031 | 56.49 | 4354.49 | 4188.75 | 165.74 | 4386 | 5.834 | 73.27 | Inverter #4 is morning time on, off on, off, call to schneider service engineer is going to attend this problem tomorrow. | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2014-11-27 | 1063 | 1131 | 1091 | 348 | 56.47 | 3689.47 | 3512.25 | 177.22 | 3720 | 5.761 | 70.9 | Inverter # 4 ,11:15 auto trip and it was not able to reset after schneider engineer come to our side and resolve issue inverter started from 17:05 WO#2700380 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2014-11-28 | 1040 | 1103 | 1063 | 874 | 55.32 | 4135.32 | 3983.25 | 152.07 | 4173 | 5.764 | 68.53 | Inverter # 4 ,11:35 auto tripped & 13:05 auto start & Grid Failure From -17:05 to 17:11 & scond time 17:27 to 17:33 WO# 2719696 & WO#2720220 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2014-11-29 | 984 | 1040 | 1012 |  | 51.45 | 3087.45 | 2931.75 | 155.7 | 3115 | 5.418 | 66.16 | Inverter 4 is down, informed Schneider.They will be working resolve this issue & Grid Failure From- 17:31 to 17:39 WO#2738903 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 2014-11-30 | 978 | 1040 | 1023 | 957 | 51.77 | 4049.77 | 3883.5 | 166.27 | 4084 | 5.426 | 63.79 | Inverter #4 replesh the D.C 12 Volts realy & solle the issue Inverter started 09:10 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2014-12-01 | 904 | 955 | 967 | 976 | 46.94 | 3848.94 | 3686.25 | 162.69 | 3879 | 5.317 | 71.1 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 ++tive in AJB-101 of The Inverter-4 during The Period of 10:35 To 10:40.WO#(2766976) & Grid Failure From- 14:08 to 15:09 WO#2769479 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
347 | 2014-12-02 | 916 | 995 | 995 | 1008 | 51.67 | 3965.67 | 3809.25 | 156.42 | 4004 | 5.251 | 74.31 | Grid Failure From- 11:32 to 11:45 WO#2783874 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2014-12-03 | 1035 | 1131 | 1108 | 1113 | 61.31 | 4448.31 | 4266 | 182.31 | 4468 | 5.768 | 75.49 | Grid Failure From- 16:50 to 16:58 WO#2803128 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2014-12-04 | 1057 | 1131 | 1108 | 1095 | 62.69 | 4453.69 | 4283.25 | 170.44 | 4483 | 5.81 | 75.2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 2014-12-05 | 1023 | 1097 | 1063 | 1057 | 58.87 | 4298.87 | 4126.5 | 172.37 | 4342 | 5.608 | 75.46 | Grid Failure From- 12:39 to 13:05 WO#2832390 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2014-12-06 | 1024 | 1096 | 1069 | 1076 | 52.46 | 4317.46 | 4153.5 | 163.96 | 4365 | 5.532 | 76.9 | Grid Failure From 15:00 to 15:04 WO#2848950 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2014-12-07 | 1068 | 1148 | 1114 | 1143 | 62.32 | 4535.32 | 4355.25 | 180.07 | 4558 | 5.919 | 75.05 | Grid Failure-Plant started 7:55 to WO#2861355 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2014-12-08 | 972 | 1051 | 1023 | 1035 | 50.84 | 4131.84 | 3963 | 168.84 | 4165 | 5.425 | 74.82 | Grid Failure From 7:05 to 8:07 WO#2878909 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2014-12-09 | 1052 | 1131 | 1142 | 1023 | 58.23 | 4406.23 | 4231.5 | 174.73 |  |  |  | Inverter No-4 started 9:13 WO#2895864 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2014-12-10 | 972 | 1057 | 1074 | 1015 | 51.41 | 4169.41 | 3995.25 | 174.16 | 4191 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2014-12-11 | 916 | 1018 | 1000 | 909 | 48.04 | 3891.04 | 3729.75 | 161.29 | 3911 | 4.893 | 77.9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2014-12-12 | 944 | 1029 | 1012 | 930 | 48.41 | 3963.41 | 3792 | 171.41 | 3994 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2014-12-13 | 967 | 1023 | 1012 | 929 | 49.31 | 3980.31 | 3822 | 158.31 | 4001 | 5.146 | 75.77 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2014-12-14 | 1023 | 1091 | 1069 | 986 | 53.29 | 4222.29 | 4048.5 | 173.79 | 4234 | 5.435 | 75.92 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2014-12-15 | 1086 | 1159 | 1142 | 1079 | 57.41 | 4523.41 | 4338.75 | 184.66 | 4539 | 5.882 | 75.21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2014-12-16 | 1000 | 1057 | 1046 |  | 55.14 | 3158.14 | 3026.25 | 131.89 | 3199 | 5.336 | 58.43 | Grid Failure From 7:05 to 8:07 WO#2878909 & Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2014-12-17 | 1074 | 1142 | 1131 |  | 65.75 | 3412.75 | 3243 | 169.75 | 3423 | 5.686 | 58.67 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2014-12-18 | 967 | 1018 | 1062 |  | 60.44 | 3107.44 | 2961.75 | 145.69 | 3143 |  |  | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 15:19 to 16:35 WO# 3108567 & 2 Time 16:39 to 16:44 WO#3108613 3 Time 17:42 to 1749 WO#3109816 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2014-12-19 | 860 | 978 | 1001 |  | 46.05 | 2885.05 | 2751 | 134.05 | 2900 | 5.059 | 55.87 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 14:35 to 16:05 WO#3127429 & Inverter 1 is down Informed ABB (Inverter side Mini power supply faulty) | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2014-12-20 | 390 | 435 | 531 |  | 21.83 | 1377.83 | 1298.25 | 79.58 | 1415 | 2.472 | 55.79 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 12:24 to 12:47 WO#3144608 & 15:21 to 15:23 WO#3150822 & Inverter 1 is down Informed ABB (Inverter side Mini power supply faulty) inverter started 11:40 a.m & Cloudy Day | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
366 | 2014-12-21 | 1051 | 1142 | 1148 |  | 66.68 | 3407.68 | 3268.5 | 139.18 | 3414 | 5.867 | 56.71 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 14:20 to 14:30 WO# 3167155 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 2014-12-22 | 1018 | 1058 | 1063 |  | 61.05 | 3200.05 | 3055.5 | 144.55 | 3212 |  |  | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-103 of The Inverter-1 during The Period of 9:55 To 10:00.WO#(3181932) & Inverter No-1 mini power bank (D.C.15 VOLTS) Repleshed & Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
368 | 2014-12-23 | [5 empty] | 0 |  | 0 | 560 |  |  | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 10:25 to 19:30 WO# 3201757 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 2014-12-24 | [5 empty] | 0 |  | 0 | 3159 |  |  | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 2014-12-25 | 1012 | 1063 | 1063 |  | 62.49 | 3200.49 | 3074.25 | 126.24 | 3212 | 5.473 | 57.2 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 12:38 to 12:43 WO# 3240768 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 2014-12-26 | 1131 | 1176 | 1215 |  | 73.58 | 3595.58 | 3441 | 154.58 | 3589 | 6.107 | 57.27 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 2014-12-27 | 882 | 933 | 967 |  | 56.9 | 2838.9 | 2713.5 | 125.4 | 2841 | 5.052 | 54.81 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 14:31 to 16:38 WO# 3283954 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 2014-12-28 | 1085 | 1187 | 1210 |  | 67.18 | 3549.18 | 3384.75 | 164.43 | 3542 | 5.93 | 58.21 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 --tive in AJB-101 of The Inverter-1 during The Period of 15:25 To 15:30.WO#(3300992) & Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
374 | 2014-12-29 | 667 | 707 | 723 |  | 42.84 | 2139.84 | 2031.75 | 108.09 | 2155 | 3.683 | 57.02 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 12:48 to 12:54 WO# 3316468 & Grid Failure From 13:22 to 17:41 WO# | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 2014-12-30 | 1001 | 1080 | 1086 |  | 56.74 | 3223.74 | 3087 | 136.74 | 3237 | 5.335 | 59.13 | Inverter 4 is down, informed Schneider.They will be working resolve this issue (Inverter side D.C,contector Blon) & Grid Failure From 17:09 to 17:14 WO# | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | 2014-12-31 | 899 | 949 | 944 | 827 | 48.65 | 3667.65 | 3494.25 | 173.4 | 3623 | 4.717 | 74.86 | Inverter 4 is resolve the issue started 9:05 (Replesh Inverter side D.C,contector) & Grid Failure From 16:47 to 17:48 WO# | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2015
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2015-01-01 | 542 | 560 | 509 | 529 | 22.5 | 2162.5 | 2035.5 | 127 | 2197 | 2.78 | 77.02 | Inverter No- 3 Auto trip 8:50 (modulre fan problem) 9:50 Auto start WO#3381467 & Today I Replaced The D.C.12Amp Fuse Link of The String- 01 --tive in AJB-105 of The Inverter-4 during The Period of 10:25 To 10:30.WO#(3381507) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
1 | 2015-01-02 | 792 | 831 | 842 | 821 | 36.93 | 3322.93 | 3177 | 145.93 | 3352 | 4.15 | 78.72 | Grid Failure From 13:02 to 13:09 WO#3402756 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2015-01-03 | 933 | 978 | 995 | 953 | 49.96 | 3908.96 | 3755.25 | 153.71 | 3942 | 5.303 | 72.45 | Grid Failure From 8:05 to 9:19 WO#3419549 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2015-01-04 | 1046 | 1102 | 1114 | 1071 | 61.29 | 4394.29 | 4210.5 | 183.79 | 4430 |  |  | Grid Failure From 16:45 to 18:45 WO#3450753 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2015-01-05 | 893 | 939 | 944 | 902 | 41.55 | 3719.55 | 3556.5 | 163.05 | 3744 | 4.8 | 76.02 | The GERMI Plant has Failure The GRID From -14:34 to 17:54 (wo#3470232) With high Frequency so our D.O Fuse of 'B' phase blown at 17:54 to 18:40 (WO#3473799) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2015-01-06 | 1040 | 1097 | 1102 | 1065 | 58.77 | 4362.77 | 4194 | 168.77 | 4388 | 5.726 | 74.69 | Today I Replaced The D.C.12Amp Fuse Link of The String- 08 --tive in AJB-105 of The Inverter-4 during The Period of 10:05 To 10:10.WO#(3486775) & Grid Failure From 15:57 to 18:28 WO# |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
6 | 2015-01-07 | 543 | 571 | 577 | 551 | 29.48 | 2271.48 | 2167.5 | 103.98 | 3212 | 3.165 | 71.19 | Grid Failure From 15:57 to 18:28 WO# 3518160 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2015-01-08 | 1051 | 1113 | 1120 | 1077 | 60.24 | 4421.24 | 4242.75 | 178.49 | 4444 | 5.805 | 74.61 | Grid Failure From 17:42 to 18:52 WO# 3545933 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2015-01-09 | 1092 | 1154 | 1159 | 1150 | 66.91 | 4621.91 | 4439.25 | 182.66 | 4647 | 6.106 | 74.17 | Battery water Fileed in 5 kw Battery Bank |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
9 | 2015-01-10 | 1079 | 1130 | 1130 | 1138 | 71.79 | 4548.79 | 4379.25 | 169.54 | 4580 | 6.021 | 74.13 | Grid Failure From 13:48 to 13:57 WO# 3593881 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2015-01-11 | 1091 | 1137 | 1154 | 1122 | 70.17 | 4574.17 | 4389.75 | 184.42 | 4592 | 6.051 | 73.96 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2015-01-12 | 1041 | 1085 | 1124 | 1066 | 66.71 | 4382.71 | 4197 | 185.71 | 4398 | 6.031 | 71.07 | Grid Failure From 14:48 to 15:08 WO#3648062 & 15:26 to 15:44 WO#3648693 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2015-01-13 | 1034 | 1080 | 1126 | 1048 | 60.77 | 4348.77 | 4176.75 | 172.02 | 4401 | 5.773 | 74.3 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2015-01-14 | 786 | 820 | 847 | 772 | 37.51 | 3262.51 | 3114 | 148.51 | 3290 | 4.273 | 75.04 | Cloudy day & Inverer 4 run healthy but exhaust fan faulty |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
14 | 2015-01-15 | 989 | 1023 | 1069 | 966 | 54.31 | 4101.31 | 3912.75 | 188.56 | 4110 | 5.362 | 74.7 | Inverter no-4 run healthy but exhaust fan not working |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2015-01-16 | 1040 | 1102 | 1119 | 1039 | 59.66 | 4359.66 | 4181.25 | 178.41 | 4379 | 5.738 | 74.38 | Grid Failure From 11:05 to 11:08 WO#3758192 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2015-01-17 | 1143 | 1193 | 1204 | 1113 | 66.42 | 4719.42 | 4523.25 | 196.17 | 4725 | 6.169 | 74.69 | Grid Failure From 13:39 to 13:46 WO#3798043 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2015-01-18 | 1192 | 1238 | 1238 | 1153 | 69.02 | 4890.02 | 4687.5 | 202.52 | 4901 | 6.416 | 74.45 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2015-01-19 | 1108 | 1142 | 1154 | 1072 | 63.1 | 4539.1 | 4354.5 | 184.6 | 4548 | 5.922 | 74.85 | Transformer -1 & 4 (P.M) |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2015-01-20 | 950 | 978 | 984 | 904 | 48.11 | 3864.11 | 3708.75 | 155.36 | 3872 | 5.094 | 74.08 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2015-01-21 | 509 | 515 | 520 | 506 | 19.88 | 2069.88 | 1950.75 | 119.13 | 2092 | 2.54 | 80.27 | fully cloudy Day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
21 | 2015-01-22 | 1131 | 1198 | 1215 | 1171 | 59.33 | 4774.33 | 4583 | 191.33 | 4797 | 6.087 | 76.81 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2015-01-23 | 1142 | 1205 | 1227 | 1171 | 69.43 | 4814.43 | 4617.75 | 196.68 | 4824 | 6.101 | 77.06 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-101 of The Inverter-4 during The Period of 10:25 To 10:30.WO#(3984715) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
23 | 2015-01-24 | 1012 | 1063 | 1080 | 1020 | 57.57 | 4232.57 | 4059 | 173.57 | 4271 | 5.268 | 78.97 | Grid supply failure from 13:29 to 13:34(WO#4024145) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2015-01-25 | 622 | 650 | 661 | 618 | 26.01 | 2577.01 | 2443.5 | 133.51 | 2621 | 3.217 | 79.4 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2015-01-26 | 1023 | 1074 | 1097 | 1010 | 52.93 | 4256.93 | 4077.75 | 179.18 | 4292 | 5.451 | 76.74 | Grid supply failure from 17:22 to 17:55 (WO#) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2015-01-27 | 1159 | 1221 | 1238 | 1180 | 66.97 | 4864.97 | 4671.75 | 193.22 | 4875 | 6.162 | 77.1 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2015-01-28 | 1255 | 1334 | 1362 | 1293 | 77.77 | 5321.77 | 5103 | 218.77 | 5320 |  |  | Internet failure |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
28 | 2015-01-29 | 1211 | 1289 | 1312 | 1226 | 74.45 | 5112.45 | 4900.5 | 211.95 | 5102 | 6.498 | 76.52 | Grid supply failure from 12:20 to 12:30 (WO#4194605) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2015-01-30 | 1238 | 1329 | 1334 | 1267 | 76.26 | 5244.26 | 5031 | 213.26 | 5251 | 6.586 | 77.7 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2015-01-31 | 1260 | 1334 | 1340 | 1386 | 76.27 | 5396.27 | 5086.5 | 309.77 | 5308 | 6.783 | 76.27 | Inverter no- 1,2,3,4, filter cleaning |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2015-02-01 | 1148 | 1210 | 1221 | 1153 | 72.39 | 4804.39 | 4611 | 193.39 | 4805 | 6.005 | 77.9889 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2015-02-02 | 1098 | 1153 | 1159 | 1115 | 65.25 | 4590.25 | 4403.25 | 187 | 4609 | 5.983 | 75.08 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2015-02-03 | 735 | 775 | 775 | 766 | 30.54 | 3081.54 | 2947.5 | 134.04 | 3111 | 4.024 | 75.35 | Grid supply failure from 9:55 to 12:38 (WO#4378455) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2015-02-04 | 1227 | 1288 | 1317 | 1273 | 73.57 | 5178.57 | 4968 | 210.57 | 5207 | 6.545 | 77.54 | Module cleaning done Inverter 3 Row N,O,P,Q,R. Total module cleaning 610 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2015-02-05 | 1102 | 1165 | 1204 | 1129 | 63.38 | 4663.38 | 4477.5 | 185.88 | 4683 | 5.798 | 78.72 | Module cleaning done Inverter 2 & 3 Row K,L,M. Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2015-02-06 | 1040 | 1125 | 1131 | 1049 | 60.32 | 4405.32 | 4227.75 | 177.57 | 4425 | 5.684 | 75.87 | Module cleaning done Inverter 2 Row I,J. Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2015-02-07 | 1125 | 1198 | 1198 | 1129 | 66.99 | 4716.99 | 4522.5 | 194.49 | 4730 | 6.103 | 76.49 | Module cleaning done Inverter 2 & 3 Row . Total module cleaning 650 & Grid supply failure from 9:32 to 12:35 (WO#4540622) |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2015-02-08 | 1199 | 1272 | 1278 | 1196 | 72.62 | 5017.62 | 4812.75 | 204.87 | 5023 | 6.407 | 76.41 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2015-02-09 | 1261 | 1323 | 1323 | 1275 | 77.67 | 5259.67 | 5049 | 210.67 | 5267 | 6.666 | 77.01 | Module cleaning done Inverter 1 & 4 Row A,B.& A,B,C,D,E Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2015-02-10 | 1147 | 1199 | 1204 | 1167 | 65.98 | 4782.98 | 4591.5 | 191.48 | 4797 | 6.018 | 77.69 | Module cleaning done Inverter 4 Row .& F,G,H,I, Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2015-02-11 | 1125 | 1187 | 1199 | 1172 | 66.17 | 4749.17 | 4563.75 | 185.42 | 4769 | 6.044 | 76.9 | Module cleaning done Inverter 4 & Trackers, Row .& ,j,k,l, Total module cleaning 640 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2015-02-12 | 1244 | 1317 | 1357 | 1312 | 79.38 | 5309.38 | 5109.75 | 199.63 | 5328 | 6.699 | 77.51 | Module cleaning done Inverter 3 Row ,O,P,Q,R,S,T, Total module cleaning 640 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2015-02-13 | 1219 | 1307 | 1345 | 1287 | 77.68 | 5235.68 | 5032.5 | 203.18 | 5248 | 6.674 | 76.64 | Module cleaning done Inverter 3 & 2 Row ,K,L,M,N, Total module cleaning 645 & Replaced The Demaj module as a 11`nd From Uper Last of The `L` Row,String- 3 JB-110 (OLD Module Sr.no-PB10B068470151) NEW MODULE-PB10B047480118 & 2 Module Replaced Front of the Row no-T string no-1 AJB NO-117 INverter no-3 Damege modulr sr.no-PB10B071470175 NEW Module sr.no-PB10B068470104 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2015-02-14 | 1161 | 1249 | 1272 | 1208 | 72.81 | 4962.81 | 4760.25 | 202.56 | 4969 | 6.383 | 75.87 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2015-02-15 | 1119 | 1198 | 1221 | 1169 | 69.15 | 4776.15 | 4593 | 183.15 | 4791 | 6.186 | 75.48 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2015-02-16 | 1199 | 1312 | 1312 | 1267 | 75.22 | 5165.22 | 4971 | 194.22 | 5207 | 6.606 | 76.82 | Module cleaning done Inverter 2 Row ,I,J Total module cleaning 604 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2015-02-17 | 1210 | 1323 | 1317 | 1260 | 76.37 | 5186.37 | 4988.25 | 198.12 | 5197 | 6.613 | 76.59 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2015-02-18 | 1102 | 1181 | 1176 | 1111 | 64.29 | 4634.29 | 4456.5 | 177.79 | 4652 | 6 | 75.56 | Grid supply failure from 16:14 to 16:19 (WO#5113888) & Module cleaning done Inverter 2 & 1, Row ,E,F,G,H, Total module cleaning 630 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2015-02-19 | 1125 | 1165 | 1159 | 1085 | 63.91 | 4597.91 | 4413.75 | 184.16 | 4634 | 5.931 | 76.15 | Module cleaning done Inverter -1 & 4 Row ,A,B,C,D,Inverter -No-4 Row- A,B,C, Total module cleaning 640 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2015-02-20 | 1153 | 1199 | 1187 | 1170 | 65.8 | 4774.8 | 4594.5 | 180.3 | 4800 | 6.22 | 75.21 | Module cleaning done Inverter -4 Row -D,E,F,G, Total module cleaning 652 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2015-02-21 | 1142 | 1181 | 1176 | 1205 | 67.7 | 4771.7 | 4587.75 | 183.95 | 4811 | 6.379 | 73.5 | Grid Failure From - 13:10 to 13:13 (WO#5285421) & Module cleaning done Inverter-4 Row H,I,J, Total module cleaning 630 & Plant shutdown due to replace isolator switch (G.O.D) @ 17:18 to 2:25 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
53 | 2015-02-22 | 864 | 933 | 921 | 937 | 43.45 | 3698.45 | 3587.25 | 111.2 | 3721 |  |  | Our side Grid Failure due to R' Y' B', D.O, fuse Blown & 'B' Phase L.A, Failure @9:21 to 11:35 WO#5340473 & seeds P.M |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2015-02-23 | 1147 | 1193 | 1222 | 1209 | 66.41 | 4837.41 | 4649.25 | 188.16 | 4855 | 6.286 | 75.27 | Module cleaning done Inverter -4 Row -K,L, & Trackers & Inverter-3 ROW- R,S,T, Total module cleaning 650 & Combiner P.M, |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2015-02-24 | 973 | 1017 | 1068 | 1002 | 54.34 | 4114.34 | 3954.75 | 159.59 | 4163 | 5.179 | 78.34 | Module cleaning done Inverter-3 ROW- N,O,P,Q, Total module cleaning 645 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2015-02-25 | 1204 | 1306 | 1334 | 1260 | 74.06 | 5178.06 | 4966.5 | 211.56 | 5177 | 6.275 | 8041 | Module cleaning done Inverter-3 &2 ROW- J,K,L,M, Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2015-02-26 | 1312 | 1436 | 1431 | 1345 | 85.14 | 5609.14 | 5393.25 | 215.89 | 5605 | 6.926 | 78.87 | Module cleaning done Inverter- 2 & 1 ROW- G,H,I, Total module cleaning 660 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2015-02-27 | 1277 | 1352 | 1334 | 1267 | 78.11 | 5308.11 | 5097.75 | 210.36 | 5340 | 6.89 | 75.53 | Module cleaning done Inverter- 1 ROW- A,B,C,D,E,F, Total module cleaning 670 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2015-02-28 | 1035 | 1073 | 1074 | 1002 | 56.6 | 4240.6 | 4071.75 | 168.85 | 4267 | 5.59 | 74.39 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 --tive in AJB-102 of The Inverter-4 during The Period of 15:10 To 15:15.WO#(5732232) & Module cleaning done Inverter- 4 ROW- A,B,C,D,E, Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
61 | 2015-03-01 | 639 | 673 | 673 | 667 | 31.64 | 2683.64 | 2541 | 142.64 | 2706 | 3.361 | 78.47 | Grid Failure From - 12:02 to 12:07 (WO#5787456) & Fully Cloudy Day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
62 | 2015-03-02 | 1153 | 1221 | 1227 | 1206 | 63.95 | 4870.95 | 4676.25 | 194.7 | 4873 | 6.049 | 78.51 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07 --tive in AJB-108 of The Inverter-2 during The Period of 10:05 To 10:10.WO#(5847185) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
63 | 2015-03-03 | 1046 | 1114 | 1108 | 1092 | 62.6 | 4422.6 | 4241.25 | 181.35 | 4430 | 5.622 | 76.8 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03 --tive in AJB-102 of The Inverter-4 during The Period of 15:10 To 15:15.WO#(5914038) & Grid Failure From - 17:20 to 17:32 (WO#5982141) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
64 | 2015-03-04 | 1277 | 1357 | 1345 | 1375 | 80.68 | 5434.68 | 5217.75 | 216.93 | 5441 | 6.891 | 76.95 | Grid supply failure from 15:10 to 15:15 (WO#6007340) & Module cleaning done Inverter 4 Row ,A,B,C,D,E, Total module cleaning 650 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2015-03-05 | 1221 | 1300 | 1283 | 1302 | 74.51 | 5180.51 | 4977.75 | 202.76 | 5231 | 6.734 | 75.71 | Module cleaning done Inverter 4 Row ,F,G,H,I, Total module cleaning 660 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2015-03-06 | 1210 | 1284 | 1278 | 1301 | 73.53 | 5146.53 | 4943.25 | 203.28 | 5193 | 6.682 | 75.74 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2015-03-07 | 1086 | 1153 | 1165 | 1166 | 63.68 | 4633.68 | 4435.5 | 198.18 | 4671 | 6.051 | 75.23 | Module cleaning done Inverter 4 Row ,J,K,L, & Trackers Total module cleaning 660 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2015-03-08 | 1221 | 1306 | 1323 | 1340 | 79.43 | 5269.43 | 5061 | 208.43 | 5322 | 6.96 | 74.52 | Grid supply failure from 16:58 to 17:15 (WO#6308762) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2015-03-09 | 1306 | 1396 | 1430 | 1382 | 81.91 | 5595.91 | 5379 | 216.91 | 5603 | 7.172 | 76.14 | Module cleaning done Inverter 3 Row O,P,Q,R,S,T, Total module cleaning 660 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2015-03-10 | 1153 | 1250 | 1244 | 1211 | 66.54 | 4924.54 | 4725.75 | 198.79 | 4934 | 6.29 | 76.45 | Grid supply Failure From - 9:45 to 9:47 & 9:59 to 10:11 & 10:48 to 11:00 & 11:33 to 11:36 & 12:22 to 12:25. Module cleaning done Inverter 2 & 3 Row L,M,N, Total module cleaning 670 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2015-03-11 | 1137 | 1232 | 1221 | 1184 | 63.96 | 4837.96 | 4653.75 | 184.21 | 4851 | 6.293 | 75.13 | Module cleaning done Inverter 2 Row H,I,J,K, Total module cleaning 665 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2015-03-12 | 1017 | 1080 | 1063 | 1011 | 50.99 | 4221.99 | 4044 | 177.99 | 4236 | 5.623 | 73.42 | Module cleaning done Inverter -1 Row D,E,F,G, Total module cleaning 650 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2015-03-13 | 933 | 984 | 978 | 962 | 45.58 | 3902.58 | 3732.75 | 169.83 | 3945 | 5.085 | 75.61 | Module cleaning done Inverter 1 & 4 Row A,B,C,& A,B,C, Total module cleaning 665 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2015-03-14 | 984 | 1034 | 1034 | 988 | 48.18 | 4088.18 | 3912.75 | 175.43 | 4124 | 5.318 | 75.58 | Grid supply failure from 13:40 to 13:47 (WO#6689811) & Module cleaning done Inverter- 4 Row -D,E,F,G, Total module cleaning 660 |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2015-03-15 | 1221 | 1300 | 1295 | 1157 | 65.12 | 5038.12 | 4847.25 | 190.87 | 5084 | 6.704 | 73.91 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 --tive in AJB-105 of The Inverter-4 during The Period of 16:10 To 16:15.WO#(6754787) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
76 | 2015-03-16 | 1351 | 1448 | 1441 | 1412 | 77.5 | 5729.5 | 5504.25 | 225.25 | 5727 | 7.375 | 75.68 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 --tive in AJB-105 of The Inverter-4 during The Period of 10:15 To 10:20.WO#(6812097) | 6812097 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
77 | 2015-03-17 | 1345 | 1436 | 1431 | 1441 | 78.4 | 5731.4 | 5505.75 | 225.65 | 5760 | 7.287 | 77.04 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2015-03-18 | 1380 | 1475 | 1475 | 1474 | 80.42 | 5884.42 | 5661 | 223.42 | 5918 | 7.515 | 76.75 | Module cleaning done Inverter-3 Row P,Q,R,S,T, Total module cleaning 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2015-03-19 | 1323 | 1425 | 1419 | 1408 | 77.55 | 5652.55 | 5451 | 201.55 | 5701 | 7.45 | 75.58 | Module cleaning done Inverter-3 & 2 Row L,M,N,O, Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2015-03-20 | 1289 | 1391 | 1369 | 1382 | 73.98 | 5504.98 | 5292 | 212.98 | 5538 | 7.291 | 74.03 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-101 of The Inverter-4 during The Period of 12:20 To 12:25.WO#(7104864) & Grid supply failure from 8:07 to 8:13 (WO#7098699) & Module cleaning done Inverter- 4 Row -H,I,J,K, Total module cleaning- 650 | 7098699 7104864 | 650 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
81 | 2015-03-21 | 1130 | 1198 | 1159 | 1213 | 56.1 | 4756.1 | 4575 | 181.1 | 4801 | 7.105 | 65.85 | Grid failure from - early morning to 9:26. Module cleaning done Inverter-1 Row D,E,F,G,Total module cleaning 650 | 7165762 | 650 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2015-03-22 | 1222 | 1295 | 1272 | 1303 | 61.11 | 5153.11 | 4953 | 200.11 | 5186 | 6.875 | 73.52 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2015-03-23 | 1238 | 1317 | 1294 | 1292 | 62.83 | 5203.83 | 5006.25 | 197.58 | 5242 | 7.116 | 71.79 | Module cleaning done Inverter-1 & 4 Row A,B,C,& A,B,C, Total module cleaning 640 & Inverter No-4 AJB No- 104 MCB Trip 12:40 to 14:02 WO#7318204 | 7318204 | 640 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2015-03-24 | 1255 | 1334 | 1317 | 1396 | 64.21 | 5366.21 | 5168.25 | 197.96 | 5385 | 7.155 | 73.35 | Module cleaning done Inverter-4 Row D,E,F,G, Total module cleaning 660 |  | 660 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2015-03-25 | 1164 | 1227 | 1233 | 1288 | 58.06 | 4970.06 | 4787.25 | 182.81 | 5014 | 6.696 | 72.98 | Module cleaning done Inverter-4 Row H,I,J,K,L, & Tracker Total module cleaning 720 |  | 720 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2015-03-26 | 978 | 1035 | 1074 | 1062 | 44.13 | 4193.13 | 4023.75 | 169.38 | 4217 | 5.582 | 73.63 | Today I Replaced The D.C.12Amp Fuse Link of The String- 02 --tive in AJB-116 of The Inverter-3 during The Period of 10:35 To 10:40.WO#(7506678) & Module cleaning done Inverter- 3 ROW- ,P,Q,R,S,T, Total module cleaning 630 | 7506678 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
87 | 2015-03-27 | 990 | 1079 | 1091 | 1058 | 47.59 | 4265.59 | 4097.25 | 168.34 | 4291 | 5.613 | 74.51 | Module cleaning done Inverter-3 & 2 Row L,M,N,O, & Total module cleaning 660 |  | 660 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2015-03-28 | 1108 | 1199 | 1199 | 1182 | 53.72 | 4741.72 | 4569.75 | 171.97 | 4756 | 6.255 | 74.1 | Module cleaning done Inverter-1 & 2 Row ,H,I,J,K, & Total module cleaning 670 |  | 670 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2015-03-29 | 599 | 627 | 627 | 599 | 22.46 | 2474.46 | 2353.5 | 120.96 | 2512 | 3.007 | 81.42 | Grid supply failure from 16:51 to 18:02 (WO#7717067) | 7717067 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2015-03-30 | 1323 | 1369 | 1402 | 1411 | 60.95 | 5565.95 | 5362.5 | 203.45 | 5613 | 7.373 | 74.19 | Module cleaning done Inverter-1 Row ,A,B,C,D,E,F,G, & Total module cleaning 685 |  | 685 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2015-03-31 | 1306 | 1373 | 1374 | 1411 | 60.49 | 5524.49 | 5325.75 | 198.74 | 5536 | 7.335 | 73.56 | Module cleaning done Inverter-4 Row ,A,B,C,D,E, & Total module cleaning 630 & Today I Replaced The D.C.12Amp Fuse Link of The String- 01 --tive in AJB-106 of The Inverter-2 during The Period of 10:35 To 10:40.WO#(7849439) & Replace the silica gel | 7849439 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
93 | 2015-04-01 | 1232 | 1295 | 1294 | 1337 | 57.1 | 5215.1 | 5001.75 | 213.35 |  |  |  | Module cleaning done Inverter-4 Row ,F,G,H,I, & Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2015-04-02 | 1187 | 1249 | 1250 | 1324 | 53.11 | 5063.11 | 4883.25 | 179.86 |  |  |  | Module cleaning done Inverter-4 Row ,J,K,L, & Trackers Total module cleaning 610 |  | 610 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2015-04-03 | 1278 | 1346 | 1391 | 1433 | 61.73 | 5509.73 | 5315.25 | 194.48 | 5558 | 7.148 | 75.78 | Module cleaning done Inverter-3 Row P,Q,R,S,T & Total module cleaning 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2015-04-04 | 848 | 882 | 938 | 893 | 37.29 | 3598.29 | 3458.25 | 140.04 | 3628 | 4.589 | 77.05 | Module cleaning done Inverter-2 & 3 Row L,M,N,O & Total module cleaning 660. & Grid supply failure from 18:12 to 18:30 (WO#8175587) & couldy day | 817587 | 660 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2015-04-05 | 978 | 1034 | 1091 | 1049 | 48.29 | 4200.29 | 4029.75 | 170.54 | 4237 | 5.48 | 75.35 | Grid supply failure from - 9:06 to 9:12 & couldy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2015-04-06 | 1023 | 1109 | 1137 | 1103 | 54.15 | 4426.15 | 4233 | 193.15 | 4434 | 5.7 | 75.81 | Module cleaning done Inverter-2 Row ,H,I,J,K,& Total module cleaning 670. & Grid supply failure from 10:02 to 10:22 (WO#8286657) | 8286657 | 670 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2015-04-07 | 1075 | 1187 | 1175 | 1170 | 58.04 | 4665.04 | 4501.5 | 163.54 | 4705 |  |  | Module cleaning done Inverter-2 &1 Row E,F,G, & Total module cleaning 620 |  | 620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2015-04-08 | 1063 | 1142 | 1125 | 1108 | 54.36 | 4492.36 | 4311 | 181.36 | 4515 |  |  | Module cleaning done Inverter-1 Row ,A,B,C,D & Total module cleaning 590 |  | 590 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2015-04-09 | 1209 | 1266 | 1256 | 1257 | 66.75 | 5054.75 | 4861.5 | 193.25 | 5229 |  |  | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2015-04-10 | 1074 | 1108 | 1102 | 1107 | 54.42 | 4445.42 | 4276.5 | 168.92 | 4602 |  |  | Module cleaning done Inverter-4 Row ,A,B,C,D, & Total module cleaning 580 |  | 580 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2015-04-11 | 1001 | 1063 | 1063 | 1105 | 51.39 | 4283.39 | 4117.5 | 165.89 | 4374 | 5.664 | 75.26 | Module cleaning done Inverter-4 Row ,E,F,G,H, & Total module cleaning 650 & Rain |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2015-04-12 | 990 | 1069 | 1085 | 1078 | 81.28 | 4303.28 | 4032 | 271.28 | 4269 | 5.527 | 75.28 | Grid supply failure From 9:45 to 9:49 & 16:03 to 16:09 (WO#8750195) (WO#8816841) | 8750195 8816841 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2015-04-13 | 1175 | 1283 | 1306 | 1332 | 66.44 | 5162.44 | 4997.25 | 165.19 | 5151 | 6.605 | 76.01 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2015-04-14 | 1199 | 1328 | 1351 | 1387 | 70.66 | 5335.66 | 5152.5 | 183.16 | 5387 | 6.933 | 75.73 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2015-04-15 | 1199 | 1329 | 1346 | 1368 | 72.83 | 5314.83 | 5128.5 | 186.33 | 5358 | 6.899 | 75.69 | L.T PANEL P.M |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2015-04-16 | 1170 | 1295 | 1311 | 1355 | 72.03 | 5203.03 | 5014.5 | 188.53 | 5250 | 6.898 | 74.18 | Module cleaning done Inverter-4 Row ,A,B,C,D,E,& Total module cleaning 630. & Grid supply failure from 13:17 to 13:24 (WO#9086294) | 9086294 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2015-04-17 | 1130 | 1254 | 1278 | 1321 | 67.26 | 5050.26 | 4869.7 | 180.56 | 5085 | 6.719 | 73.76 | Module cleaning done Inverter-4 Row ,F,G,H,I, & Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2015-04-18 | 1148 | 1272 | 1290 | 1356 | 63.62 | 5129.62 | 4934.25 | 195.37 | 5182 | 6.814 | 74.12 | Module cleaning done Inverter-4 Row ,J,K,L, & Total module cleaning 660 |  | 660 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2015-04-19 | 1159 | 1289 | 1328 | 1375 | 68.45 | 5219.45 | 5011.5 | 207.95 | 5217 | 6.911 | 73.57 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2015-04-20 | 1204 | 1306 | 1368 | 1385 | 69.55 | 5332.55 | 5134.5 | 198.05 | 5340 | 6.908 | 75.34 | Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 09++tive in AJB-104 of The Inverter-1 & 09--tive AJB-105 during The Period of 10:15 To 10:25.WO#(9402652) & Module cleaning done Inverter-3 Row ,P,Q,R,S,T, & Total module cleaning 620 | 9402652 | 620 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
113 | 2015-04-21 | 1125 | 1222 | 1260 | 1262 | 61.65 | 4930.65 | 4764.75 | 165.9 | 4981 | 6.461 | 75.13 | Module cleaning done Inverter-3 &2 Row ,L,M,N,O, & Total module cleaning 690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2015-04-22 | 1199 | 1323 | 1340 | 1350 | 67.97 | 5279.97 | 5074.5 | 205.47 | 5287 | 6.804 | 75.73 | Module cleaning done Inverter-2 Row ,H,I,J,K, & Total module cleaning 710 |  | 710 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2015-04-23 | 1255 | 1362 | 1374 | 1388 | 72.53 | 5451.53 | 5249.25 | 202.28 | 5457 | 7.071 | 75.21 | Module cleaning done Inverter-2 & 1 Row ,D,E,F,G, & Total module cleaning 680 |  | 680 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2015-04-24 | 1243 | 1311 | 1329 | 1354 | 69.73 | 5306.73 | 5115 | 191.73 | 5318 | 6.809 | 76.12 | Module cleaning done Inverter-1 & 4 Row ,A,B,C, & ,A,B,C, & Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2015-04-25 | 1216 | 1278 | 1289 | 1325 | 64.76 | 5172.76 | 4985.25 | 187.51 | 5186 | 6.684 | 75.62 | Module cleaning done Inverter-4 Row-,D,E,F,G, & Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2015-04-26 | 1182 | 1250 | 1260 | 1305 | 64.53 | 5061.53 | 4879.5 | 182.03 | 5079 | 6.625 | 74.72 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2015-04-27 | 1192 | 1249 | 1261 | 1329 | 66.38 | 5097.38 | 4912.5 | 184.88 | 5145 | 6.705 | 74.78 | Module cleaning done Inverter-4 Row-,H,I,J,K, & Total module cleaning 660 |  | 660 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2015-04-28 | 1199 | 1266 | 1272 | 1359 | 65.69 | 5161.69 | 4972.5 | 189.19 | 5177 | 6.695 | 75.36 | Module cleaning done Inverter-4 & 3 Row-,L, -R,S,T,& Tracker & Total module cleaning 620 & Control Building P.M & Inverter P.M (1&2) |  | 620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2015-04-29 | 1164 | 1233 | 1267 | 1315 | 66.15 | 5045.15 | 4860 | 185.15 |  |  |  | Module cleaning done Inverter-3 Row- N,O,P,Q, & Total module cleaning 630 & C.R Panel P.M & Inverter P.M (3&4) & Internet Failure (POE POWER ADAPTER FAILURE)14:45 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
122 | 2015-04-30 | 1182 | 1249 | 1334 | 1345 | 69.77 | 5179.77 | 4989.75 | 190.02 |  |  |  | Module cleaning done Inverter-3 & 2 Row- J,K,L,M & Total module cleaning 680 |  | 680 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2015-05-01 | 1098 | 1188 | 1233 | 1236 | 61.55 | 4816.55 | 4656.75 | 159.8 |  |  |  | Grid supply failure from 14:59 to 15:15 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2015-05-02 | 1124 | 1243 | 1271 | 1251 | 64.5 | 4953.5 | 4764 | 189.5 |  |  |  | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2015-05-03 | 1165 | 1283 | 1317 | 1316 | 70.08 | 5151.08 | 4948.5 | 202.58 |  |  |  | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2015-05-04 | 1204 | 1346 | 1346 | 1345 | 71.88 | 5312.88 | 5091 | 221.88 |  |  |  | Module cleaning done Inverter-1 & 2 Row- G,H,I, & Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2015-05-05 | 1215 | 1295 | 1295 | 1298 | 70.55 | 5173.55 | 4989 | 184.55 |  |  |  | Module cleaning done Inverter-1 Row- ,C,D,E,F, & Total module cleaning 660 |  | 660 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2015-05-06 | 1216 | 1283 | 1277 | 1305 | 68.76 | 5149.76 | 4954.5 | 195.26 |  |  |  | Module cleaning done Inverter-1 & 4 Row- ,A,B &,A,B,C,D, & Total module cleaning 670 |  | 670 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2015-05-07 | 1215 | 1278 | 1278 | 1344 | 67.67 | 5182.67 | 4985.25 | 197.42 |  |  |  | Module cleaning done Inverter-4 Row- ,E,F,G,H, & Total module cleaning 690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2015-05-08 | 1046 | 1091 | 1091 | 1154 | 51.67 | 4433.67 | 4260 | 173.67 |  |  |  | Module cleaning done Inverter-4 Row- ,I,J,K,L, & Total module cleaning 670 |  | 670 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2015-05-09 | 1204 | 1266 | 1300 | 1379 | 71.97 | 5220.97 | 5037.75 | 183.22 |  |  |  | Module cleaning done Inverter-3 & Trackers Row- ,Q,R,S,T, & Total module cleaning 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2015-05-10 | 1193 | 1255 | 1295 | 1364 | 71.89 | 5178.89 | 4984.5 | 194.39 |  |  |  | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2015-05-11 | 1148 | 1210 | 1273 | 1327 | 68.18 | 5026.18 | 4839 | 187.18 |  |  |  | Module cleaning done Inverter-3 & Row- ,M,N,O,P, & Total module cleaning 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2015-05-12 | 1130 | 1198 | 1085 | 1297 | 65.11 | 4775.11 | 4600.5 | 174.61 |  |  |  | Inverter#3 did not wake up due to auto reset indication so reset it at 9:35am and started the inverter. & Module cleaning done Inverter-3 & 2 Row- ,J,K,L, & Total module cleaning 680 | WO#11388926 | 680 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2015-05-13 | 877 | 973 | 984 | 998 | 48.71 | 3880.71 | 3741 | 139.71 |  |  |  | 5 KV UPS System D.C, Volt Low so Bypass the system plant Trip 15:15 to 16:10 WO# & Module cleaning done Inverter-2 & Row- ,G,H,I, & Total module cleaning 650 & Cloud and Rain |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2015-05-14 | 785 | 831 | 848 | 858 | 42.33 | 3364.33 | 3271.5 | 92.83 |  |  |  | Night time 11KV Grid Failure so our plant VCB Trip plant started 9:05 & Two Time Grid Failure From-10:58 to 11:21 & 14:25 to 14:35 & Module cleaning done Inverter-1 Row- ,D,E,F, & Total module cleaning 640 & Cloud and Rain |  | 640 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2015-05-15 | 1171 | 1249 | 1272 | 1100 | 70.46 | 4862.46 | 4687.5 | 174.96 |  |  |  | Grid Failure From -11:09 to 11:16 WO# & Module cleaning done Inverter-1 Row- ,A,B,C, & Total module cleaning 350 |  | 350 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2015-05-16 | 1232 | 1301 | 1334 | 1340 | 69.15 | 5276.15 | 5082.75 | 193.4 |  |  |  | Today I Replaced The D.C.12Amp Fuse Link of The String- 04 ++tive in AJB-104 of The Inverter-4 during The Period of 19:35 To 9:40.WO#() & Module cleaning done Inverter- 4 ROW- ,A,B,C,D,E, Total module cleaning 600 |  | 600 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
140 | 2015-05-17 | 1232 | 1317 | 1340 | 1395 | 69.86 | 5353.86 | 5155.5 | 198.36 |  |  |  | Array P.M |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2015-05-18 | 1205 | 1283 | 1301 | 1377 | 71.37 | 5237.37 | 5038.5 | 198.87 |  |  |  | Module cleaning done Inverter-4 Row- ,F,G,H, & Total module cleaning 600 |  | 600 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2015-05-19 | 1187 | 1295 | 1300 | 1382 | 69.57 | 5233.57 | 5041.5 | 192.07 |  |  |  | Module cleaning done Inverter-4 Row- ,I,J,K,L, & Total module cleaning 670 & Grid Failure From -16:15 to 16:23 WO# & Combiner P.M (AJB-100 to 117 -Crystallin side 750 KW ) |  | 670 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2015-05-20 | 1204 | 1306 | 1306 | 1405 | 73.69 | 5294.69 | 5099.25 | 195.44 |  |  |  | Module cleaning done Inverter-3 & Trackers Row- ,P,Q,R,S,T, & Total module cleaning 650 & Combiner P.M (AJB-100 to 105 -Thinfilm side 250 KW ) |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2015-05-21 | 1154 | 1261 | 1300 | 1347 | 70.45 | 5132.45 | 4947 | 185.45 | 5149 |  |  | Module cleaning done Inverter-3 & 2 Row- ,L,M,N,O, & Total module cleaning 680 & Seeds P.M |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2015-05-22 | 1170 | 1305 | 1317 | 1356 | 72.4 | 5220.4 | 5025.75 | 194.65 | 5282 |  |  | Module cleaning done Inverter- 2 Row- ,I,J,K, & Total module cleaning 710 |  | 710 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2015-05-23 | 1136 | 1284 | 1272 | 1302 | 68.58 | 5062.58 | 4887 | 175.58 | 5086 | 6.521 | 76.01 | Module cleaning done Inverter-2 & 1 Row- ,F,G,H, & Total module cleaning 650 & Grid Failure From -08:07 to 08:15 WO#12532233 | 12532233 | 650 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2015-05-24 | 1125 | 1249 | 1238 | 1275 | 64 | 4951 | 4769.25 | 181.75 | 4992 | 6.427 | 75.7 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2015-05-25 | 1103 | 1210 | 1199 | 1242 | 56.27 | 4810.27 | 4664.5 | 145.77 | 4840 | 6.495 | 72.63 | Module cleaning done Inverter- 1 Row- C,D,E, & Total module cleaning 600 & Grid Failure From -07:20 to 08:05 WO#12736715 | 12736715 | 600 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2015-05-26 | 1136 | 1221 | 1215 | 1256 | 57.6 | 4885.6 | 4695 | 190.6 | 4915 | 6.432 | 74.47 | Module cleaning done Inverter- 1 & 4 Row- ,A,B, & A,B,C,D, & Total module cleaning- 610 |  | 610 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2015-05-27 | 1125 | 1210 | 1204 | 1273 | 56.94 | 4868.94 | 4692 | 176.94 | 4892 | 6.428 | 74.17 | Module cleaning done Inverter- 4 Row- ,E,F,G, & Total module cleaning- 560 |  | 560 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2015-05-28 | 1119 | 1210 | 1205 | 1297 | 57.01 | 4888.01 | 4706.25 | 181.76 | 4906 | 6.458 | 74.04 | Module cleaning done Inverter- 4 Row- ,H,I,J, & Total module cleaning- 596 |  | 596 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2015-05-29 | 1142 | 1238 | 1238 | 1340 | 64.66 | 5022.66 | 4850.25 | 172.41 | 5075 | 6.649 | 74.39 | Module cleaning done Inverter- 4 & 3 & Trackers Row- ,K,L,& R,S,T, & Total module cleaning 660 & Grid Failure From -12:52 to 12:57 WO#13149762 & Tracker P.M | 13149762 | 660 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2015-05-30 | 1148 | 1238 | 1278 | 1336 | 67.14 | 5067.14 | 4875.75 | 191.39 | 5088 | 6.727 | 73.71 | Module cleaning done Inverter- 3 Row- ,N,O,P,Q, & Total module cleaning- 660 |  | 660 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2015-05-31 | 1108 | 1193 | 1243 | 1284 | 50.45 | 4878.45 | 4718.25 | 160.2 | 4903 | 6.76 | 70.69 | Grid failure from night time so our plant side V.C.B. trip Morning 8:00a.m on V.C.B. plant started 8:00a.m.WO#13316368 | 13316368 | 610 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2015-06-01 | 1108 | 1198 | 1255 | 1285 | 58.15 | 4904.15 | 4728.75 | 175.4 | 4951 | 6.549 | 73.68 | Module cleaning done Inverter- 2 Row- ,H,I,J, & Total module cleaning- 670 |  | 670 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2015-06-02 | 1006 | 1120 | 1136 | 1145 | 52.89 | 4459.89 | 4286.25 | 173.64 | 4499 | 4.53 | 96.79 | Module cleaning done Inverter- 2 Row- ,H,I,J, & Total module cleaning- 670 |  | 670 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2015-06-03 | 961 | 1051 | 1046 | 1088 | 26.49 | 4172.49 | 4040.25 | 132.24 | 4243 | 5.546 | 74.56 | Module cleaning done Inverter- 1 Row- E,F,G, & Total module cleaning 580 & Grid Failure From -12:55 to 13:05 WO# & Trackers 4 S.Q. m.m. 4 core cable B Phase Ground folt (Tracker Inverter no-3 S.M.A. power supply failure) | 14331961 13587960 | 580 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2015-06-04 | 950 | 1012 | 1007 | 1013 | 19.57 | 4001.57 | 3864.75 | 136.82 | 4064 | 5.63 | 70.35 | Module cleaning done Inverter- 1 Row- A,B,C,D, 550 & Total module cleaning 550 & Grid Failure From -08:20 to 08:45 WO#13640469 | 13640469 | 550 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2015-06-05 | 1069 | 1119 | 1108 | 1129 | 22.58 | 4447.58 | 4283.25 | 164.33 | 4488 | 6.185 | 70.72 | Module cleaning done Inverter- 4 Row- ,A,B,C,D,E, & Total module cleaning- 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2015-06-06 | 1130 | 1193 | 1187 | 1253 | 22.95 | 4785.95 | 4619.25 | 166.7 | 4831 | 6.494 | 72.5 | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning- 594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2015-06-07 | 1057 | 1131 | 1125 | 1206 | 22.27 | 4541.27 | 4377.75 | 163.52 | 4596 | 6.273 | 71.4 | Grid Failure From -17:48 to 17:55 WO# & Inverter no-1 ABB, From- 17:55 inverter not started (sleep mode) |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2015-06-08 | 374 | 402 | 401 | 412 | 6.37 | 1595.37 | 1486.5 | 108.87 | 1626 | 2.083 | 76.08 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Total module cleaning- 650 |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2015-06-09 | 808 | 865 | 871 | 945 | 17.2 | 3506.2 | 3370.5 | 135.7 | 3559 | 4.714 | 73.58 | Module cleaning done Inverter- 3 Row- ,P,Q,R,S,T, & Total module cleaning- 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2015-06-10 | 475 | 695 | 729 | 821 | 17.96 | 2737.96 | 2676.75 | 61.21 | 2853 | 4.949 | 56.18 | Today Eight time Grid failure-8:00 to 8:50 , 12:32 to 12:42, 14:50 to 14:55, 15:20 to 15:26 , 15:50 to 15:55, 16:46 to 16:50, 17:15 to 17:19, 17:31 to 17:59 & Inverter no-1,2,3, Emergency stop reset Inverter started 9:10 & Inverter no-1 Grid folt Err code NONFOLT(8189 A.C. VOLT LOW) 15:20 TO 16:20 | WO#14227355 WO#14238706 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2015-06-11 | 729 | 786 | 809 | 833 | 14.4 | 3171.4 | 3025.5 | 145.9 | 3219 | 4.037 | 77.71 | Module cleaning done Inverter- 3 Row- ,L,M,N,O, 670 & Total module cleaning 670 & Grid Failure From -12:58 to 13:06 WO# |  | 670 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2015-06-12 | 1041 | 1136 | 1130 | 1200 | 21.1 | 4528.1 | 4404 | 124.1 | 4559 | 5.874 | 75.64 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2015-06-13 | 1023 | 1114 | 1120 | 1174 | 21.32 | 4452.32 | 4363.5 | 88.82 | 4504 | 5.711 | 76.86 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 2015-06-14 | 1012 | 1096 | 1085 | 1163 | 21.18 | 4377.18 | 4134.75 | 242.43 | 4411 | 5.692 | 75.53 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 2015-06-15 | 944 | 1035 | 1023 | 1084 | 21.1 | 4107.1 | 3939 | 168.1 | 4160 | 5.492 | 73.82 | Module cleaning done Inverter- 3 Row- ,P,Q,R,S,T, & Total module cleaning 650 & Grid Failure From -12:01 to 12:07 WO# |  | 650 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2015-06-16 | 927 | 1001 | 984 | 1054 | 21.08 | 3987.08 | 3840 | 147.08 | 4037 | 5.227 | 75.27 | Module cleaning done Inverter- 3 Row- ,L,M,N,O, & Total module cleaning- 670 |  | 670 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 2015-06-17 | 851 | 904 | 894 | 942 | 18.64 | 3609.64 | 3479.25 | 130.39 | 3671 | 4.908 | 72.9 | Module cleaning done Inverter- 1 & 2 Row- ,G,H,I,J,K, & Total module cleaning 900 & Grid Failure From -07:40 to 08:00 & 10:24 to 10:39 WO# | 14626095 | 900 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 2015-06-18 | 924 | 984 | 972 | 1020 | 19.95 | 3919.95 | 3787.5 | 132.45 | 3972 | 5.165 | 74.95 | Module cleaning done Inverter- 1 Row- ,A,B,C,D,E, & Total module cleaning 950 & Grid Failure From -12:10 to 12:15 WO#14683274 | 14683274 | 950 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 2015-06-19 | 718 | 757 | 757 | 775 | 14.53 | 3021.53 | 2890.5 | 131.03 | 3071 | 3.884 | 77.06 | Module cleaning done Inverter- 4 Row- ,A,B,C,D,E, & Total module cleaning- 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 2015-06-20 | 1007 | 1080 | 1069 | 1161 | 21.7 | 4338.7 | 4174.5 | 164.2 | 4370 | 5.65 | 75.38 | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning- 594 |  | 564 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2015-06-21 | 955 | 1025 | 1018 | 1119 | 15.77 | 4132.77 | 3978 | 154.77 | 4186 | 5.453 | 74.81 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2015-06-22 | 661 | 700 | 712 | 749 | 14.09 | 2836.09 | 2725.5 | 110.59 | 2887 | 3.588 | 78.42 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Trackers & Total module cleaning 750 & Grid Failure From -08:13 to 08:22 WO#14882219 & cloudy day | 14882219 | 750 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
178 | 2015-06-23 | 515 | 554 | 565 | 555 | 10.24 | 2199.24 | 2083.5 | 115.74 | 2239 | 2.71 | 80.52 | Module cleaning done Inverter- 3 Row- ,P,Q,R,S,T, & Total module cleaning- 650 & cloudy day |  | 650 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
179 | 2015-06-24 | 186 | 203 | 198 | 197 | 3.44 | 787.44 | 699 | 88.44 | 842 | 998 | 82.23 | Grid Failure From- 15:08 to 16:05 Inverters note started sleep mode because D.C.Valltege low heavy rain & Grid Failure From- 17:13 to 17:39 | 14998049 14997953 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2015-06-25 | 865 | 939 | 944 | 952 | 19.67 | 3719.67 | 3575.25 | 144.42 | 3792 | 4.759 | 77.66 | Grid Failure From- 14:22 to 14:30 WO#15038762 | 15038762 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2015-06-26 | 973 | 1051 | 1052 | 1077 | 20.81 | 4173.81 | 4017.75 | 156.06 | 4212 | 5.35 | 76.73 | Grid Failure From- 07:54 to 8:02 WO#1508660 | 15086600 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2015-06-27 | 938 | 1006 | 1006 | 1035 | 20.5 | 4005.5 | 3858 | 147.5 | 4057 | 5.192 | 76.15 | Grid Failure From- 15:00 to 15:20 WO#15158620 | 15158620 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2015-06-28 | 1103 | 1199 | 1198 | 1258 | 24.12 | 4782.12 | 4599.75 | 182.37 | 4823 | 6.312 | 74.47 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2015-06-29 | 814 | 876 | 877 | 896 | 17.64 | 3480.64 | 3330.75 | 149.89 | 3514 | 4.414 | 77.59 | Module cleaning done Inverter- 4 Row- ,A,B,C,D,E, & Total module cleaning- 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 2015-06-30 | 966 | 1040 | 1040 | 1099 | 21.64 | 4166.64 | 4026 | 140.64 | 4225 | 5.515 | 74.66 | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning 594 & Grid Failure From -13:13 to 13:20 WO#15323914 | 15323914 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 2015-07-01 | 944 | 1024 | 1029 | 1090 | 21.21 | 4108.21 | 3948.75 | 159.46 | 4146 | 5.407 | 74.73 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Total module cleaning- 690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2015-07-02 | 996 | 1068 | 1074 | 1157 | 22.39 | 4317.39 | 4153.5 | 163.89 | 4353 | 5.674 | 74.77 | Module cleaning done Inverter- 3 & Trackers Row- ,P,Q,R,S,T, & Total module cleaning- 710 |  | 710 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2015-07-03 | 938 | 1018 | 1046 | 1074 | 21.58 | 4097.58 | 3944.25 | 153.33 | 4142 | 5.458 | 73.96 | Module cleaning done Inverter- 3 Row- ,L,M,N,O, & Total module cleaning 670 & Grid Failure From -11:36 to 11:42 WO#15472920 | 15472920 | 670 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2015-07-04 | 950 | 1057 | 1091 | 1068 | 21.33 | 4187.33 | 4037.25 | 150.08 | 4235 | 5.562 | 74.21 | Module cleaning done Inverter- 2 Row- ,I,J,K, & Total module cleaning 710 & Grid Failure From -18:50 to 18:02 WO#15545727 | 15545727 | 710 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2015-07-05 | 802 | 882 | 899 | 904 | 18.17 | 3505.17 | 3358.5 | 146.67 | 3549 | 4.575 | 75.6 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2015-07-06 | 741 | 831 | 831 | 827 | 17.18 | 3247.18 | 3116.25 | 130.93 | 3294 | 4.168 | 77.02 | Module cleaning done inverter -1 Row- G,H & Total module cleaning 504 & Cloudy day |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
193 | 2015-07-07 | 622 | 690 | 684 | 669 | 14.34 | 2679.34 | 2564.25 | 115.09 | 2730 | 3.522 | 75.54 | Module cleaning done Inverter- 1 Row- ,D,E,F, & Total module cleaning 462 & Grid Failure From -11:36 to 11:46 & 15:01 to 15:40 WO# | 15702683 15713587 | 462 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2015-07-08 | 616 | 656 | 656 | 657 | 11.97 | 2596.97 | 2469.75 | 127.22 | 2639 | 3.24 | 79.38 | Module cleaning done inverter -1 Row- A,B,C, & Total module cleaning 540 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 2015-07-09 | 747 | 797 | 797 | 810 | 15.66 | 3166.66 | 3026.25 | 140.41 | 3212 | 3.991 | 78.44 | Module cleaning done inverter -4 Row- A,B,C,D,E, & Total module cleaning 630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 2015-07-10 | 757 | 814 | 814 | 832 | 17.38 | 3234.38 | 3093.75 | 140.63 | 3283 | 4.14 | 77.28 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning 594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 2015-07-11 | 826 | 893 | 888 | 920 | 18.82 | 3545.82 | 3403.5 | 142.32 | 3605 | 4.584 | 76.65 | Module cleaning done Inverter- 4 Row- ,I,J,K,L, & Total module cleaning- 690 & Grid Failure From -18:03 to 18:09 WO# | 16007430 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2015-07-12 | 915 | 989 | 995 | 1022 | 20.65 | 3941.65 | 3792 | 149.65 | 3983 | 5.459 | 71.11 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 2015-07-13 | 1024 | 1108 | 1108 | 1159 | 22.66 | 4421.66 | 4252.5 | 169.16 | 4460 | 5.799 | 74.96 | NO any Issue |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 2015-07-14 | 1023 | 1109 | 1119 | 1166 | 22.27 | 4439.27 | 4280.25 | 159.02 | 4486 | 5.863 | 74.57 | Module cleaning done Inverter- 3 & Trackers Row- ,Q,R,S,T, & Total module cleaning- 354 & Grid Failure From -16:57 to 17:03 WO# | 16151488 | 354 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 2015-07-15 | 893 | 961 | 989 | 1012 | 19.12 | 3874.12 | 3726.75 | 147.37 | 3928 | 5.116 | 74.83 | Module cleaning done Inverter- 3 Row- ,N,O,P,, & Total module cleaning- 546 & Grid Failure From -17:58 to 18:04 WO# | 16208984 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 2015-07-16 | 916 | 995 | 1012 | 1021 | 20.44 | 3964.44 | 3783 | 181.44 | 4002 | 5.148 | 75.76 | Module cleaning done inverter -2 & 3 Row- ,L,M, & Total module cleaning 504 |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 2015-07-17 | 803 | 887 | 899 | 896 | 18.67 | 3503.67 | 3389.25 | 114.42 | 3551 | 4.481 | 77.23 | Module cleaning done inverter -2 Row- ,J,K, & Total module cleaning 570 |  | 570 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 2015-07-18 | 819 | 922 | 905 | 917 | 19 | 3582 | 3433.5 | 148.5 | 3621 | 4.652 | 75.86 | Inverter-2 AJB -106 String -7 MC4 connector bourned so replace connector and string started WO#() & Module cleaning done inverter -2 & 1 Row- ,I,J, & Total module cleaning 504 |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2015-07-19 | 464 | 497 | 492 | 492 | 9.42 | 1954.42 | 1845.75 | 108.67 | 1995 | 2.332 | 83.38 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 2015-07-20 | 452 | 486 | 492 | 490 | 8.89 | 1928.89 | 1797 | 131.89 |  |  |  | Internet failure & Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning 489 |  | 489 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
207 | 2015-07-21 | 328 | 345 | 356 | 356 | 6.54 | 1391.54 | 1339.5 | 52.04 |  |  |  | Grid Failure From-11:40 to 14:08 WO# |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 2015-07-22 | 458 | 486 | 492 | 494 | 9.53 | 1939.53 | 1818 | 121.53 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 2015-07-23 | 825 | 899 | 910 | 913 | 18.76 | 3565.76 | 3411 | 154.76 |  |  |  | 11K.V side (G.O.D. Swich) R, phase sparking so maintains R, phase sutdown plant-10:03 to 10:20 WO# |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 2015-07-24 | 634 | 679 | 684 | 691 | 14.48 | 2702.48 | 2586 | 116.48 |  |  |  | Grid Failure From-15:45 to 16:33 WO# |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 2015-07-25 | 390 | 424 | 418 | 418 | 7.9 | 1657.9 | 1543.5 | 114.4 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 2015-07-26 | 164 | 175 | 175 | 172 | 2.81 | 688.81 | 610.5 | 78.31 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 2015-07-27 | 152 | 164 | 170 | 159 | 2.53 | 647.53 | 551.25 | 96.28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 2015-07-28 | [5 empty] | 0 |  | 0 |  |  |  | Grid Failure From-28-7-2015-08:58 to 30-7-2015 -14:43 WO#16824672 | 16824672 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 2015-07-29 | [5 empty] | 0 |  | 0 |  |  |  | Grid Failure From-28-7-2015-08:58 to 30-7-2015 -14:43 WO#16824672 | 16824672 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2015-07-30 | 204 | 220 | 226 | 218 | 4.2 | 872.2 | 782.25 | 89.95 |  |  |  | Grid Failure From-28-7-2015-08:58 to 30-7-2015 -14:43 WO#16824672 | 16824672 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 2015-07-31 | 690 | 758 | 758 | 769 | 15.74 | 2990.74 | 2845.5 | 145.24 |  |  |  | Grid Failure From-08:42 to 10:30 WO# |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 2015-08-01 | 605 | 656 | 661 | 665 | 13.16 | 2600.16 | 2491.5 | 108.66 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 2015-08-02 | 706 | 769 | 764 | 763 | 15.03 | 3017.03 | 2865.75 | 151.28 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 2015-08-03 | 984 | 1079 | 910 | 1098 | 21.46 | 4092.46 | 3964.25 | 128.21 |  |  |  | Inverter no-3 morning time note wakeup Err-no-ISU (8185) Folt reset manualy inverter started -10:01 WO# & Grid Failure From-15:40 to 15:49 WO#17070345 | 17070345 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 2015-08-04 | 967 | 1058 | 1057 | 1078 | 21.82 | 4181.82 | 4021.5 | 160.32 |  |  |  | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 2015-08-05 | 825 | 899 | 899 | 920 | 17.57 | 3560.57 | 3386.25 | 174.32 |  |  |  | Module cleaning done Inverter- 4 Row- ,F,G,H, & Total module cleaning- 594 & Grid Failure From -06:30 to 06:40 WO#17177576 | 17177576 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 2015-08-06 | 792 | 859 | 853 | 896 | 17.74 | 3417.74 | 3301.5 | 116.24 |  |  |  | Module cleaning done inverter -4 Row- ,I,J,K,L,, & Total module cleaning -690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 2015-08-07 | 887 | 972 | 973 | 1013 | 19.99 | 3864.99 | 3714 | 150.99 |  |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 |  | 604 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 2015-08-08 | 950 | 1040 | 1046 | 1079 | 21.91 | 4136.91 | 3973.5 | 163.41 |  |  |  | Module cleaning done Inverter- 3&2 Row- ,L,M,N, & Total module cleaning- 714 & Grid Failure From -15:03 to 15:10 WO#17364939 | 1736439 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 2015-08-09 | 899 | 509 | 983 | 1030 | 20.78 | 3441.78 | 3305.25 | 136.53 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -12:20 to 15:55 WO# |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 2015-08-10 | 548 | 356 | 605 | 603 | 12.36 | 2124.36 | 2007 | 117.36 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -13:20 to 17:05 WO# & Module cleaning done inverter -2 Row- ,J,K, & Total module cleaning -567 |  | 567 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 2015-08-11 | 746 | 272 | 814 | 820 | 15.7 | 2667.7 | 2520.75 | 146.95 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -10:00 to 16:00 WO# & Module cleaning done inverter -2&1 Row- ,H,I, & Total module cleaning -504 |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 2015-08-12 | 470 | 514 | 515 | 514 | 9.69 | 2022.69 | 1906.5 | 116.19 |  |  |  | Inverter no-2 ABB-Auto Trip becose Inverters Bloware fan (supply card) Bourned Inverter trip -10:20 to 10:40 WO# |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 2015-08-13 | 361 | 396 | 395 | 396 | 7.57 | 1555.57 | 1470 | 85.57 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 2015-08-14 | 486 | 543 | 532 | 542 | 10.52 | 2113.52 | 2010.75 | 102.77 |  |  |  | Two time Grid Failure From-9:50 to 9:59 WO#17658237 & 14:20 to 14:40 WO#17660923 | 17658237 17660923 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 2015-08-15 | 752 | 831 | 831 | 831 | 16.44 | 3261.44 | 3112.5 | 148.94 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 2015-08-16 | 860 | 944 | 938 | 958 | 17.74 | 3717.74 | 3558 | 159.74 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 2015-08-17 | 814 | 899 | 888 | 909 | 19.19 | 3529.19 | 3368.25 | 160.94 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 2015-08-18 | 820 | 904 | 859 | 931 | 18.95 | 3532.95 | 3384.75 | 148.2 |  |  |  | Inverter no-3 morning time note wakeup Err-no-ISU (8185) Folt reset manualy inverter started -09:40 WO# |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 2015-08-19 | 989 | 1092 | 1086 |  | 17.03 | 3184.03 | 3030 | 154.03 |  |  |  | Inverter no-4 morning time not wakeup Err code-0252 (IGBT SWICH) WO# |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 2015-08-20 | 775 | 706 | 837 |  | 10.34 | 2328.34 | 2201.25 | 127.09 |  |  |  | Inverter no-2 ABB sutdown to inverter 11:20 to 12:25 replace the Than card inverter started 12:25 WO#() & Inverter no-1,2,3,SMA Trackers sutdown to inverters 10:40 to 14:10 Mager testing Folt Faund inverter no-3 Folt issue sold out WO#() & Combiner P.M (750 Kw side) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 2015-08-21 | 983 | 1074 | 1073 |  | 33.02 | 3163.02 | 2998.5 | 164.52 |  |  |  | Combiner P.M (250K.w) & Seeds P.M |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 2015-08-22 | 786 | 860 | 860 |  | 28.24 | 2534.24 | 2403.75 | 130.49 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 2015-08-23 | 871 | 943 | 944 |  | 29.99 | 2787.99 | 2645.25 | 142.74 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 2015-08-24 | 904 | 984 | 978 |  | 31.99 | 2897.99 | 2752.5 | 145.49 |  |  |  | Inverter no-1,2,3,4, inverters Filter cleaning |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 2015-08-25 | 854 | 928 | 921 | 769 | 31.07 | 3503.07 | 3345 | 158.07 |  |  |  | Inverter no-4 inverter started 10:15 a.m WO#() |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 2015-08-26 | 842 | 915 | 911 | 897 | 29.35 | 3594.35 | 3406.5 | 187.85 |  |  |  | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 2015-08-27 | 1007 | 1103 | 1102 | 1075 | 35.62 | 4322.62 | 4136.25 | 186.37 |  |  |  | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 2015-08-28 | 966 | 1063 | 1052 | 1039 | 33.76 | 4153.76 | 3963 | 190.76 |  |  |  | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 & Grid Failure From-10:00 to 10:05 WO#() |  | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 2015-08-29 | 1007 | 1096 | 1079 | 1081 | 35.21 | 4298.21 | 4108.5 | 189.71 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 2015-08-30 | 825 | 894 | 888 | 896 | 27.64 | 3530.64 | 3374.25 | 156.39 |  |  |  | Two time Grid Failure From-07:09 to 07:21 & 11:28 to 11:38 WO#() |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 2015-08-31 | 803 | 876 | 876 | 832 | 29 | 3416 | 3234 | 182 |  |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-13:57 to 14:07 WO#(18593384) | 18593384 | 604 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | 2015-09-01 | 1012 | 1102 | 1120 | 1086 | 37.87 | 4357.87 | 4167 | 190.87 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 & Two Time Grid Failure From-06:18 to 06:25 & 10:15 to 10:20 WO#(18632721 & 18635335) | 18632721 18635330 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 2015-09-02 | 972 | 1086 | 1085 | 1031 | 37.99 | 4211.99 | 4020.75 | 191.24 |  |  |  | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 & Grid Failure From-10:50 to 10:59 WO#(18695171) | 18695171 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 2015-09-03 | 972 | 1091 | 1069 | 1066 | 32.91 | 4230.91 | 3996 | 234.91 |  |  |  | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 2015-09-04 | 1058 | 1164 | 1130 | 1010 | 36.4 | 4398.4 | 4277.25 | 121.15 |  |  |  | Module cleaning done inverter -1 Row- ,A,B,C,D,E, & Total module cleaning -483 & Grid Failure From-16:07 to 16:58 WO#(18814517) | 18814517 | 483 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 2015-09-05 | 955 | 1041 | 1012 | 965 | 33.45 | 4006.45 | 3814.5 | 191.95 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 2015-09-06 | 1091 | 1192 | 1148 | 1109 | 36.48 | 4576.48 | 4370.25 | 206.23 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 2015-09-07 | 1063 | 1142 | 1108 | 1040 | 38.06 | 4391.06 | 4217.25 | 173.81 |  |  |  | Inverter no-4 shutdown 13:00 to 13:28 for maintance Replace IGBT 'Y' Phase inverter started 13:28 WO#() & Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 2015-09-08 | 871 | 933 | 910 | 962 | 31.53 | 3707.53 | 3546.75 | 160.78 |  |  |  | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2015-09-09 | 1046 | 1159 | 1153 | 1176 | 35.72 | 4569.72 | 4375.5 | 194.22 |  |  |  | Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 07++tive in AJB-116 of The Inverter-3 & 03--tive Line AJB-100 Inverter no-4 during The Period of 10:30 To 10:45.WO#(19058966) & Module cleaning done Inverter-4 Row ,I,J,K,L, & Total module cleaning 690 | 19058966 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
260 | 2015-09-10 | 1028 | 1125 | 1114 | 1148 | 33.08 | 4448.08 | 4287 | 161.08 |  |  |  | Two time Grid Failure From-14:36 to 14:47 & 16:25 to 17:55 WO#() |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 2015-09-11 | 1154 | 1267 | 1261 | 1271 | 40.2 | 4993.2 | 4802.25 | 190.95 |  |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-18:35 to 19:05 WO#() |  | 604 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | 2015-09-12 | 1023 | 1113 | 1119 | 1132 | 34.94 | 4421.94 | 4258.5 | 163.44 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 & Grid Failure From-17:05 to 18:30 WO#(19203752) | 19203752 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | 2015-09-13 | 1046 | 1148 | 1154 | 1199 | 38.52 | 4585.52 | 4433.25 | 152.27 |  |  |  | Three Time Grid Failure From-07:02 to 07:10 & 09:07 to 9:34 & 11:28 to 11:33 WO#() & Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 03++tive in AJB-101 of The Inverter-4 & 03--tive Line AJB-102 Inverter no-4 during The Period of 10:45 To 11:00.WO#(19237302) | 19225941 19232703 19235820 19237302 |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
264 | 2015-09-14 | 1102 | 1210 | 1227 | 1265 | 39.33 | 4843.33 | 4659.75 | 183.58 |  |  |  | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 2015-09-15 | 1063 | 1187 | 1175 | 1213 | 39.88 | 4677.88 | 4487.25 | 190.63 |  |  |  | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 2015-09-16 | 1125 | 1261 | 1238 | 1273 | 39.55 | 4936.55 | 4756.5 | 180.05 |  |  |  | Module cleaning done inverter -1 Row- ,A,B,C,D, E, & Total module cleaning -483 |  | 483 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | 2015-09-17 | 1001 | 1091 | 1075 | 1092 | 35.8 | 4294.8 | 4139.25 | 155.55 |  |  |  | Module cleaning done inverter -4 Row- ,A,B,C,D, E, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | 2015-09-18 | 656 | 718 | 701 | 731 | 23.53 | 2829.53 | 2710.5 | 119.03 |  |  |  | Grid Failure From-14:40 to 14:54 WO#19495606 & Module clean by Rain | 19495606 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 2015-09-19 | [5 empty] | 0 |  | 0 |  |  |  | Grid Failure From-yesterday night to 18:05 WO# & Module clean by Rain & Main Transformer P.M |  |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
270 | 2015-09-20 | 17 | 11 | 11 | 16 | 0.54 | 55.54 | 1.5 | 54.04 |  |  |  | Grid Failure From-08:00 to 16:20 WO#(A.C.Voltage low) & Module clean by Rain |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 2015-09-21 | 305 | 453 | 452 | 361 | 14.73 | 1585.73 | 1489.5 | 96.23 |  |  |  | Inverter no-4 morning time not wake up Err no-0012 A.C.Voltage low reset Err code inverter started 11:25WO#19640583 & Inverter no-1 ABB 250 KVA Bloware than card failure Auto trip 13:00 to 13:35 WO#19640666 & Module clean by Rain | 19640583 19640666 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 2015-09-22 | 622 | 757 | 758 | 750 | 23.23 | 2910.23 | 2792.25 | 117.98 |  |  |  | Inverter no-1 ABB 250 KVA morning time note wake up Blowre than card Failure By pass 3 phase supply blowre & inverter started 10:08 WO#19676055 Module clean by Rain | 19676055 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 2015-09-23 | 898 | 984 | 984 | 1004 | 33.23 | 3903.23 | 3744 | 159.23 | 3950 | 5.29 | 72.77 | Grid Failure From-10:02 to 10:54 WO#(19734203) & Module clean by Rain | 19734203 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 2015-09-24 | 1120 | 1255 | 1243 | 1293 | 41.7 | 4952.7 | 4755.75 | 196.95 | 5000 | 6.56 | 74.288 | Today I Replaced The D.C.12Amp Fuse Link of The String- 05++tive in AJB-101 of The Inverter-1 during The Period of 10:30 To 10:45.WO#(19839635) | 19839635 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
275 | 2015-09-25 | 673 | 712 | 707 | 735 | 23.84 | 2850.84 | 2713.5 | 137.34 | 2910 | 5.09 | 55.7221 | Grid Failure (low voltege) From-08:15 to 12:27 WO#19835946 | 19835946 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 2015-09-26 | 1176 | 1289 | 1278 | 1329 | 42.39 | 5114.39 | 4914.75 | 199.64 | 5170 | 6.82 | 73.8854 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 & Grid Failure From-12:41 to 12:50 WO#(19898067) | 19898067 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2015-09-27 | 1091 | 1204 | 1192 | 1258 | 37.67 | 4782.67 | 4594.5 | 188.17 |  |  |  | Grid Failure From-16:28 to 17:58 WO#(19957162) | 19957162 | 594 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 2015-09-28 | 1181 | 1317 | 1301 | 1376 | 42.59 | 5217.59 | 5033.25 | 184.34 | 5280 |  |  | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 & Grid Failure From-09:22 to 09:32 WO#(19991956) | 19991956 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2015-09-29 | 1035 | 1126 | 1114 | 1167 | 37.01 | 4479.01 | 4279.5 | 199.51 | 4530 |  |  | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 2015-09-30 | 972 | 1068 | 1068 | 92.04 | 37.44 | 3237.48 | 3075 | 162.48 | 3250 |  |  | Grid Failure From-08:30 to 10:05 WO#(20099787) & Inverter No-4 sleep mode 10:07 to 17:05 Err code - sleep mode inverter WO#20108412 | 20099787 20108412 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 2015-10-01 | 1188 | 1300 | 1328 | 1300 | 42.34 | 5158.34 | 5001 | 157.34 | 5260 |  |  | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 |  | 604 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2015-10-02 | 1136 | 1267 | 1278 | 1300 | 41.14 | 5022.14 | 4816.5 | 205.64 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 2015-10-03 | 1046 | 1164 | 1153 | 1200 | 37.65 | 4600.65 | 4351.5 | 249.15 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2015-10-04 | 1153 | 1289 | 1267 | 1200 | 41.36 | 4950.36 | 4848 | 102.36 |  |  |  | Grid Failure From-09:06 to 09:13 WO#(20317939) | 20317939 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2015-10-05 | 1131 | 1238 | 1221 | 1200 | 40.32 | 4830.32 | 4674 | 156.32 |  |  |  | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 & Grid Failure From-07:48 to 07:55 WO#(20355081) | 20355081 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2015-10-06 | 1142 | 1250 | 1227 | 1200 | 40.37 | 4859.37 | 4737 | 122.37 | 4960 | 6.51 | 74.2597 | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2015-10-07 | 1142 | 1249 | 1227 | 1300 | 40.43 | 4958.43 | 4737 | 221.43 | 4970 | 6.53 | 74.1815 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,E, & A,B,C,D,E, & Total module cleaning -1103 |  | 1103 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 2015-10-08 | 1125 | 1233 | 1221 | 1300 | 40.52 | 4919.52 | 4693.5 | 226.02 | 4930 | 6.5 | 73.9241 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,E, & A,B,C,D,E,F,G,H, & Total module cleaning -2188 |  | 2188 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 2015-10-09 | 1080 | 1170 | 1193 | 1200 | 39.06 | 4682.06 | 4498.5 | 183.56 | 4720 | 6.29 | 73.1382 | Module cleaning done inverter -2 & 3 Row- ,K,L,M, & Total module cleaning -770 & Grid Failure From-13:42 to 13:55 & 16:43 to 16:54 WO#(20521472) |  | 770 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2015-10-10 | 1040 | 1136 | 1147 | 1100 | 48.64 | 4471.64 | 4370.25 | 101.39 | 4600 | 6.09 | 73.6196 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-09:45 to 09:55 & 16:31 to 16:42 & 17:19 to 17:25 WO#() | 20561787 20580052 20580124 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 2015-10-11 | 486 | 526 | 537 | 500 | 20.57 | 2069.57 | 1987.5 | 82.07 |  |  |  | Grid Failure From-06:15 to 12:37 WO#() |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 2015-10-12 | 927 | 1006 | 1012 | 1000 | 36.98 | 3981.98 | 3877.5 | 104.48 | 4070 | 5.72 | 69.3507 | 6 Time Grid Failure From-08:45 to 08:56 & 9:00 to 9:22 & 10:11 to 10:28 & 15:52 to 15:58 & 17:05 to 17:52 & 17:37 to 17:43 WO#() | 20657087 20657369 20659381 20674817 20675269 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 2015-10-13 | 1023 | 1114 | 1125 | 1200 | 39.87 | 4501.87 | 4332.75 | 169.12 | 4480 | 6.27 | 69.6407 | Night time grid failure to 8:32 WO#20699781 & 17:51 to 17:56 | 20699781 20719213 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 2015-10-14 | 1103 | 1199 | 1210 | 1200 | 43.14 | 4755.14 | 4599 | 156.14 | 4830 | 6.4 | 73.5563 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 & Grid Failure From-16:28 to 16:33 WO#(20757004) | 20757004 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2015-10-15 | 1091 | 1181 | 1193 | 1200 | 42.53 | 4707.53 | 4519.5 | 188.03 | 4750 | 6.29 | 73.603 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 & L.T PANEL P.M |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2015-10-16 | 1051 | 1131 | 1136 | 1189 | 41.24 | 4548.24 | 4344 | 204.24 | 4570 | 6.07 | 73.3804 | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2015-10-17 | 1007 | 1085 | 1097 | 1121 | 42.3 | 4352.3 | 4163.25 | 189.05 | 4390 | 5.96 | 71.7911 | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-16:28 to 16:33 WO#(20757004) | 20757004 | 604 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2015-10-18 | 1012 | 1097 | 1097 | 1147 | 43.66 | 4396.66 | 4191 | 205.66 | 4410 | 5.9 | 72.8516 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 2015-10-19 | 966 | 1046 | 1068 | 1072 | 41.89 | 4193.89 | 3993 | 200.89 | 4210 | 5.7 | 71.988 | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2015-10-20 | 1018 | 1096 | 1154 | 1100 | 44.15 | 4412.15 | 4224 | 188.15 | 4450 | 5.86 | 74.0142 | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2015-10-21 | 984 | 1063 | 1130 | 1200 | 43 | 4420 | 4163.25 | 256.75 | 4390 | 5.7 | 75.0658 | Today I Replaced The 3 D.C.12Amp Fuse Link of The String- 04--tive in AJB-101 of The Inverter-4 & String no-2 & 4 --tive line AJB -105 Inverter no-4 during The Period of 09:40 To 09:50.WO#(21052510) & Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 | 21052510 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
303 | 2015-10-22 | 1017 | 1142 | 1176 | 1200 | 44.92 | 4579.92 | 4381.5 | 198.42 | 4610 | 5.96 | 75.3889 | Module cleaning done inverter -1 Row- ,A,B,C,D,E, & Total module cleaning -483 |  | 483 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2015-10-23 | 1063 | 1222 | 1227 | 1100 | 46.77 | 4658.77 | 4572.75 | 86.02 | 4810 | 6.19 | 75.7368 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 2015-10-24 | 1074 | 1249 | 1221 | 1248 | 46.88 | 4838.88 | 4620.75 | 218.13 | 4860 | 6.2 | 76.4007 | Grid Failure From-17:21 to 17:32 WO#21218179 | 21218179 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2015-10-25 | 826 | 933 | 922 | 936 | 36.13 | 3653.13 | 3478.5 | 174.63 | 3690 | 4.82 | 74.616 | Grid Failure From-11:10 to 11:22 WO#21252902 | 21252902 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2015-10-26 | 1034 | 1153 | 1124 | 1146 | 43.24 | 4500.24 | 4280.25 | 219.99 | 4510 | 5.89 | 74.6301 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2015-10-27 | 1046 | 1136 | 1109 | 1126 | 42.96 | 4459.96 | 4249.5 | 210.46 | 4480 | 5.78 | 75.5445 | Module cleaning done inverter -4 Row- ,I,J,K,L, & Total module cleaning -690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2015-10-28 | 1120 | 1216 | 1192 | 1261 | 46.51 | 4835.51 | 4620 | 215.51 | 4860 | 6.35 | 74.5959 | Module cleaning done inverter -3 & Trackers Row- ,O,P,Q,R,S,T, & Total module cleaning -604 & Grid Failure From-08:57 to 09:15 WO#(21392605) & Today Replace Transformers New Bridhar & slicagel (2,3,4,) | 21392605 | 604 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2015-10-29 | 1193 | 1306 | 1272 | 1373 | 50.11 | 5194.11 | 4953.75 | 240.36 | 5210 | 6.62 | 76.7065 | Module cleaning done inverter -3 & 2 Row- ,L,M,N, & Total module cleaning -714 & Grid Failure From-16:49 to 16:55 WO#() Transformers p.m & Inverter P.M (1,2,) | 21451062 | 714 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2015-10-30 | 1181 | 1289 | 1278 | 1360 | 50.75 | 5158.75 | 4926 | 232.75 | 5170 | 6.44 | 78.2451 | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -840 & Inverter P.M (3,4) |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2015-10-31 | 1165 | 1277 | 1301 | 1341 | 50.36 | 5134.36 | 4899.75 | 234.61 | 5140 | 6.41 | 78.1552 | Module cleaning done inverter -1 Row- ,F,G,H, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 2015-11-01 | 1068 | 1171 | 1193 | 1218 | 46.26 | 4696.26 | 4467.75 | 228.51 | 4710 | 6.01 | 76.38 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2015-11-02 | 989 | 1108 | 1102 | 1134 | 43.21 | 4376.21 | 4188 | 188.21 | 4410 | 5.71 | 75.27 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,E, & A,B, & Total module cleaning -645 & Grid Failure From-08:49 to 08:54 WO#(21624101) | 21624101 | 645 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2015-11-03 | 950 | 1068 | 1046 | 1066 | 40.78 | 4170.78 | 3984 | 186.78 | 4200 | 5.5 | 74.42 | Module cleaning done inverter - 4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-08:32 to 08:53 WO#(21667547) | 21667547 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2015-11-04 | 882 | 973 | 944 | 965 | 36.66 | 3800.66 | 3608.25 | 192.41 | 3810 | 5.04 | 73.67 | Module cleaning done inverter - 4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-14:50 to 16:37 WO#(21738513) | 21738513 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2015-11-05 | 1018 | 1119 | 1091 | 1119 | 42.26 | 4389.26 | 4187.25 | 202.01 | 4420 | 5.73 | 75.18 | Module cleaning done inverter -4,3,& Trackers Row- ,J,K,L,& S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 2015-11-06 | 865 | 955 | 916 | 968 | 37.27 | 3741.27 | 3571.5 | 169.77 | 3780 | 5.07 | 72.66 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-09:45 to 10:14 & 13:53 to 14:35 WO#(21826715) | 21826715 21838639 | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2015-11-07 | 899 | 984 | 961 | 1005 | 38.68 | 3887.68 | 3714 | 173.68 | 3930 | 5.14 | 74.52 | Module cleaning done inverter - 3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-15:57 to 16:05 WO#(21892950) | 21892950 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2015-11-08 | 932 | 1018 | 1006 | 1010 | 40.31 | 4006.31 | 3804.75 | 201.56 | 4020 | 5.27 | 74.34 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2015-11-09 | 933 | 1023 | 1023 | 1046 | 40.21 | 4065.21 | 3867.75 | 197.46 | 4090 | 5.3 | 75.21 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2015-11-10 | 927 | 1018 | 1035 | 1042 | 39.75 | 4061.75 | 3855.75 | 206 | 4080 | 5.26 | 75.6 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2015-11-11 | 928 | 1040 | 1040 | 1046 | 40.31 | 4094.31 | 3890.25 | 204.06 | 4110 | 5.29 | 75.72 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2015-11-12 | 955 | 1068 | 1069 | 1072 | 42.03 | 4206.03 | 4004.25 | 201.78 | 4230 | 5.47 | 75.37 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2015-11-13 | 972 | 1091 | 1091 | 1083 | 42.67 | 4279.67 | 4068 | 211.67 | 4300 | 5.62 | 74.57 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2015-11-14 | 1001 | 1137 | 1125 | 1136 | 44.15 | 4443.15 | 4226.25 | 216.9 | 4460 | 5.82 | 74.69 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2015-11-15 | 995 | 1142 | 1114 | 1120 | 43.54 | 4414.54 | 4199.25 | 215.29 | 4430 | 5.68 | 76.01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2015-11-16 | 893 | 1012 | 983 | 1006 | 40.13 | 3934.13 | 3750.75 | 183.38 | 3997 | 5.22 | 74.63 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-07:49 to 08:07 & 14:01 to 14:59 & 17:10 to 17:27 WO#() | 22307137 22318269 22324208 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2015-11-17 | 1001 | 1096 | 1069 | 1048 | 42.43 | 4256.43 | 4057.5 | 198.93 | 4280 | 5.56 | 75.02 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-16:13 to 16:20 & 17:00 to 17:28 WO#() | 22403483 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2015-11-18 | 995 | 1092 | 1062 | 1069 | 42.67 | 4260.67 | 4043.25 | 217.42 | 4280 | 5.68 | 73.44 | Module cleaning done inverter -4 & 3 Row- ,J,K,L, & S,T, & Trackers & Total module cleaning -612 & Grid Failure From-09:49 to 10:04 WO#() | 22414913 | 612 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2015-11-19 | 1029 | 1125 | 1098 | 1122 | 43.88 | 4417.88 | 4211.25 | 206.63 | 4430 | 5.75 | 75.09 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2015-11-20 | 1029 | 1136 | 1108 | 1146 | 45.53 | 4464.53 | 4250.25 | 214.28 | 4480 | 5.84 | 74.76 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2015-11-21 | 995 | 1091 | 1097 | 1120 | 43.84 | 4346.84 | 4138.5 | 208.34 | 4360 | 5.68 | 74.81 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 & seeds P.M |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2015-11-22 | 898 | 989 | 1007 | 1010 | 39.67 | 3943.67 | 3781.5 | 162.17 | 3950 | 4.79 | 80.37 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2015-11-23 | 860 | 967 | 977 | 994 | 37.9 | 3835.9 | 3639 | 196.9 | 3850 | 5.02 | 74.74 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2015-11-24 | 650 | 741 | 724 | 726 | 27.72 | 2868.72 | 2704.5 | 164.22 | 2890 | 3.69 | 76.33 | Module cleaning done inverter -4 & 1 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Grid Failure From-15:09 to 15:17 WO#() | 22716056 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2015-11-25 | 735 | 814 | 797 | 779 | 31.13 | 3156.13 | 2985 | 171.13 | 3180 | 4.23 | 73.27 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2015-11-26 | 803 | 893 | 877 | 800 | 34.25 | 3407.25 | 3303.75 | 103.5 | 3500 | 4.66 | 73.2 | Module cleaning done inverter -4 Row- ,G,H,I & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2015-11-27 | 984 | 1108 | 1079 | 1116 | 41.73 | 4328.73 | 4126.5 | 202.23 | 4350 | 5.65 | 75.04 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Grid Failure From-17:08 to 17:19 WO#(22855523) | 22855523 | 612 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2015-11-28 | 864 | 961 | 962 | 982 | 40.1 | 3809.1 | 3629.25 | 179.85 | 3840 | 5.2 | 71.97 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-11:13 to 11:45 WO#(22889812) | 22889812 | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2015-11-29 | 1024 | 1112 | 1147 | 1157 | 46.17 | 4486.17 | 4299.75 | 186.42 | 4520 | 6 | 73.42 | Today I Replaced The D.C.12Amp Fuse Link of The String- 07--tive in AJB-105 of The Inverter-1 during The Period of 11:10 To 11:15.WO#(22939578) & Trackers P.M | 22939578 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
343 | 2015-11-30 | 848 | 939 | 956 | 943 | 37.36 | 3723.36 | 3540 | 183.36 | 3875 | 5.1 | 74.055 | Module cleaning done inverter -2 & 3 Row- ,K,L,M, & Total module cleaning -777 & Transformer No-2 300kva P.M |  | 777 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
345 | 2015-12-01 | 825 | 1006 | 1000 | 985 | 39.24 | 3855.24 | 3672.75 | 182.49 | 3890 | 5.21 | 72.77 | today ABB engineer has come at site for replacing blower than card so for replacing purpose we took shut down at 15:50 and switching on at 16:45. But that card couldn’t work so they will get to fix some other card by this week. & Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 | 23044484 | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2015-12-02 | 984 | 1119 | 1091 | 1072 | 43.36 | 4309.36 | 4107 | 202.36 | 4330 | 5.71 | 73.9 | Today I Replaced The D.C.12Amp Fuse Link of The String- 05--tive in AJB-105 of The Inverter-1 during The Period of 10:15 To 10:20.WO#() & Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-16:59 to 17:22 WO#() | 23332248 23824011 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
347 | 2015-12-03 | 1080 | 1193 | 1165 | 1150 | 46.83 | 4634.83 | 4419.75 | 215.08 | 4650 | 6.23 | 72.74 | Module cleaning done inverter -4 & 1 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2015-12-04 | 1045 | 1154 | 1119 | 1200 | 45.65 | 4563.65 | 4305 | 258.65 | 4520 | 6.15 | 71.63 | Module cleaning done inverter -4 Row- C,D,E,F & Total module cleaning -630 & Grid failure from - 12:40 to 12:49 WO# | 23332366 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2015-12-05 | 973 | 1062 | 1040 | 1078 | 42.11 | 4195.11 | 3977.25 | 217.86 | 4210 | 5.72 | 71.73 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 2015-12-06 | 1001 | 1097 | 1070 | 1121 | 43.48 | 4332.48 | 4116 | 216.48 | 4340 | 5.9 | 71.69 | Module cleaning done inverter -4 Row- G,H,I, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2015-12-07 | 932 | 1018 | 995 | 1052 | 41.97 | 4038.97 | 3840.75 | 198.22 | 4058 | 5.7 | 69.3889 | Module cleaning done inverter -4 & Trackers Row- ,J,K,L,& S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2015-12-08 | 933 | 1063 | 1069 | 1084 | 43.45 | 4192.45 | 3991.5 | 200.95 | 4205 | 5.7 | 71.9025 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2015-12-09 | 899 | 983 | 1011 | 1008 | 40.58 | 3941.58 | 3751.5 | 190.08 | 3940 | 5.33 | 72.04 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2015-12-10 | 916 | 1035 | 1035 | 1000 | 41.3 | 4027.3 | 3891 | 136.3 | 4110 | 5.33 | 75.15 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2015-12-11 | 938 | 1085 | 1063 | 1026 | 42.87 | 4154.87 | 3965.25 | 189.62 | 4180 | 5.38 | 75.72 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid failure from - 10:32 to 10:38 WO#() | 23500607 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2015-12-12 | 1086 | 1199 | 1170 | 1149 | 47.56 | 4651.56 | 4432.5 | 219.06 | 4660 | 6.08 | 74.7 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D & A,B & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2015-12-13 | 1063 | 1164 | 1119 | 1111 | 46.31 | 4503.31 | 4296 | 207.31 | 4520 | 5.96 | 73.91 | Module cleaning done inverter -4 Row- C,D,E,F, & Total module cleaning -630 & Grid failure from - 14:04 to 14:09 WO#() | 23602126 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2015-12-14 | 1068 | 1171 | 1126 | 1121 | 46.58 | 4532.58 | 4314 | 218.58 | 4540 | 5.98 | 73.99 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2015-12-15 | 1108 | 1226 | 1187 | 1203 | 48.83 | 4772.83 | 4545.75 | 227.08 | 4780 | 6.29 | 74.06 | Today I Replaced The D.C.12Amp Fuse Link of The String- 05--tive in AJB-115 of The Inverter-1 during The Period of 10:20 To 10:25.WO#() & Module cleaning done inverter -3&4 Trackers Row- ,J,K,L, & S,T, & Total module cleaning -612 | 23684627 | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
360 | 2015-12-16 | 1069 | 1171 | 1142 | 1191 | 46.91 | 4619.91 | 4393.5 | 226.41 | 4630 | 6.14 | 73.49 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2015-12-17 | 1040 | 1147 | 1147 | 1184 | 47.32 | 4565.32 | 4353 | 212.32 | 4590 | 5.94 | 75.31 | Module cleaning done inverter -2 & 3 Row- ,K,L,M, & Total module cleaning -777 & Grid failure from - 17:09 to 17:13 WO#() | 23827201 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2015-12-18 | 1063 | 1176 | 1205 | 1184 | 48.66 | 4676.66 | 4453.5 | 223.16 | 4680 | 6.08 | 75.02 | Module cleaning done inverter -1 & 2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2015-12-19 | 1012 | 1154 | 1147 | 1113 | 46.46 | 4472.46 | 4283.25 | 189.21 | 4480 | 5.8 | 75.28 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2015-12-20 | 1023 | 1187 | 1159 | 1127 | 46.69 | 4542.69 | 4332 | 210.69 | 4560 | 5.98 | 74.32 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2015-12-21 | 967 | 1074 | 1057 | 1000 | 42.7 | 4140.7 | 3933 | 207.7 | 4150 | 5.35 | 75.6 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 2015-12-22 | 916 | 1012 | 990 | 927 | 39.94 | 3884.94 | 3687.75 | 197.19 | 3900 | 5.06 | 75.12 | Inverter No-1,2,3,4, Filter Cleaning & Inverter No- 4 (P.M) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 2015-12-23 | 916 | 1006 | 983 | 921 | 39.78 | 3865.78 | 3663.75 | 202.03 | 3880 | 5.08 | 74.44 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 2015-12-24 | 1000 | 1103 | 1080 | 1021 | 43.69 | 4247.69 | 4039.5 | 208.19 | 4260 | 5.61 | 74.01 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 2015-12-25 | 972 | 1068 | 1040 | 974 | 42.62 | 4096.62 | 3886.5 | 210.12 | 4110 | 5.4 | 74.18 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 2015-12-26 | 1030 | 1131 | 1103 | 1079 | 45.08 | 4388.08 | 4169.25 | 218.83 | 4400 | 5.81 | 73.81 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 2015-12-27 | 977 | 1085 | 1057 | 1049 | 43.78 | 4211.78 | 4008.75 | 203.03 | 4230 | 5.68 | 72.58 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 2015-12-28 | 198 | 221 | 209 | 225 | 10.26 | 863.26 | 768.75 | 94.51 |  |  |  | Grid Failure From-08:20 to 14:40 WO#24330844 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 2015-12-29 | 566 | 1051 | 1029 | 1029 | 48.01 | 3723.01 | 3531.75 | 191.26 | 3740 | 5.74 | 63.5 | Inverter no- 1 ABB (250KW) Auto trip 10:00 to 17:00 wo# | 24379670 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 2015-12-30 | 712 | 1024 | 995 | 970 | 45.03 | 3746.03 | 3550.5 | 195.53 | 3770 | 5.51 | 66.68 | Inverter-no-1 ABB was shut down from 12:30 to 14:00 for replacing the IGBT blower by ABB engineer but job could't completed |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 2015-12-31 | 628 | 808 | 972 | 949 | 45.39 | 3402.39 | 3230.25 | 172.14 | 3430 | 5.35 | 62.48 | Inverter-no-1 ABB was shut down from 13:25 to 16:00 & Inverter-no-2 was shut down from14:00 to 15:30 for replacing the IGBT blower by ABB engineer but job could't completed |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2016
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2016-01-01 | 966 | 1080 | 1046 | 1034 | 49.08 | 4175.08 | 3960 | 215.08 | 4180 | 5.76 | 70.73 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2016-01-02 | 865 | 966 | 939 | 934 | 43.44 | 3747.44 | 3560.25 | 187.19 | 3770 | 5.14 | 71.48 | Module cleaning done inverter -4 Row- ,A,B,C,D,E, & Total module cleaning -594 & Grid Failure From- 14:03 to 14:08WO# | 24587769 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2016-01-03 | 876 | 979 | 938 | 940 | 43.52 | 3776.52 | 3585.75 | 190.77 | 3800 | 5.18 | 71.5 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2016-01-04 | 877 | 978 | 944 | 986 | 43.77 | 3828.77 | 3599.25 | 229.52 | 3840 | 5.24 | 71.42 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2016-01-05 | 904 | 1012 | 973 | 1077 | 45.85 | 4011.85 | 3841.5 | 170.35 | 4030 | 5.43 | 72.33 | Module cleaning done inverter -4 & 3 Row- ,I,J,K,L, & S,T, & Total module cleaning -818 |  | 818 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2016-01-06 | 888 | 989 | 972 | 1085 | 48.93 | 3982.93 | 3782.25 | 200.68 | 4000 | 5.33 | 73.14 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2016-01-07 | 865 | 961 | 1001 | 1050 | 48.21 | 3925.21 | 3732.75 | 192.46 | 3950 | 5.26 | 73.19 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2016-01-08 | 921 | 1040 | 1125 | 1124 | 51.44 | 4261.44 | 4018.5 | 242.94 | 4270 | 5.58 | 74.58 | Module cleaning done inverter -2 Row- ,I,J,K, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2016-01-09 | 905 | 1080 | 1108 | 1069 | 50.06 | 4212.06 | 4015.5 | 196.56 | 4220 | 5.43 | 75.74 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2016-01-10 | 904 | 1114 | 1102 | 1058 | 41.29 | 4219.29 | 4039.5 | 179.79 | 4210 | 5.51 | 74.47 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2016-01-11 | 860 | 1051 | 1018 | 981 | 38.31 | 3948.31 | 3763.5 | 184.81 | 3980 | 5.27 | 0.73608 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From- 14:00 to 14:07 WO# |  | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2016-01-12 | 802 | 956 | 972 | 930 | 37.22 | 3697.22 | 3491.25 | 205.97 | 3720 | 5 | 72.51 | Inverter-no-1 ABB was shut down from 16:05 & Inverter-2 was shut down 16:25 for replacing the IGBT blower by ABB engineer but job could't completed & Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2016-01-13 | 962 | 1080 | 1046 | 1063 | 49.8 | 4200.8 | 4004.25 | 196.55 | 4250 | 5.5 | 75.31 | Module cleaning done inverter - 4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From- 10:30 to 10:42 & 15:25 to 15:36 WO# |  | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2016-01-14 | 995 | 1102 | 1058 | 1059 | 50.25 | 4264.25 | 4104.75 | 159.5 | 4280 | 5.51 | 0.75709 | Grid Failure From- 8:32 to 8:35 WO#25122514 | 25122514 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2016-01-15 | 1012 | 1114 | 1085 | 1077 | 52.34 | 4340.34 | 4134.75 | 205.59 | 4370 | 5.7 | 74.72 | Module cleaning done inverter - 4 & 3 Trackers Row- ,J,K,L, & S,T, Total module cleaning -612 & Grid Failure From- 11:55 to 12:02 & 17:04 to 17:08 & 17:32 TO 17:35 WO# | 25178460 25190550 25191566 | 612 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2016-01-16 | 876 | 961 | 933 | 907 | 42.58 | 3719.58 | 3516.75 | 202.83 | 3740 | 4.79 | 76.1 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2016-01-17 | 786 | 853 | 826 | 807 | 32.22 | 3304.22 | 3138 | 166.22 | 3330 | 4.3 | 75.47 | Grid Failure From- 7:30 to 9:20 WO# | 25282478 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2016-01-18 | 752 | 809 | 786 | 761 | 30.61 | 3138.61 | 2967.75 | 170.86 | 3150 | 4.04 | 75.99 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2016-01-19 | 859 | 938 | 915 | 910 | 37.54 | 3659.54 | 3467.25 | 192.29 | 3670 | 4.72 | 75.78 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2016-01-20 | 1023 | 1137 | 1125 | 1140 | 54.04 | 4479.04 | 4255.5 | 223.54 | 4490 | 5.67 | 77.18 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2016-01-21 | 1097 | 1236 | 1255 | 1222 | 61.01 | 4871.01 | 4652.25 | 218.76 | 4870 | 6.55 | 72.46 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Change the pyranometer & Change the inverter no-1 ABB new Blower fan |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2016-01-22 | 792 | 905 | 905 | 885 | 30.11 | 3517.11 | 3357 | 160.11 | 3550 | 4.92 | 70.32 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-14:15 to 17:08 | 25545549 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2016-01-23 | 1102 | 1300 | 1273 | 1245 | 47.88 | 4967.88 | 4739.25 | 228.63 | 4980 | 6.87 | 70.65 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2016-01-24 | 1091 | 1278 | 1238 | 1208 | 46.87 | 4861.87 | 4638.75 | 223.12 | 4870 | 6.77 | 70.11 | Grid Failure From- 15:35 to 15:43 WO# | 25639141 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2016-01-25 | 1091 | 1249 | 1216 | 1173 | 45.06 | 4774.06 | 4563 | 211.06 | 4790 | 6.65 | 70.2 | Module cleaning done inverter -4 & 3 & Trackers Row- ,J,K,L, & S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2016-01-26 | 1091 | 1216 | 1193 | 1181 | 44.1 | 4725.1 | 4500.75 | 224.35 | 4730 | 6.45 | 71.47 |  |  | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2016-01-27 | 968 | 1114 | 1079 | 1098 | 40.41 | 4299.41 | 4132.5 | 166.91 | 4350 | 5.85 | 72.47 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2016-01-28 | 995 | 1113 | 1086 | 1114 | 40.41 | 4348.41 | 4148.25 | 200.16 | 4370 | 5.97 | 71.34 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-15:06 to 15:12 | 25775460 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2016-01-29 | 899 | 1012 | 983 | 1021 | 38.08 | 3953.08 | 3758.25 | 194.83 | 3980 | 6.05 | 64.11 | Module cleaning done inverter - 2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-14:52 to 15:15 & Transformer P.M | 258770143 | 798 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2016-01-30 | 1068 | 1193 | 1210 | 1236 | 44.18 | 4751.18 | 4518 | 233.18 | 4770 | 6.34 | 73.33 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2016-01-31 | 1058 | 1187 | 1210 | 1223 | 43.45 | 4721.45 | 4527.75 | 193.7 | 4740 | 6.34 | 72.86 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2016-02-01 | 944 | 1069 | 1097 | 1079 | 39.2 | 4228.2 | 4014 | 214.2 | 4250 | 5.72 | 72.41 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2016-02-02 | 1006 | 1198 | 1164 | 1128 | 42.38 | 4538.38 | 4343.25 | 195.13 | 4560 | 6.04 | 73.58 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-16:38 to 16:47 | 25944632 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2016-02-03 | 1108 | 1271 | 1233 | 1193 | 44.49 | 4849.49 | 4593 | 256.49 | 4870 | 6.41 | 74.04 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2016-02-04 | 1199 | 1357 | 1317 | 1295 | 47.57 | 5215.57 | 5013.75 | 201.82 | 5220 | 6.92 | 73.52 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2016-02-05 | 1130 | 1278 | 1244 | 1256 | 44.6 | 4952.6 | 4732.5 | 220.1 | 4970 | 6.61 | 73.28 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2016-02-06 | 984 | 1198 | 1159 | 1194 | 44.34 | 4579.34 | 4385.25 | 194.09 | 4610 | 6.28 | 71.54 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Two Time Grid Failure From -7:55 to 8:13 & 8:20 to 8:45 & Inverter no-1 ABB 8:20 Auto trip D.C. Bracker of manual Auto reset inverter started 9:35 | 25946601 25946588 25946589 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2016-02-07 | 1080 | 1222 | 1210 | 1215 | 48.72 | 4775.72 | 4554.75 | 220.97 | 4790 | 6.34 | 73.63 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2016-02-08 | 1170 | 1323 | 1334 | 1296 | 50.01 | 5173.01 | 4920 | 253.01 | 5170 | 6.92 | 72.81 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2016-02-09 | 1086 | 1255 | 1260 | 1196 | 47.32 | 4844.32 | 4640.25 | 204.07 | 4860 | 6.43 | 73.66 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2016-02-10 | 1119 | 1323 | 1284 | 1220 | 48.16 | 4994.16 | 4780.5 | 213.66 | 5020 | 6.6 | 74.13 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-9:42 to 9:50 WO# | 25957936 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2016-02-11 | 1068 | 1255 | 1187 | 1133 | 44.37 | 4687.37 | 4446.75 | 240.62 | 4660 | 6.34 | 71.63 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-16:50 to 16:58 WO# | 25961555 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2016-02-12 | 1086 | 1221 | 1181 | 1145 | 44.53 | 4677.53 | 4463.25 | 214.28 | 4690 | 6.31 | 72.44 | Today I Replaced The 2 D.C.12Amp Fuse Link of The String- 03--tive in AJB-102 of The Inverter-4 & 07--tive AJB-104 Inverter NO-4 during The Period of 16:45 To 17:00.WO#() & Module cleaning done Inverter-4 Row ,G,H,I, & Total module cleaning 594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
44 | 2016-02-13 | 1091 | 1238 | 1205 | 1221 | 44.88 | 4799.88 | 4584.75 | 215.13 | 4810 | 6.34 | 73.94 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2016-02-14 | 1102 | 1238 | 1187 | 1225 | 46.5 | 4798.5 | 4590 | 208.5 | 4820 | 6.39 | 73.51 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2016-02-15 | 1080 | 1222 | 1181 | 1208 | 45.87 | 4736.87 | 4518 | 218.87 | 4750 | 6.3 | 73.48 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2016-02-16 | 911 | 1017 | 1024 | 981 | 38.14 | 3971.14 | 3783.75 | 187.39 | 3990 | 5.23 | 74.35 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2016-02-17 | 848 | 961 | 961 | 913 | 35.05 | 3718.05 | 3534 | 184.05 | 3740 | 4.91 | 74.24 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2016-02-18 | 915 | 1063 | 1035 | 982 | 38.43 | 4033.43 | 3851.25 | 182.18 | 4060 | 5.46 | 72.47 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2016-02-19 | 928 | 1035 | 1006 | 992 | 36.73 | 3997.73 | 3806.25 | 191.48 | 4020 | 5.35 | 73.23 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2016-02-20 | 802 | 893 | 865 | 890 | 31.53 | 3481.53 | 3307.5 | 174.03 | 3510 | 4.45 | 76.87 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Combiner P.M |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2016-02-21 | 865 | 978 | 950 | 976 | 35.83 | 3804.83 | 3633.75 | 171.08 | 3840 | 5.21 | 71.83 | Two time Grid Failure From-12:53 to 14:08 & 14:17 to 14:22WO# & SEEDS P.M | 25995899 25995901 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2016-02-22 | 1057 | 1193 | 1153 | 1205 | 44.54 | 4652.54 | 4444.5 | 208.04 | 4670 | 6.2 | 73.41 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2016-02-23 | 1216 | 1379 | 1379 | 1398 | 53.44 | 5425.44 | 5178.75 | 246.69 | 5430 | 7.25 | 72.99 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2016-02-24 | 1035 | 1176 | 1199 | 1165 | 45.15 | 4620.15 | 4417.5 | 202.65 | 4640 | 6.11 | 74.01 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2016-02-25 | 836 | 1086 | 1074 | 1042 | 40.93 | 4078.93 | 3900.75 | 178.18 | 4120 | 5.56 | 72.22 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Two Time Grid Failure From -7:50 to 8:20 & 11:20 to 8:27 & Inverter no-1 ABB 8:20 Auto trip D.C. Bracker of manual Auto 7:50 reset inverter started 9:28 | 26005473 26005832 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2016-02-26 | 1154 | 1328 | 1300 | 1278 | 48.86 | 5108.86 | 4884.75 | 224.11 | 5123 | 6.5 | 76.8181 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2016-02-27 | 1215 | 1385 | 1251 | 1353 | 51.49 | 5255.49 | 5109 | 146.49 | 5336 | 6.7 | 77.62 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2016-02-28 | 1176 | 1340 | 1312 | 1334 | 50.11 | 5212.11 | 4984.5 | 227.61 | 5230 | 6.95 | 73.34 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2016-02-29 | 1102 | 1261 | 1227 | 1251 | 47.46 | 4888.46 | 4641 | 247.46 | 4910 | 6.6 | 72.5 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-14:56 to 15:06 WO# | 26016220 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2016-03-01 | 781 | 1170 | 1159 | 1172 | 45.59 | 4327.59 | 4193.25 | 134.34 | 4210 | 5.6 | 0.73273 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From -10:01 to 10:09 & Inverter no-1 ABB 10::09 Auto trip D.C. Bracker of manual Auto reset inverter started 12:00 | 26018866 26015567 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2016-03-02 | 853 | 955 | 978 | 934 | 37.26 | 3757.26 | 3575.25 | 182.01 | 3930 | 5.31 | 0.72136 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2016-03-03 | 888 | 1012 | 961 | 1004 | 39.51 | 3904.51 | 3744 | 160.51 | 3920 | 5.34 | 71.54 | Inverter #3 didn’t wake up in the morning due to DC breaker tripped , this problem occur due to grid outage from 2:30am to 6:00am.Inverter started 9:14 & Module clean by rain | 26029140 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2016-03-04 | 1034 | 1122 | 1170 | 1159 | 46.3 | 4531.3 | 4384.5 | 146.8 | 4610 | 6.2 | 72.47 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2016-03-05 | 667 | 752 | 741 | 762 | 28.53 | 2950.53 | 2808.75 | 141.78 | 2990 | 3.96 | 73.59 | Module cleaning done Inverter-4 Row ,A,B,C,D,E, & Total module cleaning 630 & Grid Failure From-10:50 to 14:00 WO# | 26028652 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2016-03-06 | 1142 | 1312 | 1294 | 1341 | 56.01 | 5145.01 | 4924.5 | 220.51 | 5162 | 6.87 | 73.23 | Today I Replaced The D.C.12Amp Fuse Link of The String- 04--tive in AJB-105 of The Inverter-4 during The Period of 10:05 To 10:10.WO#() | 26030635 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
68 | 2016-03-07 | 1131 | 1294 | 1278 | 1333 | 58.28 | 5094.28 | 4872 | 222.28 | 5101 | 6.73 | 73.87 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2016-03-08 | 1176 | 1351 | 1234 | 1414 | 62.83 | 5237.83 | 5104.5 | 133.33 | 5353 | 7.15 | 72.96 | Module cleaning done Inverter-4 Row ,F,G,H, & Total module cleaning 594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2016-03-09 | 1114 | 1289 | 1275 | 1349 | 60.76 | 5087.76 | 4883.25 | 204.51 | 5130 | 6.91 | 72.35 | Module cleaning done inverter -4 & 3 Trackers Row- ,I,J,K,L, & ,S,T, & Total module cleaning -710 & Grid Failure From-10:48 to 10:53 |  | 710 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2016-03-10 | 1102 | 1272 | 1295 | 1335 | 59.55 | 5063.55 | 4869.75 | 193.8 | 5090 | 6.76 | 73.38 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-17:29 to 17:56 |  | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2016-03-11 | 1142 | 1368 | 1351 | 1360 | 65.41 | 5286.41 | 5055 | 231.41 | 5280 | 7.03 | 73.2 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2016-03-12 | 1035 | 1272 | 1249 | 1155 | 58.92 | 4769.92 | 4568.25 | 201.67 | 4875 |  |  | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Morning Time Grid Failure Inverter No-2,3,4, started 8:35 & Inverter No-1 started 9:20 (D.C. Bracker Auto trip) |  | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2016-03-13 | 1108 | 1261 | 1244 | 1248 | 59.43 | 4920.43 | 4700.25 | 220.18 | 4888 |  |  | Grid Failure From-11:07 to 11:11 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2016-03-14 | 1164 | 1371 | 1328 | 1366.88 | 64.24 | 5294.12 | 5079 | 215.12 | 5309 |  |  | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-7:26 to 7:51 & 11:20 to 11:30 | 26046664 26047323 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2016-03-15 | 978 | 1159 | 1142 | 1172 | 52.57 | 4503.57 | 4313.25 | 190.32 | 4520 | 6.1 | 72.22 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-09:05 to 9:51 | 260447572 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2016-03-16 | 1159 | 1300 | 1284 | 1380 | 61.65 | 5184.65 | 4949.25 | 235.4 | 5190 | 6.9 | 73.31 | Today I Replaced The D.C.12Amp Fuse Link of The String- 03++tive in AJB-101 of The Inverter-4 during The Period of 10:05 To 10:10 & Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 | 26049799 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
78 | 2016-03-17 | 1131 | 1278 | 1306 | 1368 | 60.54 | 5143.54 | 4920.75 | 222.79 | 5150 | 6.77 | 74.14 | Module cleaning done inverter -4 Row- ,G,H,I,, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2016-03-18 | 1148 | 1340 | 1339 | 1398 | 60.3 | 5285.3 | 5049 | 236.3 | 5290 | 6.88 | 74.94 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2016-03-19 | 1051 | 1204 | 1193 | 1243 | 52.04 | 4743.04 | 4544.25 | 198.79 | 4770 | 6.22 | 74.74 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-14:52 to 14:58 & 15:56 to 16:05 | 26066161 26066162 | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2016-03-20 | 1148 | 1317 | 1278 | 1338 | 58.38 | 5139.38 | 4920.75 | 218.63 | 5150 | 7.03 | 71.4 | Grid Failure From-13:46 to 13:52 & 16:08 to 16:30 | 26066355 26066361 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2016-03-21 | 1164 | 1334 | 1323 | 1335 | 54.54 | 5210.54 | 4984.5 | 226.04 | 5220 | 7.07 | 73.96 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2016-03-22 | 1216 | 1363 | 1340 | 1390 | 56.49 | 5365.49 | 5128.5 | 236.99 | 5370 | 7.28 | 71.89 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2016-03-23 | 916 | 1362 | 1345 | 1420 | 57.48 | 5100.48 | 4861.5 | 238.98 | 5110 | 7.48 | 66.58 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Inverter No-1 ABB (250 KW) Auto trip Err code- (8189) D.C. Bracker off 14:30 (inverter stoped) WO# | 26070546 | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2016-03-24 |  | 1295 | 1284 | 1354 | 54.19 | 3987.19 | 3783.75 | 203.44 | 4012 | 7.14 | 54.76 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2016-03-25 |  | 1080 | 1068 | 1156 | 42.41 | 3346.41 | 3191.5 | 154.91 | 3390 | 5.93 | 55.71 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-09:11 to 9:26 | 26071335 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2016-03-26 |  | 831 | 825 | 882 | 31.93 | 2569.93 | 2401.5 | 168.43 | 2610 | 4.45 | 57.16 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
88 | 2016-03-27 |  | 1148 | 1193 | 1326 | 48 | 3715 | 3531 | 184 | 3750 | 6.57 | 55.63 | Grid Failure From-08:52 to 09:10 & Inverter No-2 ABB 250 KW Trip -9:10 Auto Run Lost Reset Err Inverter started 9:37 | 26079827 26079828 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2016-03-28 |  | 1073 | 1063 | 1170 | 42.73 | 3348.73 | 3157.5 | 191.23 | 3380 | 5.77 | 57.09 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2016-03-29 | 181 | 854 | 1199 | 1333 | 48.32 | 3615.32 | 3474 | 141.32 | 3660 | 6.83 | 52.22 | Grid Failure From- 8:41 to 8:48 & 11:49 to 11:59 & Inverter No-2 ABB 250 KW Trip -9:40 Auto Run Lost Reset Err Inverter started 12:00 & Inverter No-1 ABB 250kw Resolved the issue change the R,D,I Card inverter started 15:10 | 26070546 26080565 26080994 26081477 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2016-03-30 | 1108 | 1233 | 1221 | 1345 | 49.05 | 4956.05 | 4714.5 | 241.55 | 4960 | 6.81 | 70.98 | no module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2016-03-31 | 995 | 1091 | 1079 | 1208 | 44.31 | 4417.31 | 4239.75 | 177.56 | 4440 | 6.12 | 70.71 | Module cleaning done Inverter-4 Row ,A,B,C,D,E, & Total module cleaning 630 & Grid Failure From-13:40 to 13:50 & 14:13 to 14:58 | 26087168 26087178 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2016-04-01 | 1040 | 1147 | 1137 | 1321 | 43.58 | 4688.58 | 4475.25 | 213.33 | 4700 | 6.32 | 72.48 | Module cleaning done inverter -4 Row- ,F,G,H, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2016-04-02 | 887 | 1063 | 1052 | 1263 | 40 | 4305 | 4117.5 | 187.5 | 4070 | 5.8 | 68.3942 | Module cleaning done inverter -4 & 3 Trackers Row- ,I,J,K,L, & ,S,T, & Total module cleaning -710 & Grid Failure From-08:00 to 08:13 & 10:04 to 10:13 & 12:09 to 12:15 & Inverter No-1 ABB (250 KW) Auto trip 08:13 Err code- (8189) D.C. Bracker off Inverter started 09:30 WO# | 26092349 26092348 26092355 | 710 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2016-04-03 | 984 | 1142 | 1130 | 1344 | 47.64 | 4647.64 | 4452 | 195.64 | 4950 | 6.3 | 76.5803 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2016-04-04 | 939 | 1024 | 1057 | 1211 | 43.54 | 4274.54 | 4080 | 194.54 | 4300 | 5.62 | 74.57 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-11:02 to 11:10 | 26098344 | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2016-04-05 | 1063 | 1170 | 1284 | 1373 | 49.52 | 4939.52 | 4712.25 | 227.27 | 4960 | 6.57 | 73.58 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 Grid Failure From-16:21 to 16:28 | 26099407 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2016-04-06 | 938 | 1074 | 1170 | 1239 | 43.21 | 4464.21 | 4319.25 | 144.96 | 4500 | 5.74 | 76.41 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-15:51 to 18:00 | 26100997 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2016-04-07 | 882 | 1068 | 1114 | 1150 | 41.05 | 4255.05 | 4060.5 | 194.55 | 4280 | 5.87 | 71.06 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-10:20 to 11:24 & 16:43 to 17:02 | 26101088 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2016-04-08 | 1097 | 1374 | 1351 | 1391 | 50.55 | 5263.55 | 5053.5 | 210.05 | 5270 | 6.71 | 76.54 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2016-04-09 | 1085 | 1346 | 1323 | 1371 | 51.5 | 5176.5 | 4937.25 | 239.25 | 5190 | 6.7 | 75.49 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-13:00 to 13:06 & D.O Fuse of "Y" phase blown at 17:18 pm, Fuse was replaced and plant started at 17:55 | 26108015 26110490 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2016-04-10 | 1119 | 1305 | 1283 | 1323 | 50.5 | 5080.5 | 4853.25 | 227.25 | 5090 | 6.52 | 76.08 | Grid Failure From-07:25 to 07:38 | 26110549 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2016-04-11 | 1227 | 1397 | 1368 | 1416 | 51.77 | 5459.77 | 5233.5 | 226.27 | 5460 | 6.87 | 77.46 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-17:58 to 19:24 |  | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2016-04-12 | 1159 | 1300 | 1278 | 1342 | 47.89 | 5126.89 | 4905 | 221.89 | 5150 | 6.55 | 76.63 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2016-04-13 | 1182 | 1323 | 1300 | 1393 | 49.32 | 5247.32 | 5037.75 | 209.57 | 5250 | 6.76 | 75.69 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2016-04-14 | 1181 | 1317 | 1295 | 1425 | 49.73 | 5267.73 | 4986 | 281.73 | 5280 | 6.74 | 76.35 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2016-04-15 | 1176 | 1323 | 1311 | 1444 | 51.76 | 5305.76 | 5133.75 | 172.01 | 5312 | 6.75 | 0.76702 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & L.T. Panal P.M |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2016-04-16 | 1114 | 1244 | 1267 | 1348 | 49.03 | 5022.03 | 4794.75 | 227.28 | 5030 | 6.45 | 0.76008 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2016-04-17 | 1063 | 1176 | 1215 | 1289 | 46.48 | 4789.48 | 4574.25 | 215.23 | 4822 | 6.13 | 0.76669 | Grid Failure From- 13:26 to 13:33 & 13:40 & 13:49 & 16:10 to 16:15 | 26126850 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2016-04-18 | 1097 | 1272 | 1295 | 1365 | 48.97 | 5077.97 | 4866.75 | 211.22 | 5100 | 6.39 | 0.7779 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & A,B, & Total module cleaning -498 & Grid Failure From-08:52 to 9:05 | 26126929 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2016-04-19 | 1136 | 1340 | 1328 | 1391 | 50.41 | 5245.41 | 5025.75 | 219.66 | 5263 | 6.58 | 0.77958 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2016-04-20 | 1159 | 1345 | 1318 | 1377 | 49.97 | 5248.97 | 5031.75 | 217.22 | 5253 | 6.47 | 0.79133 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2016-04-21 | 1232 | 1397 | 1339 | 1433 | 52.55 | 5453.55 | 5220 | 233.55 | 5463 | 6.99 | 0.76174 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2016-04-22 | 1210 | 1362 | 1318 | 1432 | 51.81 | 5373.81 | 5139.75 | 234.06 | 5400 | 6.11 | 0.8614 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2016-04-23 | 1125 | 1261 | 1210 | 1344 | 47.01 | 4987.01 | 4778.25 | 208.76 | 5000 | 6.5 | 0.74974 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-17:17 to 17:27 | 26139894 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2016-04-24 | 1137 | 1278 | 1226 | 1369 | 47.48 | 5057.48 | 4828.5 | 228.98 | 5060 | 6.57 | 0.75065 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2016-04-25 | 983 | 1096 | 1069 | 1173 | 43.2 | 4364.2 | 4178.25 | 185.95 | 4390 | 5.87 | 0.72892 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Grid Failure From-09:22 to 09:32 | 26144105 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2016-04-26 | 645 | 713 | 695 | 762 | 25.64 | 2840.64 | 2684.25 | 156.39 | 2870 | 3.6 | 0.77702 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2016-04-27 | 1142 | 1300 | 1212 | 1409 | 52.5 | 5115.5 | 4977.75 | 137.75 | 5230 | 6.77 | 0.75295 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Grid Failure From-09:40 to 09:45 | 26146070 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2016-04-28 | 1079 | 1238 | 1372 | 1323 | 49.13 | 5061.13 | 4758 | 303.13 | 4990 | 6.5 | 0.74824 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-17:10 to 17:53 & Today I Replaced The D.C.12Amp Fuse Link of The String- 05++tive in AJB-117 of The Inverter-3 during The Period of 10:35 To 10:40 | 26147097 26147351 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
122 | 2016-04-29 | 1086 | 1283 | 1283 | 1298 | 49.3 | 4999.3 | 4803 | 196.3 | 5004 | 6.55 | 0.74461 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Today I Replaced The D.C.12Amp Fuse Link of The String- 01--tive in AJB-101 of The Inverter-1 during The Period of 18:35 To 18:40 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
123 | 2016-04-30 | 1102 | 1295 | 1266 | 1294 | 49.18 | 5006.18 | 4779 | 227.18 | 5012 | 6.61 | 0.73903 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2016-05-01 | 1108 | 1278 | 1260 | 1297 | 48.71 | 4991.71 | 4782 | 209.71 | 5010 | 6.57 | 0.74323 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2016-05-02 | 922 | 1080 | 1065 | 1090 | 37 | 4194 | 3991.5 | 202.5 | 4210 | 5.65 | 0.72625 | Module clean by Rain & Grid Failure From-17:55 to 22:20 | 26160730 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2016-05-03 | 1010 | 1300 | 1290 | 1350 | 50.37 | 5000.37 | 4831.5 | 168.87 | 5014 | 6.93 | 0.70519 | Inverter No-1 ABB (250 KW) Morning time not wake up Err code- (8189) D.C. Bracker off Inverter started 09:15 & Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 | 26160727 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2016-05-04 | 945 | 1052 | 1051 | 1118 | 40.14 | 4206.14 | 4005.75 | 200.39 | 4220 | 5.58 | 0.73711 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-17:55 to 18:05 |  | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2016-05-05 | 887 | 995 | 989 | 1020 | 38.12 | 3929.12 | 3747.75 | 181.37 | 3950 | 5.56 | 0.69243 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2016-05-06 | 1012 | 1136 | 1131 | 1264 | 45.37 | 4588.37 | 4426.5 | 161.87 | 4610 | 6.44 | 0.6977 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From-14:37 to 14:42 |  | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2016-05-07 | 989 | 1109 | 1108 | 1253 | 43.13 | 4502.13 | 4293.75 | 208.38 | 4523 | 6.13 | 0.71915 | Grid Failure From-17:27 to 17:43 & Today I Replaced The D.C.12Amp Fuse Link of The String- 04--tive in AJB-105 of The Inverter-4 during The Period of 10:10 To 10:15 | 26175697 26169117 |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
132 | 2016-05-08 | 967 | 1085 | 1074 | 1242 | 43.1 | 4411.1 | 4206 | 205.1 | 4440 | 6.3 | 0.6869 | Grid Failure From-08:47 to 09:14 | 26175729 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2016-05-09 | 984 | 1108 | 1103 | 1236 | 43.69 | 4474.69 | 4330.5 | 144.19 | 4530 | 6.29 | 0.70194 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Grid Failure From-17:35 to 17:45 | 26178351 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2016-05-10 | 989 | 1108 | 1102 | 1295 | 46.86 | 4540.86 | 4329.75 | 211.11 | 4560 | 6.28 | 0.70771 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2016-05-11 | 1001 | 1131 | 1182 | 1317 | 48.15 | 4679.15 | 4482.75 | 196.4 | 4691 | 6.34 | 0.72116 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2016-05-12 | 1012 | 1142 | 1261 | 1325 | 48.83 | 4788.83 | 4581.75 | 207.08 | 4800 | 6.44 | 0.72645 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2016-05-13 | 1023 | 1210 | 1288 | 1330 | 50.31 | 4901.31 | 4713 | 188.31 | 4910 | 6.51 | 0.73511 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2016-05-14 | 1063 | 1283 | 1307 | 1372 | 51.11 | 5076.11 | 4850.25 | 225.86 |  |  |  | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2016-05-15 | 1029 | 1283 | 1272 | 1334 | 49.7 | 4967.7 | 4760.25 | 207.45 |  |  |  | Grid Failure From -12:43 to 12:52 | 26187259 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2016-05-16 | 1029 | 1272 | 1260 | 1321 | 48.55 | 4930.55 | 4723.5 | 207.05 |  |  |  | no module cleaning & No any issue |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2016-05-17 | 1046 | 1227 | 1216 | 1269 | 46.7 | 4804.7 | 4568.25 | 236.45 |  |  |  | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2016-05-18 | 1108 | 1221 | 1209 | 1263 | 46.94 | 4847.94 | 4671.75 | 176.19 |  |  |  | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Array P.M (750 kw PolyCrystallin side) |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2016-05-19 | 1108 | 1215 | 1199 | 1284 | 46.36 | 4852.36 | 4600.5 | 251.86 |  |  |  | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Array P.M (250 Kw Thinfilm side) |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2016-05-20 | 1103 | 1210 | 1199 | 1320 | 45.86 | 4877.86 | 4689 | 188.86 |  |  |  | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Combiner P.M (750 kw PolyCrystallin side) |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2016-05-21 | 955 | 1035 | 1023 | 1173 | 40.77 | 4226.77 | 4044 | 182.77 |  |  |  | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Grid Failure From-14:55 to 16:21 & Combiner P.M (250 Kw Thinfilm side) | 26201454 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2016-05-22 | 933 | 1012 | 1012 | 1140 | 41.43 | 4138.43 | 3957.75 | 180.68 |  |  |  | Grid Failure From-10:32 to 10:41 & 14:15 to 14:55 | 26201531 26201620 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2016-05-23 | 1085 | 1193 | 1210 | 1325 | 50.71 | 4863.71 | 4670 | 193.71 |  |  |  | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 & Grid Failure From-16:28 to 10:35 | 26203336 | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2016-05-24 | 1041 | 1159 | 1204 | 1281 | 48.31 | 4733.31 | 4514.25 | 219.06 | 4740 |  |  | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Cloudy day |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
149 | 2016-05-25 | 938 | 1080 | 1085 | 1140 | 42.28 | 4285.28 | 4093.5 | 191.78 | 4300 | 5.67 | 0.73916 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Cloudy day |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
150 | 2016-05-26 | 905 | 1012 | 1012 | 1060 | 40.04 | 4029.04 | 3846 | 183.04 | 4050 | 5.5 | 0.7177 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Grid Failure From-12:54 to 13:08 & Cloudy day | 26213053 | 612 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
151 | 2016-05-27 | 983 | 1096 | 1091 | 1191 | 46.14 | 4407.14 | 4201.5 | 205.64 | 4420 | 6.44 | 0.66894 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From- 12:25 to 12:55 & Cloudy day | 26213473 | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
152 | 2016-05-28 | 990 | 1103 | 1097 | 1177 | 44.57 | 4411.57 | 4206 | 205.57 | 4420 | 6 | 0.718 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Cloudy day |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
153 | 2016-05-29 | 1023 | 1136 | 1136 | 1220 | 47.08 | 4562.08 | 4363.5 | 198.58 | 4571 | 6.2 | 0.71858 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
154 | 2016-05-30 | 1063 | 1182 | 1193 | 1293 | 52.67 | 4783.67 | 4586.25 | 197.42 | 4794 | 6.48 | 0.72107 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Cloudy day |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
155 | 2016-05-31 | 1028 | 1159 | 1188 | 1258 | 52.37 | 4685.37 | 4465.5 | 219.87 | 4690 | 6.34 | 0.721 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Cloudy day |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
157 | 2016-06-01 | 1086 | 1215 | 1243 | 1335 | 55.69 | 4934.69 | 4719.75 | 214.94 | 4951 | 6.67 | 0.72347 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2016-06-02 | 1063 | 1193 | 1216 | 1303 | 54.13 | 4829.13 | 4645.5 | 183.63 | 4860 | 6.59 | 0.71879 | Grid Failure From-17:28 to 17:33 | 26228906 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2016-06-03 | 1097 | 1249 | 1272 | 1348 | 56.68 | 5022.68 | 4809.75 | 212.93 | 5020 | 6.75 | 0.72486 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D,& A,B, & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2016-06-04 | 1097 | 1278 | 1260 | 1348 | 64.63 | 5047.63 | 4860.75 | 186.88 | 5080 | 6.85 | 0.72281 | Module cleaning done inverter -4 Row- ,C,D,E,F, & Total module cleaning -630 & Grid Failure From-15:26 to 15:31 | 26236085 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2016-06-05 | 1102 | 1289 | 1273 | 1337 | 64.04 | 5065.04 | 4821 | 244.04 | 5050 | 6.82 | 0.7217 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2016-06-06 | 1097 | 1272 | 1249 | 1317 | 64.13 | 4999.13 | 4806 | 193.13 | 5011 | 6.66 | 0.73334 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2016-06-07 | 831 | 922 | 746 | 967 | 49.18 | 3515.18 | 3378.75 | 136.43 | 3540 | 5.71 | 0.60425 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Grid Failure From-09:55 to 11:58 & Inverter No- 3 morning time not wake up Reset Err code (Emergency stop) Inverter started 9:30 | 26237681 26237680 | 612 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2016-06-08 | 864 | 994 | 967 | 1089 | 44.94 | 3958.94 | 3747.75 | 211.19 | 3980 | 5.35 | 0.72507 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Grid Failure From- 07:00 to 10:05 | 26239070 | 765 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2016-06-09 | 1063 | 1176 | 1159 | 1299 | 52.43 | 4749.43 | 4552.5 | 196.93 | 4751 | 6.33 | 0.73153 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2016-06-10 | 752 | 843 | 825 | 930 | 30.92 | 3380.92 | 3231 | 149.92 | 3400 | 4.58 | 0.72355 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Cloudy day & Grid Failure From-06:53 to 07:55 | 26241421 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
167 | 2016-06-11 | 780 | 859 | 876 | 936 | 33.16 | 3484.16 | 3333 | 151.16 | 3520 | 4.63 | 0.74099 | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Cloudy day & Grid Failure From-13:10 to 13:24 | 26246410 | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
168 | 2016-06-12 | 996 | 1108 | 1137 | 1180 | 46.25 | 4467.25 | 4297.5 | 169.75 | 4481 | 5.91 | 0.73899 | Grid Failure From-14:20 to 14:27 & Cloudy day | 26247134 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
169 | 2016-06-13 | 943 | 1052 | 1080 | 1117 | 43.45 | 4235.45 | 4004.25 | 231.2 | 4250 | 5.57 | 0.74368 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
170 | 2016-06-14 | 803 | 898 | 893 | 937 | 33.41 | 3564.41 | 3422.25 | 142.16 | 3600 | 4.64 | 0.7562 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
171 | 2016-06-15 | 961 | 1086 | 1074 | 1108 | 42.74 | 4271.74 | 4060.5 | 211.24 | 4280 | 5.55 | 0.75163 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
172 | 2016-06-16 | 945 | 1063 | 1052 | 1071 | 37.36 | 4168.36 | 3859.5 | 308.86 | 4190 | 5.4 | 0.75626 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
173 | 2016-06-17 | 961 | 1085 | 1074 | 1108 | 41.87 | 4269.87 | 4083 | 186.87 | 4270 | 5.55 | 0.74987 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
174 | 2016-06-18 | 1045 | 1187 | 1181 | 1216 | 47.29 | 4676.29 | 4470 | 206.29 | 4690 | 6.09 | 0.7506 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
175 | 2016-06-19 | 543 | 605 | 594 | 602 | 17.89 | 2361.89 | 2218.5 | 143.39 | 2390 | 3.08 | 0.75631 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
176 | 2016-06-20 | 820 | 911 | 916 | 959 | 29.14 | 3635.14 | 3501 | 134.14 | 3640 | 4.77 | 0.74376 | Grid Failure From-15:48 to 16:10 & Cloudy day | 26285676 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
177 | 2016-06-21 | 447 | 491 | 446 | 506 | 15.2 | 1905.2 | 1858 | 47.2 | 1940 | 2.61 | 0.72446 | Module cleaning done inverter -1 & 4 Row- ,A,B,C,D, & ,A,B,C,D,E,F, & Total module cleaning -1158 & Grid Failure From-09:45 to 13:10 & Cloudy day | 26285801 | 1158 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
178 | 2016-06-22 | 164 | 181 | 170 | 215 | 5.9 | 735.9 | 679.5 | 56.4 | 805 | 1.1 | 0.71327 | Module cleaning done inverter -4 Row- ,G,H,I, & Total module cleaning -594 & Grid Failure From-07:45 to 13:45 & 15:35 to 15:40 & 16:48 to 16:54 & Cloudy day | 26286960 26290185 | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
179 | 2016-06-23 | 887 | 990 | 989 | 1051 | 33.14 | 3950.14 | 3613.5 | 336.64 | 3960 | 4.6 | 0.83905 | Module cleaning done inverter -4 & 3 Trackers Row- ,J,K,L, & ,S,T, & Total module cleaning -612 & Cloudy day |  | 612 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
180 | 2016-06-24 | 860 | 961 | 973 | 1026 | 29.09 | 3849.09 | 3841.5 | 7.59 | 3870 | 4.5 | 0.83821 | Module cleaning done inverter -3 Row- ,N,O,P,Q,R, & Total module cleaning -756 & Cloudy day |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
181 | 2016-06-25 | 859 | 961 | 961 | 1021 | 31.37 | 3833.37 | 3632.25 | 201.12 | 3840 | 4.4 | 85.0611 | Module cleaning done inverter -3 & 2 Row- ,K,L,M, & Total module cleaning -777 & Cloudy day |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
182 | 2016-06-26 | 814 | 904 | 898 | 936 | 28.5 | 3580.5 | 3411.75 | 168.75 |  |  |  | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
183 | 2016-06-27 | 938 | 1046 | 1041 | 1081 | 30.4 | 4136.4 | 3948.75 | 187.65 |  |  |  | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Cloudy day |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
184 | 2016-06-28 | 928 | 1029 | 1023 | 1116 | 33.09 | 4129.09 | 3960 | 169.09 |  |  |  | Module cleaning done inverter -1 Row- ,E,F,G, & Total module cleaning -546 & Cloudy day & Grid Failure From-18:10 to 18:27 |  | 546 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
185 | 2016-06-29 | 469 | 515 | 515 | 536 | 14.46 | 2049.46 | 1975.5 | 73.96 |  |  |  | Module cleaning By Rain & Grid Failure From-13:20 to 13:42 | 26312420 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 2016-06-30 | 582 | 633 | 633 | 655 | 17.92 | 2520.92 | 2324.25 | 196.67 |  |  |  | Module cleaning done inverter - 4 Row- A,B,C,D,E,F, & Total module cleaning -792 & Grid Failure From-17:43 to 17:50 & Cloudy day | 26312801 | 792 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
188 | 2016-07-01 | 803 | 887 | 882 | 957 | 29.42 | 3558.42 | 3445.5 | 112.92 |  |  |  | Cloudy day & Grid Failure From-16:42 to 16:45 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
189 | 2016-07-02 | 616 | 673 | 667 | 724 | 21.3 | 2701.3 | 2519.25 | 182.05 |  |  |  | Module cleaning By Rain & Grid Failure From-11:40 to 12:25 | 26340427 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2016-07-03 | 769 | 860 | 848 | 914 | 28.11 | 3419.11 | 3290.25 | 128.86 |  |  |  | Module cleaning By Rain & Grid Failure From-16:53 to 18:03 |  | 26321795 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2016-07-04 | 147 | 158 | 164 | 182 | 4.78 | 655.78 | 580.5 | 75.28 |  |  |  | Module cleaning By Rain & Grid Failure From-10:26 to 11:22 & 11:40 to 13:20 & 15:00 to 16:42 | 26321972 26322069 26322087 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2016-07-05 | 983 | 1096 | 1096 | 1151 | 33.23 | 4359.23 | 4129.5 | 229.73 |  |  |  | Module cleaning By Rain |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 2016-07-06 | 888 | 984 | 984 | 1025 | 29.51 | 3910.51 | 3729 | 181.51 |  |  |  | Module cleaning By Rain |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2016-07-07 | 786 | 871 | 871 | 897 | 27.33 | 3452.33 | 3311.25 | 141.08 |  |  |  | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
195 | 2016-07-08 | 729 | 808 | 808 | 835 | 25.33 | 3205.33 | 3032.25 | 173.08 |  |  |  | Module cleaning By Rain |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 2016-07-09 | 441 | 469 | 475 | 482 | 13.55 | 1880.55 | 1762.5 | 118.05 |  |  |  | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
197 | 2016-07-10 | 447 | 492 | 486 | 500 | 14.01 | 1939.01 | 1807.5 | 131.51 |  |  |  | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
198 | 2016-07-11 | 599 | 650 | 656 | 678 | 19.37 | 2602.37 | 2465.25 | 137.12 |  |  |  | Module cleaning By Rain & Today I Replaced The D.C.12Amp Fuse Link of The String- 07++tive in AJB-100 of The Inverter-4 during The Period of 10:00 To 10:10 | 26333796 |  | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
199 | 2016-07-12 | 226 | 244 | 243 | 232 | 6.14 | 951.14 | 833 | 118.14 |  |  |  | Module cleaning By Rain & Grid Failure From-12:44 to 12:53 | 26335963 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 2016-07-13 | 272 | 294 | 283 | 0 | 8.02 | 857.02 | 738.75 | 118.27 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 2016-07-14 | 814 | 910 | 876 | 0 | 23.64 | 2623.64 | 2484.75 | 138.89 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 2016-07-15 | 814 | 921 | 922 | 0 | 26.99 | 2683.99 | 2533.5 | 150.49 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 2016-07-16 | 548 | 605 | 610 | 0 | 17.93 | 1780.93 | 1675.5 | 105.43 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-17:53 to 18:03 | 26336217 26339370 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 2016-07-17 | 600 | 667 | 515 | 0 | 21.22 | 1803.22 | 1703.25 | 99.97 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-12:13 to 12:28 & 17:40 to 17:50 & Inverter no-3 ABB 250KW Auto trip 14:25 Err code D14 ALM (108A) Reset Err code Inverter started-15:08 | 26336217 26343266 26343722 26344456 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2016-07-18 | 785 | 865 | 865 | 0 | 27.63 | 2542.63 | 2380 | 162.63 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-17:25 to 17:35 | 26336217 26347162 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 2016-07-19 | 645 | 701 | 611 | 0 | 22.02 | 1979.02 | 1964 | 15.02 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:02 Err code D14 ALM (108A) Reset Err code Inverter started-13:50 | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 2016-07-20 | 798 | 877 | 972 | 0 | 28.34 | 2675.34 | 2410 | 265.34 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 2016-07-21 | 745 | 814 | 814 | 0 | 25.87 | 2398.87 | 2267 | 131.87 |  |  |  | Module clean By Rain & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-09:59 to 10:32 | 26336217 26350357 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 2016-07-22 | 854 | 944 | 949 | 0 | 30.83 | 2777.83 | 2680 | 97.83 |  |  |  | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-06:15 to 06:25 & 14:15 to 14:20 | 26336217 26350606 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
210 | 2016-07-23 | 944 | 1046 | 1029 | 0 | 33.55 | 3052.55 | 2900 | 152.55 |  |  |  | Cloudy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:30 Err code D14 ALM (108A) Reset Err code Inverter started-13:45 & Grid Failure From-18:38 to 19:25 | 26336217 26351121 26354403 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
211 | 2016-07-24 | 791 | 876 | 882 | 0 | 28.46 | 2577.46 | 2474 | 103.46 |  |  |  | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
212 | 2016-07-25 | 368 | 390 | 390 | 0 | 11.27 | 1159.27 | 1043 | 116.27 |  |  |  | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-10:44 to 10:55 | 26336217 26358319 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
213 | 2016-07-26 | 752 | 831 | 803 | 0 | 26.26 | 2412.26 | 2274 | 138.26 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:30 Err code D14 ALM (108A) Reset Err code Inverter started-13:45 | 26336217 26364369 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
214 | 2016-07-27 | 379 | 390 | 407 | 0 | 12.24 | 1188.24 | 1105.5 | 82.74 |  |  |  | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
215 | 2016-07-28 | 407 | 441 | 221 | 0 | 12.59 | 1081.59 | 963 | 118.59 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip 13:30 Err code D14 ALM (108A) Inverter steel sut Down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
216 | 2016-07-29 | 644 | 701 | 333 | 0 | 21.86 | 1699.86 | 1585.5 | 114.36 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Morning time wake up & than Auto trip 13:30 Err code D14 ALM (108A) Inverter steel sut Down & Transformer P.M | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
217 | 2016-07-30 | 780 | 865 | 0 | 0 | 26.73 | 1671.73 | 1552.5 | 119.23 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW Auto trip Err code D14 ALM (108A) Inverter steel sut Down & Inverters Filter cleaning (1,2,3,4,) | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
218 | 2016-07-31 | 729 | 803 | 764 | 0 | 24.82 | 2320.82 | 2210 | 110.82 |  |  |  | Cloudy & Rainy Day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Inverter no-3 ABB 250KW By Pass Inverter realy morning time Auto start Resolve Err code D14 ALM (108A) | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
220 | 2016-08-01 | 747 | 815 | 808 | 0 | 25.02 | 2395.02 | 2262.75 | 132.27 | 2345 | 3.9 | 58.6045 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Inverter steel sut down & Grid Failure From-15:45 to 16:19 | 26336217 26376332 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
221 | 2016-08-02 | 441 | 474 | 486 | 0 | 14.04 | 1415.04 | 1314.75 | 100.29 | 1440 | 1.56 | 0.89969 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
222 | 2016-08-03 | 265 | 283 | 294 | 0 | 7.71 | 849.71 | 739.5 | 110.21 | 865 | 0.999 | 0.84392 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
223 | 2016-08-04 | 781 | 859 | 871 | 0 | 28.56 | 2539.56 | 2403 | 136.56 | 2584 | 4.1 | 61.4273 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
224 | 2016-08-05 | 650 | 712 | 729 | 0 | 21.8 | 2112.8 | 2017.5 | 95.3 | 2142 | 3.86 | 0.54086 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:40 to 15:50 WO# | 26336217 26380329 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
225 | 2016-08-06 | 282 | 300 | 311 | 0 | 8.7 | 901.7 | 840 | 61.7 | 930 | 1.57 | 0.57735 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:15 to 16:37 WO# | 26336217 26386258 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
226 | 2016-08-07 | 374 | 401 | 413 | 0 | 11.77 | 1199.77 | 1088.25 | 111.52 | 1211 | 2 | 0.59016 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
227 | 2016-08-08 | 288 | 317 | 322 | 0 | 9.15 | 936.15 | 846.75 | 89.4 | 985 | 1.32 | 0.7273 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:30 to 08:50 WO# | 26336217 26389343 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
228 | 2016-08-09 | 305 | 328 | 333 | 0 | 9.33 | 975.33 | 873.75 | 101.58 | 984 | 1.31 | 0.73211 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
229 | 2016-08-10 | 221 | 240 | 244 | 0 | 6.7 | 711.7 | 624 | 87.7 | 755 | 1.29 | 0.57044 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From- 11:07 to 11:10 WO# | 26336217 26394284 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
230 | 2016-08-11 | 379 | 415 | 435 | 0 | 13.16 | 1242.16 | 1159.5 | 82.66 | 1295 | 2.3 | 0.54878 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-09:30 to 09:55 & 16:10 to 16:40 WO# | 26336217 26394870 26394898 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
231 | 2016-08-12 | 638 | 702 | 718 | 0 | 22.54 | 2080.54 | 1965 | 115.54 | 2102 | 3.66 | 0.55976 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-10:27 to 10:36 WO# | 26336217 26394967 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
232 | 2016-08-13 | 752 | 825 | 842 | 0 | 26.7 | 2445.7 | 2301.75 | 143.95 | 2455 | 4.24 | 0.56434 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:26 to 16:33 WO# | 26336217 26399788 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
233 | 2016-08-14 | 933 | 1034 | 1052 | 0 | 35.42 | 3054.42 | 2918.25 | 136.17 | 3064 | 5.29 | 0.56453 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & G.O.D, Swich ,B, Phase Luge rusted so Replace New Luge | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
234 | 2016-08-15 | 769 | 854 | 859 | 0 | 26.88 | 2508.88 | 2383.5 | 125.38 | 2520 | 4.47 | 0.54947 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Today I Replaced The D.C.12Amp Fuse Link of The String- 05---tive in AJB-107 of The Inverter-2 during The Period of 10:00 To 10:05 | 26336217 26400127 |  | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
235 | 2016-08-16 | 729 | 814 | 809 | 0 | 26.4 | 2378.4 | 2270.25 | 108.15 | 2413 | 4.21 | 0.55863 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:38 to 16:48 & 17:35 to 17:40 WO# | 26336217 26407752 26407754 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
236 | 2016-08-17 | 916 | 1029 | 1028 | 0 | 33.63 | 3006.63 | 2862.75 | 143.88 | 3043 | 5.52 | 0.5373 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
237 | 2016-08-18 | 933 | 1052 | 1052 | 0 | 34.43 | 3071.43 | 2928.75 | 142.68 | 3093 | 5.67 | 0.53168 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:25 to 15:36 WO# | 26336217 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
238 | 2016-08-19 | 548 | 610 | 611 | 0 | 19.64 | 1788.64 | 1694.25 | 94.39 | 1822 | 3.1 | 0.57285 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
239 | 2016-08-20 | 249 | 272 | 277 | 0 | 7.77 | 805.77 | 717 | 88.77 | 835 | 1.42 | 0.57313 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:22 to 16:28 WO# & Combiner P.M | 26336217 26413413 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
240 | 2016-08-21 | 322 | 361 | 367 | 0 | 10.8 | 1060.8 | 978 | 82.8 | 1100 | 1.85 | 0.57953 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:44 to 07:52 WO# & SEEDS P.M | 26336217 26413466 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
241 | 2016-08-22 | 520 | 577 | 582 | 0 | 18.57 | 1697.57 | 1595 | 102.57 | 1731 | 3 | 0.56238 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:58 to 08:11 & 18:06 to 18:24 WO# | 26336217 26413842 26414448 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
242 | 2016-08-23 | 159 | 181 | 181 | 0 | 4.88 | 525.88 | 455.25 | 70.63 | 558 | 0.981 | 0.55439 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
243 | 2016-08-24 | 294 | 333 | 340 | 0 | 9.32 | 976.32 | 873 | 103.32 | 996 | 1.64 | 0.59193 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
244 | 2016-08-25 | 407 | 481 | 480 | 0 | 16.16 | 1384.16 | 1280 | 104.16 | 1422 | 2.49 | 0.55661 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
245 | 2016-08-26 | 554 | 616 | 622 | 0 | 18.03 | 1810.03 | 1682.25 | 127.78 | 1833 | 3.15 | 0.56716 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
246 | 2016-08-27 | 825 | 939 | 927 | 0 | 30.29 | 2721.29 | 2566.5 | 154.79 | 2733 | 5.01 | 0.53169 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
247 | 2016-08-28 | 464 | 526 | 532 | 0 | 16.98 | 1538.98 | 1443 | 95.98 | 1562 | 2.78 | 0.54763 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-12:28 to 13:28 WO# | 26336217 26431636 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
248 | 2016-08-29 | 627 | 706 | 706 | 0 | 21.57 | 2060.57 | 1961.25 | 99.32 | 2093 | 3.5 | 0.58285 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-12:58 to 13:05 WO# | 26336217 26431958 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
249 | 2016-08-30 | 436 | 499 | 492 | 0 | 17.24 | 1444.24 | 1360 | 84.24 | 1492 | 2.8 | 0.51935 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-10:22 to 10:59 & 13:59 to 15:48 WO# | 26336217 26433094 26435469 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
250 | 2016-08-31 | 548 | 616 | 616 | 0 | 19.03 | 1799.03 | 1679.25 | 119.78 | 1822 | 3.11 | 0.57101 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
252 | 2016-09-01 | 701 | 792 | 792 | 0 | 26.2 | 2311.2 | 2194 | 117.2 | 2341 | 4.05 | 0.56338 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
253 | 2016-09-02 | 808 | 915 | 910 | 0 | 30 | 2663 | 2509.5 | 153.5 | 2672 | 4.81 | 0.54143 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
254 | 2016-09-03 | 1018 | 1148 | 803 | 0 | 38.21 | 3007.21 | 2873.25 | 133.96 | 3030 | 6.2 | 0.47633 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Inverter No-3 ABB 250 KW Morning time note wake up Err code- Emergency stop satemaster Relay By pass Inverter started 11:25 WO# | 26336217 26440841 |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
255 | 2016-09-04 | 1012 | 1136 | 1136 | 0 | 38.49 | 3322.49 | 3173.25 | 149.24 | 3342 | 6.12 | 0.53224 | cloudy & Rainy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:20 to 15:30 WO# | 26336217 26445915 |  | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
256 | 2016-09-05 | 910 | 1029 | 1023 | 0 | 34.71 | 2996.71 | 2853 | 143.71 | 3010 | 5.5 | 0.5334 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
257 | 2016-09-06 | 809 | 910 | 911 | 0 | 39.41 | 2669.41 | 2559 | 110.41 | 2688 | 4.98 | 0.52608 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:33 to 09:12 & 17:15 to 17:49 & 18:10 to 18:17 WO# | 26336217 26446442 26449700 26449709 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
258 | 2016-09-07 | 819 | 922 | 910 | 0 | 32.29 | 2683.29 | 2560.5 | 122.79 | 2694 | 4.89 | 0.53696 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-13:26 to 14:11 & 15:12 to 15:21 WO# | 26336217 26450567 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
259 | 2016-09-08 | 950 | 1080 | 1074 | 0 | 34.87 | 3138.87 | 3000 | 138.87 | 3150 | 5.7 | 0.53863 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
260 | 2016-09-09 | 996 | 1136 | 1125 | 0 | 37.17 | 3294.17 | 3154.5 | 139.67 | 3320 | 6.12 | 0.52874 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:53 to 17:01 WO# | 26336217 26453610 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
261 | 2016-09-10 | 887 | 1001 | 1001 | 0 | 32.47 | 2921.47 | 2791.5 | 129.97 | 2941 | 5.39 | 0.53181 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
262 | 2016-09-11 | 966 | 1085 | 1068 | 0 | 35.44 | 3154.44 | 3005.25 | 149.19 | 3160 | 5.94 | 0.51851 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
263 | 2016-09-12 | 967 | 1086 | 1086 | 0 | 37.48 | 3176.48 | 3029.25 | 147.23 | 3192 | 5.99 | 0.51938 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
264 | 2016-09-13 | 1040 | 1179 | 1193 | 0 | 38.91 | 3450.91 | 3294 | 156.91 | 3462 | 6.41 | 0.52641 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
265 | 2016-09-14 | 1041 | 1184 | 1187 | 0 | 39.52 | 3451.52 | 3300.75 | 150.77 | 3465 | 6.4 | 0.52769 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
266 | 2016-09-15 | 983 | 1119 | 1119 | 0 | 38.39 | 3259.39 | 3126 | 133.39 | 3302 | 6.19 | 0.51992 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-11:50 to 11:56 & 13:16 to 13:25 & 16:00 to 16:12 WO# | 26336217 26460513 26466933 26469676 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
267 | 2016-09-16 | 741 | 814 | 837 | 0 | 29.13 | 2421.13 | 2332.5 | 88.63 | 2662 | 4.54 | 0.57149 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-10:08 to 10:17 & 12:58 to 13:07 WO# | 26336217 26469738 26472264 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
268 | 2016-09-17 | 786 | 865 | 887 | 0 | 30.86 | 2568.86 | 2464.5 | 104.36 | 2582 | 4.8 | 0.52429 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-09:05 to 09:10 WO# | 26336217 26472456 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
269 | 2016-09-18 | 327 | 356 | 362 | 0 | 10.67 | 1055.67 | 988.5 | 67.17 | 1102 | 1.86 | 0.57746 | Today I Replaced The D.C.12Amp Fuse Link of The String-08++tive in AJB-108 of The Inverter-2 during The Period of 11:00 To 11:10 & Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:37 to 07:42 & 16:20 to 16:37 & 18:10 to 18:30 WO# | 26336217 26476746 26476871 26476897 26476906 |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
270 | 2016-09-19 | 555 | 617 | 616 | 0 | 19.23 | 1807.23 | 1698 | 109.23 | 1832 | 3.15 | 0.56685 | Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:18 to 07:23 WO# | 26336217 26476946 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
271 | 2016-09-20 | 983 | 1113 | 1108 | 0 | 37.45 | 3241.45 | 3109.5 | 131.95 | 3272 | 5.86 | 0.54421 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:20 to 08:25 WO# | 26336217 26477125 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
272 | 2016-09-21 | 911 | 1035 | 1040 | 0 | 35.98 | 3021.98 | 2903.25 | 118.73 | 3062 | 6.14 | 0.48606 | Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure (Low voltage)From-08:03 to 08:08 & 11:06 to 12:10 & 16:44 to 16:49 WO# | 26336217 26478142 26478240 26479500 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
273 | 2016-09-22 | 401 | 441 | 453 | 0 | 10.34 | 1305.34 | 1226.25 | 79.09 | 1332 | 2.19 | 0.59281 | Rainy & cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-17:28 to 17:33 WO# | 26336217 26481144 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
274 | 2016-09-23 | 1102 | 1261 | 1238 | 0 | 40.85 | 3641.85 | 3493.5 | 148.35 | 3655 | 6.66 | 0.53489 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:50 to 08:00 & 11:55 to 12:01 WO# | 26336217 26481238 26481420 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
275 | 2016-09-24 | 1091 | 1243 | 1238 | 0 | 40.95 | 3612.95 | 3459.75 | 153.2 | 3623 | 6.51 | 0.54243 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
276 | 2016-09-25 | 1058 | 1205 | 1199 | 0 | 40.97 | 3502.97 | 3338.25 | 164.72 | 3515 | 6.35 | 0.53952 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
277 | 2016-09-26 | 1063 | 1209 | 1198 | 0 | 41.11 | 3511.11 | 3387 | 124.11 | 3522 | 6.44 | 0.53304 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:36 to 15:41 WO# | 26336217 26490687 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
278 | 2016-09-27 | 1096 | 1278 | 1272 | 0 | 41.79 | 3687.79 | 3532.5 | 155.29 | 3692 | 6.78 | 0.53074 | Module cleaning done inverter -3 Row- ,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:25 to 16:30 & 17:45 TO 17:56 WO# | 26336217 26491679 26491670 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2016-09-28 | 1029 | 1210 | 1210 | 0 | 41.46 | 3490.46 | 3366 | 124.46 | 3525 | 6.49 | 0.52938 | Module cleaning done inverter -3&2 Row- ,K,L,M,N, & Total module cleaning -987 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:07 to 08:14 & 09:24 TO 09:32 WO# | 26336217 26491735 26491736 | 987 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 2016-09-29 | 1108 | 1294 | 1283 | 0 | 42.48 | 3727.48 | 3572.25 | 155.23 | 3720 | 6.7 | 0.54115 | Module cleaning done inverter -2 Row- ,H,I,J, & Total module cleaning -798 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-16:52 to 16:57 WO# | 26336217 26494557 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 2016-09-30 | 1001 | 1159 | 1142 | 0 | 38.3 | 3340.3 | 3196.5 | 143.8 | 3485 | 6.5 | 0.52257 | Module cleaning done inverter -1 Row- ,A,B,C,D,E,F,G, & Total module cleaning -882 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down | 26336217 | 882 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2016-10-01 | 520 | 583 | 588 | 0 | 17.84 | 1708.84 | 1609.5 | 99.34 | 1935 | 3.5 | 0.53885 | Module cleaning done inverter -3 Row- ,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day | 26336217 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
284 | 2016-10-02 | 910 | 1034 | 1035 | 0 | 32.91 | 3011.91 | 2891.25 | 120.66 | 3090 | 4.56 | 0.66046 | Today I Replaced The D.C.12Amp Fuse Link of The String-09++tive in AJB-104 of The Inverter-2 during The Period of 11:30 To 11:35 & Rainy & Rainy cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-08:15 to 08:21 WO# | 26336217 26500713 26500990 |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
285 | 2016-10-03 | 741 | 843 | 836 | 0 | 29.24 | 2449.24 | 2447.25 | 1.99 | 2402 | 3.15 | 0.74322 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day & Grid Failure From-09:24 to 09:48 & 13:58 to 16:02 WO# | 26336217 26501207 26501213 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
286 | 2016-10-04 | 548 | 610 | 611 | 0 | 20.13 | 1789.13 | 1650 | 139.13 | 1922 | 3.06 | 0.61219 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day & Grid Failure From-10:14 to 10:22 WO# | 26336217 26501268 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
287 | 2016-10-05 | 102 | 113 | 113 | 0 | 3.23 | 331.23 | 260.25 | 70.98 | 369 | 0.52 | 0.69163 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down, Rainy & cloudy day & Grid Failure From-07:45 to 07:55 & 09:30 to 12:58 WO# | 26336217 26504090 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
288 | 2016-10-06 | 266 | 294 | 300 | 0 | 8.16 | 868.16 | 771 | 97.16 | 892 | 1.47 | 0.59143 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down, Rainy & cloudy day | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
289 | 2016-10-07 | 706 | 803 | 803 | 0 | 24.52 | 2336.52 | 2216 | 120.52 | 2365 | 4.9 | 0.47042 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down, Rainy & cloudy day & Grid Failure From-15:10 to 15:18 WO# | 26336217 26505577 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
290 | 2016-10-08 | 831 | 950 | 961 | 0 | 31.92 | 2773.92 | 2646.75 | 127.17 | 2803 | 5.14 | 0.53151 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down Rainy & cloudy day & Grid Failure From-15:10 to 15:18 WO# | 26336217 26512433 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
291 | 2016-10-09 | 769 | 870 | 864 | 0 | 29.35 | 2532.35 | 2392.5 | 139.85 | 2550 | 4.65 | 0.53449 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
292 | 2016-10-10 | 831 | 956 | 956 | 0 | 34.96 | 2777.96 | 2654 | 123.96 | 2810 | 5.17 | 0.52975 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day & Grid Failure From-07:33 to 07:41 & 10:28 to 10:33 WO# | 26336217 26512676 26512677 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
293 | 2016-10-11 | 893 | 1012 | 1017 | 0 | 34.43 | 2956.43 | 2837.25 | 119.18 | 3001 | 5.5 | 0.53181 | Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day & Grid Failure From-09:51 to 09:59 & 17:27 to 17:33 WO# | 26336217 26513009 26514105 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
294 | 2016-10-12 | 1058 | 1210 | 1216 | 0 | 44.01 | 3528.01 | 3381 | 147.01 | 3540 | 6.62 | 0.52119 | Module cleaning done inverter -3 Row- ,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & cloudy day | 26336217 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
295 | 2016-10-13 | 1034 | 1192 | 1187 | 0 | 39.38 | 3452.38 | 3319.5 | 132.88 | 3470 | 6.39 | 0.52927 | Module cleaning done inverter -3&2 Row- ,K,L,M,N, & Total module cleaning -987 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-07:05 to 07:20 WO# | 26336217 26514435 | 987 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2016-10-14 | 995 | 1154 | 1137 | 0 | 38.94 | 3324.94 | 3162.75 | 162.19 | 3350 | 6.06 | 0.5388 | Module cleaning done inverter -1&2 Row- ,H,I,J, & Total module cleaning -798 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel sut down & Grid Failure From-15:06 to 15:26 & 17:30 to 18:03 WO# | 26336217 26515543 26515553 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2016-10-15 | 1040 | 1187 | 1175 | 0 | 39.23 | 3441.23 | 3291 | 150.23 | 3460 | 6.39 | 0.52775 | Module cleaning done inverter -1&3 Row-A,B,C,D ,P,Q,R,S,T & Total module cleaning -777 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel shut down & L.T pannel P.M | 26336217 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2016-10-16 | 832 | 939 | 933 | 0 | 32.26 | 2736.26 | 2606.25 | 130.01 | 2760 | 4.96 | 0.54235 | cloudy day & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel shut down | 26336217 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
299 | 2016-10-17 | 1007 | 1147 | 1148 | 0 | 38.71 | 3340.71 | 3185.25 | 155.46 | 3347 | 6.15 | 0.53044 | Module cleaning done inverter -1&3 Row-,M,N,O, & Total module cleaning -651 & Inverter no-4 Schneider 250 kw morning time note wakeup Err code-0853 ( cold OR Inverter V Range ) Date-13-07-16 Inverter steel shut down | 26336217 | 651 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 2016-10-18 | 859 | 978 | 978 | 165 | 32.22 | 3012.22 | 2875.5 | 136.72 | 3040 | 5.23 | 0.56653 | Module cleaning done inverter -4 Row-,A,B,C,D,E,F, & Total module cleaning -792 & Inverter No-4 250 KW Schneider Resolve The issue Replce D.C to D.C CONVERTER & P.C.B Inverter started-15:15 & Grid Faillure From-12:45 to 14:20 WO# | 26525947 | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2016-10-19 | 1103 | 1272 | 1266 | 1090 | 41.69 | 4772.69 | 4557 | 215.69 | 4771 | 6.62 | 0.70243 | Module cleaning done inverter -4 Row-,G,H,I,J, & Total module cleaning -774 & Inverter No-4 250 KW Schneider Morning time note wakeup Err code-0252 IGBT SWICH Reset Err code Inverter started 08:50 WO# | 26526236 | 774 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2016-10-20 | 1085 | 1250 | 1256 | 1080 | 41.82 | 4712.82 | 4488.75 | 224.07 | 4735 | 6.51 | 0.70891 | Module cleaning done inverter -4&3 Row-,K,L,&,O,P,Q,R,S,T, & Total module cleaning -918 & Inverter No-4 250 KW Schneider Inverter Auto trip15:50 Err code-0252 IGBT SWICH Reset Err code Inverter started 016:55 & Grid Failure From-06:33 to 06:42 WO# | 26526615 26526614 | 918 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2016-10-21 | 1052 | 1221 | 1221 | 996 | 40.92 | 4530.92 | 4314.75 | 216.17 | 4590 | 5.9 | 0.75825 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2016-10-22 | 910 | 1051 | 1045 | 924 | 34.26 | 3964.26 | 3798.75 | 165.51 | 4025 | 6.1 | 0.64312 | Module cleaning done inverter -1&2 Row-,I,J,K, & Total module cleaning -840 & Today I Replaced The D.C.12Amp Fuse Link of The String-09--tive in AJB-102 of The Inverter-4 during The Period of 18:15 To 18:20 & Grid Failure From-12:15 to 12:57 & 15:33 to 15:39 & 17:10 to 17:15 WO# | 26533210 26533222 26533225 26533227 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
305 | 2016-10-23 | 972 | 1108 | 1086 | 885 | 38.09 | 4089.09 | 3885.75 | 203.34 | 4125 | 6.05 | 0.66454 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2016-10-24 | 1029 | 1171 | 1159 | 1020 | 40.38 | 4419.38 | 4215 | 204.38 | 4510 | 6.5 | 0.67626 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 &Grid Failure From- 16:59 to 17:05 WO# | 26535312 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2016-10-25 | 922 | 1051 | 1040 | 943 | 35.83 | 3991.83 | 3798.75 | 193.08 | 4048 | 5.9 | 0.66872 | Module cleaning done inverter -1&4 Row-,A,B,C,D,& A,B,C,D, & Total module cleaning -768 &Grid Failure From- 13:30 to 13:39 WO# | 26539160 | 768 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2016-10-26 | 995 | 1131 | 1119 | 1180 | 38.95 | 4463.95 | 4261.5 | 202.45 | 4502 | 6.2 | 0.70773 | Module cleaning done inverter -4 Row-,E,F,G,H, & Total module cleaning -756 &Grid Failure From- 16:37 to 16:41 WO# | 26545259 | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2016-10-27 | 1051 | 1193 | 1199 | 656 | 40.7 | 4139.7 | 3920.25 | 219.45 | 4152 | 6.36 | 0.63629 | Module cleaning done inverter -4 Row-,I,J,K,L,& Trackers & Total module cleaning -726 |  | 726 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2016-10-28 | 1046 | 1210 | 1210 | 1108 | 41.41 | 4615.41 | 4394.25 | 221.16 | 4640 | 6.43 | 0.70333 | Module cleaning done inverter -3 Row-,O,P,Q,R,S,T, & Total module cleaning -630 & Inverter No-4 250 KW Schneider Auto trip 16:05 Err code-0252 IGBT SWICH Reset Err code But Inverter Not started (Inverter steel sleep mode) WO# | 26545794 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2016-10-29 | 956 | 1108 | 955 | 0 | 38.04 | 3057.04 | 2900 | 157.04 | 3120 | 5.8 | 0.5243 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning-714 & Inverter no-3 ABB 250 KW Auto trip 08:05 Err code-(32A6) Net Loss Reset Err code Inverter started-09:35 & Transformer P.M, Grid Failure From-07:55 to 08:05 & 17:25 to 17:40 WO# | 26545789 26545790 26549957 | 714 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2016-10-30 | 904 | 1040 | 1024 | 435 | 36.43 | 3439.43 | 3264.75 | 174.68 | 3480 | 5.44 | 0.6235 | Grid Failure From-11:55 to 12:03 WO# | 26551194 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 2016-10-31 | 967 | 1108 | 1091 | 365 | 38.93 | 3569.93 | 3375 | 194.93 | 3600 | 5.87 | 0.59775 | Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter started at 13:37 pm & Grid Failure From-09:52 to 10:06 WO# | 26551446 26551254 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2016-11-01 | 921 | 1057 | 1040 | 735 | 37.56 | 3790.56 | 3588.75 | 201.81 | 3820 | 5.53 | 0.67327 | Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter started at 11:04 am & Grid Failure From-17:30 to 17:38 WO# | 26551988 26554098 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2016-11-02 | 854 | 967 | 955 | 25 | 35.34 | 2836.34 | 2681.25 | 155.09 | 2890 | 5.15 | 0.54694 | Module cleaning done inverter -1 Row-A,B,C,D,E,F & Total module cleaning -672 & Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter still shut down & Grid Failure From-8:51 to 9:01 & 10:30 to 10:38 & 17:17 to 17:46 WO# | 26554859 26554159 26554164 26554858 | 672 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2016-11-03 | 899 | 1017 | 1001 | 270 | 36.58 | 3223.58 | 3057.75 | 165.83 | 3270 | 5.45 | 0.5848 | Module cleaning done inverter -3&4 Row-R,S,T,A,B,C,D & Total module cleaning -600 & Inverter No - 4 Schneider morning time not wake up on Error code 0016, DC Contactor, Inverter Start at 11:50 under observation scheider service engineer many time trip after 12:50 inverter stop to still shut down & Grid Failure From-9:57 to 10:14 & 10:55 to 11:08 WO# | 26555226 26554909 26555191 | 600 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2016-11-04 | 859 | 967 | 967 | 0 | 34.7 | 2827.7 | 2693.25 | 134.45 | 2880 | 5.1 | 0.5504 | Module cleaning done inverter -3 Row-N,O,P,Q & Total module cleaning -672 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-15:01 to 15:13 WO# | 26555226 26555622 | 672 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 2016-11-05 | 825 | 927 | 933 | 0 | 33.25 | 2718.25 | 2562.75 | 155.5 | 2760 | 4.89 | 0.55011 | Module cleaning done inverter -2&3 Row-K,L,M & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-11:13 to 11:26 WO# | 26555226 26555793 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2016-11-06 | 871 | 1001 | 989 | 0 | 35.2 | 2896.2 | 2742.75 | 153.45 | 2930 | 5.21 | 0.54813 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2016-11-07 | 978 | 1131 | 1119 | 0 | 38.58 | 3266.58 | 3108.75 | 157.83 | 3280 | 5.9 | 0.54184 | Module cleaning done inverter -1&2 Row-H,I,J & Total module cleaning -798 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-16:00 to 16:13 WO# | 26555226 26561410 | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2016-11-08 | 990 | 1119 | 1103 | 0 | 39.12 | 3251.12 | 3105.75 | 145.37 | 3280 | 6.04 | 0.52928 | Module cleaning done inverter -1 Row-,A,B,C,D,E,F,G, & Total module cleaning -832 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-08:37 to 09:13 WO# | 26555226 26561463 | 832 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2016-11-09 | 1028 | 1170 | 1147 | 0 | 40.17 | 3385.17 | 3226.5 | 158.67 | 3401 | 6.24 | 0.53122 | Module cleaning done inverter -4 Row-,A,B,C,D,E,F, & Total module cleaning -792 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2016-11-10 | 1052 | 1193 | 1170 | 0 | 40.55 | 3455.55 | 3282.75 | 172.8 | 3460 | 6.37 | 0.52941 | Module cleaning done inverter -4 Row-,G,H,I,J, & Total module cleaning -774 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 774 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2016-11-11 | 1012 | 1153 | 1142 |  | 40.77 | 3347.77 | 3192 | 155.77 | 3370 | 6.17 | 0.53235 | Module cleaning done inverter -4&3 Row-,K,L,& ,O,P,Q,R,S,T,& Trackers & Total module cleaning -978 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 978 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2016-11-12 | 1018 | 1154 | 1165 |  | 40.51 | 3377.51 | 3223.5 | 154.01 | 3409 | 6.1 | 0.54469 | Module cleaning done inverter -3&2 Row-L,M,N & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-13:03 to 13:11 WO# | 26555226 26569497 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2016-11-13 | 994 | 1136 | 1142 |  | 40.3 | 3312.3 | 3173.25 | 139.05 | 3340 | 6.12 | 0.53192 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-10:14 to 10:17 & 14:50 to 15:03 WO# | 26555226 26569541 26569893 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2016-11-14 | 928 | 107 | 1069 |  | 38.42 | 2142.42 | 2033.25 | 109.17 | 2170 | 5.65 | 0.37434 | Module cleaning done inverter -2 Row-I,J,K & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW DC Breaker failure Error code (8188) at 9:34 to still shut down & Grid Failure From-7:35 to 7:44 & 9:29 to 9:34 WO# | 26555226 26570188 26570187 26569933 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2016-11-15 | 944 |  | 1096 |  | 39.22 | 2079.22 | 1969.5 | 109.72 | 2090 | 5.8 | 0.35121 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW DC Breaker failure Error code (8188) 14/11/16 at 9:34 to still shut down & Grid Failure From-13:26 to 13:32 & Transformer No-2 300kva Padmavahini Filled Aprox 25 Litter oil WO# | 26555226 26570188 26579104 | 777 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2016-11-16 | 972 |  | 1091 |  | 39.26 | 2102.26 | 1995 | 107.26 | 2110 | 5.84 | 0.35215 | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -654 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW DC Breaker failure Error code (8188) 14/11/16 at 9:34 to still shut down & Grid Failure From-10:00 to 10:04 WO# | 26555226 26570188 26580408 | 654 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2016-11-17 | 989 | 1 | 1097 |  | 39.76 | 2126.76 | 2023.5 | 103.26 | 2035 | 5.9 | 0.33617 | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Inverter No-2 ABB 250KW Resolved The Error code (8188) DC Breaker Failure Replased The NEW DC Breaker Than Inverter started 17:40 & Grid Failure From-09:58 to 10:03 WO# | 26555226 26580460 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2016-11-18 | 984 | 1097 | 1103 |  | 39.69 | 3223.69 | 3084 | 139.69 | 3250 | 6.02 | 0.52619 | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Trackers & Total module cleaning -924 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-10:36 to 10:42 WO# Array PM | 26555226 26581054 | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2016-11-19 | 973 | 1086 | 1085 |  | 39.72 | 3183.72 | 3021 | 162.72 | 3190 | 5.97 | 0.5208 | Module cleaning done inverter -3 Row-O,P,Q,R,S,T & Total module cleaning -630 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down WO# | 26555226 | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2016-11-20 | 983 | 1102 | 1114 |  | 40.15 | 3239.15 | 3096 | 143.15 | 3270 | 6.11 | 0.52163 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Grid Failure From-16:12 to 16:22 WO# Combiner PM | 26555226 26587011 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2016-11-21 | 944 | 1046 | 1074 |  | 37.3 | 3101.3 | 2941.5 | 159.8 | 3120 | 5.79 | 0.5252 | Module cleaning done inverter -2&3 Row-L,M,N & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# Seeds PM | 26555226 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2016-11-22 | 984 | 1114 | 1125 |  | 39.8 | 3262.8 | 3101.25 | 161.55 | 3280 | 6.07 | 0.52667 | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2016-11-23 | 989 | 1125 | 1125 |  | 40.07 | 3279.07 | 3119.25 | 159.82 | 3300 | 6.11 | 0.52641 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# & All Transformers cap oil & silica Gel Replaced Aprox 4 kg | 26555226 | 777 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2016-11-24 | 1024 | 1142 | 1142 |  | 40.75 | 3348.75 | 3180 | 168.75 | 3368 | 6.29 | 0.52188 | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2016-11-25 | 1023 | 1147 | 1148 |  | 41.04 | 3359.04 | 3211.5 | 147.54 | 3390 | 6.42 | 0.51466 | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-16:24 to 16:30 WO# | 26555226 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2016-11-26 | 1001 | 1108 | 1113 |  | 39.84 | 3261.84 | 3104.25 | 157.59 | 3280 | 6.19 | 0.51646 | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-08:23 to 08:42 WO# | 26555226 26595999 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2016-11-27 | 1017 | 1131 | 1131 |  | 40.78 | 3319.78 | 3171 | 148.78 | 3330 | 6.37 | 0.50952 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2016-11-28 | 1018 | 1136 | 1136 |  | 41.35 | 3331.35 | 3164.25 | 167.1 | 3354 | 6.38 | 0.51238 | Module cleaning done inverter -3 Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down & Today 1 Module Del solar 230 watts Replaced as a 1`nd From Lower Last of The `T` Row,String-8 AJB-117 (OLD Module Sr.no-PB10B071470175) NEW MODULE-PB10B068470104 WO# | 26555226 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2016-11-29 | 989 | 1113 | 1120 |  | 40.38 | 3262.38 | 3096 | 166.38 | 3280 | 6.26 | 0.51068 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# & Trackers P.M | 26555226 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 2016-11-30 | 978 | 1081 | 1119 |  | 39.95 | 3217.95 | 3063 | 154.95 | 3240 | 6.1 | 0.51769 | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2016-12-01 | 860 | 972 | 995 |  | 36.75 | 2863.75 | 2745.75 | 118 | 2910 | 5.54 | 0.51196 | Today replaced 5 Damaged moduleModule No-1-Lower side string No-5, ROW-B, Module No-2, AJB No-100, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1108800 New Module Sr No-NPC10BY1113787 Module No-2-Lower side string No-9, ROW-G, Module No-5, AJB No-102, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1112823 New Module Sr No-NPC10BY1113788 Module No-3-Lower side string No-2, ROW-I, Module No-36, AJB No-104, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1116365 New Module Sr No-NPC10BY1113786 Module No-4-Upper side string No-2, ROW-I, Module No-36, AJB No-104, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1116358 New Module Sr No-NPC10BY1113785 Module No-5-Upper side string No-6, ROW-L, Module No-1, AJB No-105, Thin Film 140 Watts, Next Power, Damage Module Sr No-NPC10BY1113851 New Module Sr No-NPC10BY1113784 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# & Grid Failure From-08:30 to 08:40 & 10:42 to 11:00 & 17:50 to 17:54 WO# | 26555226 26602753 26603751 26606915 26606916 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 2016-12-02 | 887 | 1001 | 1023 |  | 37.35 | 2948.35 | 2807.25 | 141.1 | 2980 | 5.5 | 0.52809 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-17:05 to 17:10 WO# | 26555226 26607173 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2016-12-03 | 842 | 955 | 967 |  | 36.11 | 2800.11 | 2682.75 | 117.36 | 2850 | 5.23 | 0.53112 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-02:10 to 07:17 & 12:05 to 12:10 & 15:47 to 15:58 WO# | 26555226 26608739 26609879 26612908 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2016-12-04 | 888 | 1007 | 1012 |  | 37.68 | 2944.68 | 2811 | 133.68 | 2975 |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-07:35 to 07:39 & 13:36 to 13:40 WO# | 26555226 26613522 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 2016-12-05 | 933 | 1063 | 1074 |  | 39.85 | 3109.85 | 2981.25 | 128.6 | 3240 |  |  | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-07:37 to 07:43 & 14:18 to 14:25 WO# | 26555226 26613719 26613721 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2016-12-06 | 972 | 1108 | 1120 |  | 40.98 | 3240.98 | 3100.5 | 140.48 | 3270 |  |  | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut WO# | 26555226 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2016-12-07 | 956 | 1091 | 1108 |  | 40.74 | 3195.74 | 3038.25 | 157.49 | 3225 |  |  | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Grid Failure From-09:58 to 10:04 WO# | 26555226 26615274 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2016-12-08 | 932 | 1068 | 1108 |  | 40.03 | 3148.03 | 3005.25 | 142.78 | 3180 |  |  | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-15:12 to 15:16 WO# | 26555226 26618416 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2016-12-09 | 888 | 1040 | 1046 |  | 38.35 | 3012.35 | 2880 | 132.35 | 3045 | 5.82 | 0.50994 | Module cleaning done inverter -3&Trackers, Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:35 to 10:48 WO# | 26555226 26618453 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2016-12-10 | 906 | 1024 | 1028 |  | 36.68 | 2994.68 | 2840.25 | 154.43 | 3012 | 5.62 | 0.52236 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-07:35 to 07:40 WO# | 26555226 26620348 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2016-12-11 | 945 | 1074 | 1086 |  | 39.09 | 3144.09 | 3006.75 | 137.34 | 3180 | 5.97 | 0.51917 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-09:12 to 09:17 WO# | 26555226 26624488 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2016-12-12 | 1000 | 1125 | 1131 |  | 40.51 | 3296.51 | 3133.5 | 163.01 | 3305 | 6.2 | 0.51956 | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2016-12-13 | 961 | 1080 | 1091 |  | 39.61 | 3171.61 | 3033.5 | 138.11 | 3200 | 6 | 0.51982 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:28 to 10:34 & 16:43 to 16:49 WO# | 26555226 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2016-12-14 | 962 | 1079 | 1074 |  | 39.47 | 3154.47 | 2988 | 166.47 | 3160 | 5.95 | 0.51763 | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2016-12-15 | 966 | 1086 | 1085 |  | 39.95 | 3176.95 | 3033.75 | 143.2 | 3200 | 6.08 | 0.51298 | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2016-12-16 | 973 | 1091 | 1103 |  | 40.04 | 3207.04 | 3046.5 | 160.54 | 3070 |  |  | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2016-12-17 | 949 | 1063 | 1063 |  | 39.84 | 3114.84 | 2972.25 | 142.59 | 3125 |  |  | Module cleaning done inverter -3& Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:40 to 10:43 WO# | 26555226 26649548 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2016-12-18 | 928 | 1034 | 1062 |  | 39.09 | 3063.09 | 2915.25 | 147.84 | 3125 |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2016-12-19 | 887 | 996 | 1094 |  | 37.68 | 3014.68 | 2812.5 | 202.18 | 3195 |  |  | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:14 to 10:18 & 13:27 to 13:39 WO# | 26555226 26658394 26658737 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2016-12-20 | 927 | 1068 | 1079 |  | 39.75 | 3113.75 | 2982.75 | 131 | 3150 |  |  | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-11:20 to 11:30 & 17:02 to 17:06 WO# | 26555226 26659830 26659841 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 2016-12-21 | 995 | 1119 | 1126 |  | 41.12 | 3281.12 | 3132 | 149.12 | 3300 | 6.15 | 0.52299 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 2016-12-22 | 973 | 1097 | 1096 |  | 39.65 | 3205.65 | 3060.75 | 144.9 | 3210 | 6.02 | 0.51971 | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 2016-12-23 | 933 | 1043 | 1050 |  | 38.74 | 3064.74 | 2909.25 | 155.49 | 3060 |  |  | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:25 to 10:30 WO# | 26555226 26661656 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 2016-12-24 | 927 | 1046 | 1068 |  | 39.33 | 3080.33 | 2949.75 | 130.58 | 3140 |  |  | Module cleaning done inverter -4 Row-H,I,J,K,L & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-9:52 to 9:58 & 10:39 to 10:47 WO# | 26555226 26664656 26664657 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 2016-12-25 | 1006 | 1142 | 1165 |  | 41.94 | 3354.94 | 3197.25 | 157.69 | 3380 |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-06:59 to 07:03 WO# | 26555226 26668775 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 2016-12-26 | 955 | 1068 | 1097 |  | 40.54 | 3160.54 | 3016.5 | 144.04 | 3100 |  |  | Module cleaning done inverter -3 Row-O,P,Q,R,S,T & Total module cleaning -630 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-9:27 to 9:31 WO# | 26555226 26671474 | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 2016-12-27 | 933 | 1063 | 1068 |  | 39.8 | 3103.8 | 2946 | 157.8 | 3120 |  |  | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 2016-12-28 | 973 | 1108 | 1114 |  | 40.86 | 3235.86 | 3073.5 | 162.36 | 3320 |  |  | Module cleaning done inverter -2 Row-I,J,K & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut down WO# | 26555226 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 2016-12-29 | 915 | 1029 | 1029 |  | 38.54 | 3011.54 | 2883 | 128.54 | 3040 | 5.82 | 0.5091 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-13:58 to 14:08 & 15:49 to 15:53 & 16:01 to 16:06 WO# | 26555226 26674366 26674370 26674371 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 2016-12-30 | 894 | 1007 | 1006 |  | 37.17 | 2944.17 | 2810.25 | 133.92 | 2970 | 5.72 | 0.50607 | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C,D & Total module cleaning -768 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-11:29 to 11:35 WO# | 26555226 26674448 | 768 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | 2016-12-31 | 769 | 859 | 865 |  | 32.18 | 2525.18 | 2397 | 128.18 | 2550 | 4.78 | 0.51995 | Module cleaning done inverter -4 Row-E,F,G,H,I & Total module cleaning -954 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut & Grid Failure From-14:49 To 14:54 & 15:28 to 17:51 WO# | 26555226 26681621 26681628 | 954 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2017
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2017-01-01 | 944 | 1057 | 1069 |  | 34.24 | 3104.24 | 2958 | 146.24 | 3140 | 5.31 | 0.57635 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2017-01-02 | 938 | 1046 | 1068 |  | 39.58 | 3091.58 | 2936.25 | 155.33 | 3090 | 5.31 | 0.56717 | Module cleaning done inverter -4 Row-,J,K,L, & Total module cleaning -468 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut DownWO# | 26555226 | 468 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2017-01-03 | 916 | 1034 | 1052 |  | 34.99 | 3036.99 | 2903.25 | 133.74 | 3050 | 5.65 | 0.52614 | Today I Replaced The D.C.12Amp Fuse Link of The String-07--tive in AJB-111 of The Inverter-2 during The Period of 11:30 To 11:40 & Module cleaning done inverter -3 Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From 15:48 to 15:56 WO# | 26555226 26685039 26685046 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
3 | 2017-01-04 | 905 | 1058 | 1040 |  | 35.71 | 3038.71 | 2891.25 | 147.46 | 2940 |  |  | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From 13:54 to 14:00 & 15:35 to 15:42 WO# | 26555226 26685454 26685457 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2017-01-05 | 847 | 966 | 950 |  | 32.51 | 2795.51 | 2658 | 137.51 | 1151 |  |  | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2017-01-06 | 832 | 939 | 921 |  | 34.35 | 2726.35 | 2589 | 137.35 | 2500 |  |  | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2017-01-07 | 712 | 797 | 786 |  | 28.8 | 2323.8 | 2196 | 127.8 | 3775 |  |  | Module cleaning done inverter -1 & 4 Row-A,B,C,D & A,B,C & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2017-01-08 | 859 | 972 | 961 |  | 36.5 | 2828.5 | 2688 | 140.5 | 3062 |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-14:00 to 14:10 WO# | 26555226 26693972 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2017-01-09 | 854 | 961 | 967 |  | 36.89 | 2818.89 | 2691 | 127.89 |  |  |  | Module cleaning done inverter -4 Row-D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-14:35 to 14:41 WO# | 26555226 26695157 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2017-01-10 | 854 | 973 | 984 |  | 37.55 | 2848.55 | 2736 | 112.55 |  |  |  | Module cleaning done inverter -4 Row-H,I,J,K,L & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-5:05 to 7:30 & 9:47 to 9:53 & 10:26 to 10:34 WO# | 26555226 26696781 26696790 26697527 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2017-01-11 | 961 | 1125 | 1080 |  | 40.83 | 3206.83 | 3097.5 | 109.33 |  |  |  | Module cleaning done inverter -3 & Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:18 to 10:22 & 18::01 to 18:04 WO# | 26555226 26699268 26699344 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2017-01-12 | 1029 | 1181 | 1186 |  | 42.52 | 3438.52 | 3242.25 | 196.27 |  |  |  | Module cleaning done inverter -3&2 Trackers Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2017-01-13 | 938 | 1086 | 1052 |  | 40.12 | 3116.12 | 3003 | 113.12 |  |  |  | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-14:49 to 15:03 & 15:08 to 15:13 & 15:23 to 15:27 & 16:00 to 16:05 & 16:12 to 16:47 WO# | 26555226 26701808 26701809 26701813 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2017-01-14 | 859 | 972 | 956 |  | 35 | 2822 | 2709.75 | 112.25 |  |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-16:07 to 16:15 & 16:32 to 16:40 & 16:44 to 17:30 & 17:54 to 18:00 WO# | 26555226 26706403 26706407 26706409 26706411 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2017-01-15 | 871 | 989 | 972 |  | 33 | 2865 | 2727 | 138 |  |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2017-01-16 | 939 | 1075 | 1001 |  | 34.98 | 3049.98 | 2903.25 | 146.73 |  |  |  | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Today inverter No-3 ABB 250 KW Morning time note wake up Err code-(8189) Auto Reset ,F, Reset The Err code 3 Time inverter started 9:18 & Inverter no-1&3s Transformer maintance L.T & H.T, side tietnace & oil filing Aprox 50 liter WO# | 26555226 26707646 | 777 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2017-01-17 | 1011 | 1151 | 1147 |  | 37.96 | 3346.96 | 3194.25 | 152.71 |  |  |  | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2017-01-18 | 961 | 1099 | 1114 |  | 36.56 | 3210.56 | 3055.5 | 155.06 |  |  |  | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2017-01-19 | 741 | 865 | 865 |  | 28.32 | 2499.32 | 2363.25 | 136.07 |  |  |  | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
19 | 2017-01-20 | 769 | 865 | 853 |  | 27.23 | 2514.23 | 2377.5 | 136.73 |  |  |  | Module cleaning done inverter -4&Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
20 | 2017-01-21 | 141 | 158 | 153 |  | 4.85 | 456.85 | 396.75 | 60.1 |  |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day & Grid Failure From-09:44 to 10:40 & 10:55 to 16:01 | 26555226 26713302 26718386 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
21 | 2017-01-22 | 854 | 972 | 955 |  | 31.65 | 2812.65 | 2668.5 | 144.15 |  |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
22 | 2017-01-23 | 831 | 956 | 950 |  | 31.15 | 2768.15 | 2649 | 119.15 |  |  |  | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day & Grid Failure From-10:10 to 10:29 | 26555226 26718525 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
23 | 2017-01-24 | 893 | 1029 | 1040 |  | 35.02 | 2997.02 | 2857.5 | 139.52 |  |  |  | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day & Grid Failure From-10:05 to 10:12 | 26555226 26720440 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
24 | 2017-01-25 | 831 | 961 | 956 |  | 29.46 | 2777.46 | 2638.5 | 138.96 |  |  |  | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26552526 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
25 | 2017-01-26 | 882 | 1012 | 1001 |  | 32.98 | 2927.98 | 2787.75 | 140.23 | 2950 | 5.09 | 0.56488 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Cloudy Day | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
26 | 2017-01-27 | 1108 | 1289 | 1266 |  | 41.05 | 3704.05 | 3540 | 164.05 | 3720 | 6.58 | 0.55102 | Module cleaning done inverter -1&4 Row-,A,B,C,D,&A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:02 to 10:13 WO# | 26555226 26726608 | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2017-01-28 | 848 | 995 | 972 |  | 33.48 | 2848.48 | 2722.5 | 125.98 | 2880 | 5.18 | 0.5419 | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-08:50 to 09:14 & 09:28 to 09:45 & 9:48 to 11:20 & Today I Replaced The D.C.12Amp Fuse Link of The String-09++tive in AJB-116 of The Inverter-3 during The Period of 12:40 To 12:50 WO# | 26555226 26726819 26726820 26726821 26748457 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
28 | 2017-01-29 | 1091 | 1272 | 1244 |  | 39.83 | 3646.83 | 3486 | 160.83 | 3675 |  |  | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & TRANSFORMER P.M,WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2017-01-30 | 1069 | 1238 | 1233 |  | 43.43 | 3583.43 | 3406.5 | 176.93 | 3650 |  |  | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2017-01-31 | 1068 | 1244 | 1255 |  | 41.71 | 3608.71 | 3428.25 | 180.46 | 3610 | 6.47 | 0.54382 | Module cleaning done inverter -3& Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2017-02-01 | 1035 | 1232 | 1226 |  | 43.24 | 3536.24 | 3385.5 | 150.74 | 3560 | 6.39 | 0.543 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Grid Failure From-09:26 to 09:38 | 26555226 26733914 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2017-02-02 | 1069 | 1256 | 1244 |  | 43.34 | 3612.34 | 3446.25 | 166.09 | 3630 | 6.47 | 0.54683 | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2017-02-03 | 932 | 1080 | 1063 |  | 37.56 | 3112.56 | 2992.5 | 120.06 | 3130 | 5.74 | 0.53148 | Module cleaning done inverter -2 Row-,E,F,G,H, & Total module cleaning -77 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2017-02-04 | 865 | 989 | 978 |  | 35.51 | 2867.51 | 2727 | 140.51 | 2890 | 5.21 | 0.54065 | Module cleaning done inverter -1&4 Row-,A,B,C,D,& A,B,C, & Total module cleaning -624 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# & Grid Failure From-16:31 to 17:19 & 17:24 to 17:31 | 26555226 26741037 26741038 | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2017-02-05 | 1120 | 1307 | 1283 |  | 44.58 | 3754.58 | 3551.25 | 203.33 | 3765 | 6.76 | 0.54284 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Today Received ABB 250 KW New Inverter Our site By pdpu WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2017-02-06 | 1068 | 1238 | 1230 |  | 43.36 | 3579.36 | 3391.5 | 187.86 | 3580 | 6.42 | 0.5435 | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2017-02-07 | 1137 | 1328 | 1281 |  | 46.09 | 3792.09 | 3637.5 | 154.59 | 3810 | 7 | 0.53049 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down WO# | 26555226 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2017-02-08 | 966 | 1131 | 1113 |  | 40.78 | 3250.78 | 3122.25 | 128.53 | 3290 | 6.1 | 0.52568 | Inverter No - 4 250KW Schneider trip on Error code 0016, DC Contactor Failure, Date:03/11/2016 , 12:50 pm inverter stop to still shut Down & Grid Failure From-10:21 to 10:50 & 16:19 to 16:37 & 17:20 to 17:23WO# | 26555226 26743973 26744000 26744002 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2017-02-09 | 1137 | 1334 | 1306 | 927 | 46.77 | 4750.77 | 4406.25 | 344.52 | 4612 | 7.06 | 0.6367 | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter No - 4 250KW Schneider Replaced The New Inverter ABB 250 KW All working Fine Inverter started 11:30 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Site has taken shutdown due to Installation of New Inverter 10:18 to 10:23 WO# | 26555226 26744972 26744059 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2017-02-10 | 1119 | 1300 | 1272 | 1270 | 45.9 | 5006.9 | 4785 | 221.9 | 5020 | 6.74 | 0.72593 | Module cleaning done inverter -4 Row-O,P,Q,R,S,T & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short WO# | 26744972 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2017-02-11 | 1018 | 1171 | 1148 | 1074 | 41.5 | 4452.5 | 4269 | 183.5 | 4480 | 6.12 | 0.71348 | Module cleaning done inverter -2&3 Row-L,M,N, & Total module cleaning -714 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-12:20 to 12:24 WO# | 26744972 26751482 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2017-02-12 | 1048 | 1215 | 1187 | 1083 | 43.1 | 4576.1 | 4365.75 | 210.35 | 4605 | 6.35 | 0.70682 | Inverter no-4 ABB One AJB Down due to cable Lenth short WO# | 26744972 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2017-02-13 | 809 | 922 | 916 | 847 | 32.8 | 3526.8 | 3374.75 | 152.05 | 3565 | 4.46 | 0.77907 | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-12:13 to 12:47 WO# | 26744972 26756715 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2017-02-14 | 842 | 972 | 995 | 988 | 36.02 | 3833.02 | 3663 | 170.02 | 3862 |  |  | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-15:40 to 16:24 WO# | 26744972 26757428 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2017-02-15 | 888 | 1034 | 1068 | 1043 | 37.1 | 4070.1 | 3883.5 | 186.6 | 4100 |  |  | Module cleaning done inverter -1&4 Row-,A,B,C,D,&A,B,C, & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short WO# | 26744972 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2017-02-16 | 820 | 973 | 990 | 973 | 34.96 | 3790.96 | 3633 | 157.96 | 3840 | 5.4 | 0.69309 | Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-13:37 to 14:05 WO# & Today Module Cleaning Not done Because Grass cutting Swichyard side | 26744972 26760377 |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2017-02-17 | 989 | 1216 | 983 | 1220 | 38.84 | 4446.84 | 4249.5 | 197.34 | 4420 | 6.41 | 0.67207 | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From-13:06 to 13:15 & Today Grid Failure After Inverter No-3 ABB 250 KW not started Err code-Net Loss, Reset The Err 3 Time After Inverter started-14:37 WO# | 26744972 26760615 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2017-02-18 | 1023 | 1260 | 1222 | 1240 | 37.51 | 4782.51 | 4575 | 207.51 | 4660 | 6.54 | 0.69448 | Module cleaning done inverter -4 Row-H,I,J,K,L, & Total module cleaning -864 & Inverter no-4 ABB One AJB Down due to cable Lenth short | 26744972 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2017-02-19 | 961 | 1182 | 1142 | 1134 | 35.31 | 4454.31 | 4276.5 | 177.81 | 4465 | 6.16 | 0.70647 | Inverter no-4 ABB One AJB Down due to cable Lenth short & Grid Failure From- 18:00 to 18:45 WO# | 26744972 26764967 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2017-02-20 | 1080 | 1283 | 1215 | 1270 | 37.6 | 4885.6 | 4684.5 | 201.1 | 4910 |  |  | Module cleaning done inverter -3 & Trackers Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Yesterday Grid Failure After Inverter No-3 ABB 250 KW not started(Morning time not wake up) Due to D.C.contactor Failure, Inverter started Manually-08:38 WO# | 26744972 26764962 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2017-02-21 | 1102 | 1272 | 1232 | 1260 | 36.94 | 4902.94 | 4697.25 | 205.69 | 4925 | 6.69 | 0.71752 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today Inverter No-3 ABB 250 KW not started(Morning time not wake up) Due to D.C.contactor Failure, Inverter started Manually-07:45 WO# | 26744972 26766495 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2017-02-22 | 1080 | 1255 | 1227 | 1310 | 36.45 | 4908.45 | 4722 | 186.45 | 4930 | 6.88 | 0.69841 | Module cleaning done inverter -3&2 Row-,I,J,K, & Total module cleaning -840 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-16:58 to 17:52 WO# | 26744972 26766495 26771308 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2017-02-23 | 1001 | 1272 | 1233 | 1321 | 43.04 | 4870.04 | 4659.75 | 210.29 | 4900 | 6.99 | 0.68324 | Module cleaning done inverter -1 Row-,E,F,G,H, & Total module cleaning -777 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-08:46 to 09:05 & Grid Failure After Inverter No-1 ABB 250 KW not started Err code-8188 D.C.Breaker trip Reset Err code inverter started-9:56 WO# | 26744972 26766495 26771351 26771352 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2017-02-24 | 1091 | 1266 | 1266 | 1325 | 44.24 | 4992.24 | 4785.75 | 206.49 | 5020 |  |  | Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-08:00 & Grid Failure From-17:28 to 17:52 WO# | 26744972 26766495 26772800 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2017-02-25 | 1114 | 1301 | 1149 | 1351 | 45.16 | 4960.16 | 4721.25 | 238.91 | 4970 | 7.16 | 0.67654 | Module cleaning done inverter -1&4 Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-10:02 WO# | 26744972 26766495 26776945 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2017-02-26 | 1080 | 1278 | 1295 | 1331 | 44.34 | 5028.34 | 4824.75 | 203.59 | 5060 |  |  | Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-05:45 to 06:53 & 07:12 to 07:25 WO# | 26744972 26766495 26776955 26776956 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2017-02-27 | 1051 | 1272 | 1255 | 1295 | 43.27 | 4916.27 | 4719 | 197.27 | 4945 |  |  | Module cleaning done inverter -4 Row-,D,E,F,G, & Total module cleaning -702 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-07:47 to 07:55 to 18:08 to 18:18 WO# | 26744972 26766495 26777140 26778337 | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2017-02-28 | 950 | 1209 | 1142 | 1165 | 40.78 | 4506.78 | 4332 | 174.78 | 4535 |  |  | Module cleaning done inverter -4 Row-,H,I,J,K,L, & Total module cleaning -864 & Inverter no-4 ABB One AJB Down due to cable Lenth short & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Grid Failure From-09:07 to 09:15 & 14:10 to 14:16 & Grid Failure After Inverter No-1 ABB 250 KW not started Err code-8188 D.C.Breaker trip Reset Err code inverter started-9:47 WO# | 26744972 26766495 26778360 26778359 26778809 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 2017-03-01 | 1074 | 1255 | 1215 | 1234 | 41.39 | 4819.39 | 4604.25 | 215.14 | 4840 | 6.65 | 0.70938 | Module cleaning done inverter -3 & Trackers, Row-,O,P,Q,R,S,T, & Total module cleaning -690 & Inverter no-4 ABB 250 KW Replaced New Cable & AJB, started-18:40, & short out The Issue & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26744972 26766495 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2017-03-02 | 1086 | 1267 | 1233 | 1276 | 41.66 | 4903.66 | 4690.5 | 213.16 | 4935 | 6.71 | 0.71683 | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26766495 26781762 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2017-03-03 | 994 | 1159 | 978 | 1108 | 40.24 | 4279.24 | 4125.75 | 153.49 | 4335 | 6.17 | 0.68479 | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-09:40 & Today inverter no-4 ABB 250 KW Shut Down,16:07. Due to MJB'S One Lug sparking, Resolved The Issue Inverter started-16:55 & Grid Failure From-15:08 to 16:07 WO# | 26781838 26783992 26783988 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2017-03-04 | 1024 | 1204 | 972 | 1250 | 40.89 | 4490.89 | 4325.25 | 165.64 | 4571 | 6.51 | 0.68436 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-10:50 & Today I Replaced The D.C.12Amp Fuse Link of The String-09++tive in AJB-116 of The Inverter-3 during The Period of 12:40 To 12:50 & Grid Failure From-08:56 to 09:08 & 09:10 to 09:23 & 11:28 to 11:36 WO# | 26788033 26788032 26785405 26786933 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
65 | 2017-03-05 | 1068 | 1243 | 1204 | 1296 | 41.55 | 4852.55 | 4641.75 | 210.8 | 4880 | 6.55 | 0.72616 | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:50 WO# | 26788033 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2017-03-06 | 1103 | 1284 | 1250 | 1356 | 43.31 | 5036.31 | 4818 | 218.31 | 5065 | 6.8 | 0.72598 | Module cleaning done inverter -1&4 & Row-,A,B,C,D,& ,A,B,C, & Total module cleaning -624 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:50 WO# | 26788033 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2017-03-07 | 1046 | 1221 | 1227 | 1290 | 42.1 | 4826.1 | 4623.75 | 202.35 | 4865 | 6.54 | 0.72503 | Module cleaning done inverter -4, Row-,D,E,F,G, & Total module cleaning -704 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-08:00 & Grid Failure From-17:07 to 17:18 WO# | 26788033 26790307 | 704 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2017-03-08 | 1113 | 1323 | 1333 | 1401 | 44.12 | 5214.12 | 4971 | 243.12 | 5215 | 6.79 | 0.74858 | Module cleaning done inverter -4, Row-,H,I,J,K,L, & Total module cleaning -864 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:50 WO# | 26788033 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2017-03-09 | 1069 | 1272 | 1256 | 1311 | 42.34 | 4950.34 | 4760.25 | 190.09 | 4980 | 6.6 | 0.73542 | Module cleaning done inverter -3, Row-O,P,Q,R,S,T & Total module cleaning -690 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-08:00 & Grid Failure From-12:17 to 12:22 WO# | 26788033 26793174 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2017-03-10 | 899 | 1034 | 1000 | 1073 | 35.35 | 4041.35 | 3861 | 180.35 | 4082 | 5.42 | 0.73405 | Module cleaning done inverter -3&2 Row-,L,M,N, & Total module cleaning -714 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30 & Grid Failure From-16:17 to 16:30 WO# | 26788033 26794775 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2017-03-11 | 1193 | 1397 | 1374 | 1401 | 46.12 | 5411.12 | 5159.25 | 251.87 | 5425 | 7.4 | 0.71453 | Module cleaning done inverter -2 Row-,I,J,K, & Total module cleaning -840 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30WO# | 26788033 | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2017-03-12 | 1170 | 1368 | 1351 | 1396 | 42.58 | 5327.58 | 5089.5 | 238.08 | 5235 | 7.33 | 0.69609 | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30WO# | 26788033 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2017-03-13 | 1001 | 1340 | 1301 | 1351 | 40.81 | 5033.81 | 4833 | 200.81 | 5060 | 7.28 | 0.67744 | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:30 & Today morning time Inverter No-1 ABB 250 KW not wake up Due to error Net loss reset error code Inverter started at 9:30 & Grid Failure From-16:32 to 16:50 WO# | 26788033 26799068 26799266 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2017-03-14 | 1192 | 1390 | 1362 | 1427 | 43.22 | 5414.22 | 5188.5 | 225.72 | 5440 | 7.43 | 0.71361 | Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:40 & Grid Failure From-18:24 to 18:31 WO# | 26788033 26800001 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2017-03-15 | 1137 | 1329 | 1306 | 1386 | 38.5 | 5196.5 | 4993.5 | 203 | 5065 | 7.18 | 0.68756 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26788033 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2017-03-16 | 1063 | 1238 | 1227 | 1310 | 34.27 | 4872.27 | 4674 | 198.27 | 4895 | 6.77 | 0.70472 | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 WO# | 26788033 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2017-03-17 | 1023 | 1184 | 1215 | 1285 | 34.02 | 4741.02 | 4554 | 187.02 | 4770 | 6.64 | 0.70017 | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Today morning time Inverter No-3 ABB 250 KW not wake up Due to D.c. Breaker Failure inverter started Manually-07:45 & Today Inverter No-3 ABB 250 KW Replaced The New D.C. Breaker Resolved The Issue, & Grid Failure From-10:54 to 11:08 WO# | 26788033 26810242 | 704 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2017-03-18 | 1080 | 1244 | 1306 | 1376 | 34.52 | 5040.52 | 4831.5 | 209.02 | 5070 | 6.77 | 0.72991 | Module cleaning done inverter -3 & Trackers & Row-,O,P,Q,R,S,T, & Total module cleaning -690 WO# |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2017-03-19 | 1051 | 1232 | 1266 | 1321 | 35.02 | 4905.02 | 4702 | 203.02 | 4930 | 6.63 | 0.72475 | Grid Failure From-09:53 to 10:00 WO# | 26814767 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2017-03-20 | 1035 | 1232 | 1256 | 1310 | 35.23 | 4868.23 | 4687.5 | 180.73 | 4900 | 6.88 | 0.69416 | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714 & Grid Failure From-07:00 to 08:07 & 11:22 to 11:37 WO# | 26814794 26814841 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2017-03-21 | 1079 | 1278 | 1272 | 1316 | 35.94 | 4980.94 | 4776 | 204.94 | 5010 | 6.91 | 0.70666 | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 WO# |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2017-03-22 | 1046 | 1193 | 1192 | 1199 | 33.81 | 4663.81 | 4469.25 | 194.56 | 4690 | 6.6 | 0.6926 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2017-03-23 | 1108 | 1266 | 1261 | 1311 | 34.97 | 4980.97 | 4776.75 | 204.22 | 4910 | 6.89 | 0.69457 | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2017-03-24 | 1114 | 1284 | 1278 | 1361 | 35.46 | 5072.46 | 4874.25 | 198.21 | 5100 | 7.15 | 0.69521 | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Grid Failure From-14:58 to 15:08 WO# | 26817262 | 704 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2017-03-25 | 1097 | 1249 | 1249 | 1366 | 35.68 | 4996.68 | 4806.75 | 189.93 |  |  |  | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 & Grid Failure From-12:32 to 12:42 WO# | 26823758 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2017-03-26 | 1074 | 1233 | 1244 | 1340 | 40.61 | 4931.61 | 4752 | 179.61 |  |  |  | Grid Failure From-06:55 to 07:05 & 17:40 TO 17:45 WO# | 26823836 26823848 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2017-03-27 | 1029 | 1192 | 1210 | 1306 | 35 | 4772 | 4560.75 | 211.25 |  |  |  | Grid Failure From-09:33 to 09:40 WO# | 26824083 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2017-03-28 | 1074 | 1233 | 1283 | 1346 | 35.82 | 4971.82 | 4784.25 | 187.57 |  |  |  | Module cleaning done inverter -3, Row-O,P,Q,R,S,T & Total module cleaning -690 & Grid Failure From-07:53 to 08:00 WO# | 26824084 | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2017-03-29 | 1052 | 1232 | 1266 | 1320 | 35 | 4905 | 4728 | 177 |  |  |  | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714 & Grid Failure From-08:21 to 08:30 & 18:07 to 18:15 WO# | 26825064 26825065 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2017-03-30 | 1068 | 1278 | 1278 | 1321 | 35.23 | 4980.23 | 4776.75 | 203.48 |  |  |  | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 WO# |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2017-03-31 | 1103 | 1289 | 1278 | 1325 | 35 | 5030 | 4823.25 | 206.75 |  |  |  | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2017-04-01 | 1113 | 1277 | 1283 | 1321 | 34.96 | 5028.96 | 4830 | 198.96 |  |  |  | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2017-04-02 | 1108 | 1278 | 1278 | 1320 | 34.72 | 5018.72 | 4830 | 188.72 |  |  |  | Grid Failure From-09:57 to 10:07 & 17:07 to 17:27 WO# | 26833887 26833931 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2017-04-03 | 1012 | 1159 | 1153 | 1205 | 34.14 | 4563.14 | 4404.75 | 158.39 |  |  |  | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Grid Failure From-15:05 to 15:15 & 15:17 to 15:50 & 17:09 to 17:18 WO# | 26834042 26834045 26834049 | 704 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2017-04-04 | 1097 | 1278 | 1250 | 1346 | 41.2 | 5012.2 | 4803.75 | 208.45 |  |  |  | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 & Today I Replaced The 3, D.C.12Amp Fuse Link of The String-05--tive in AJB-109 of The Inverter-2 during The Period of 10:30 to 10:40 & string No2++tive & 3--tive line AJB No-113 Inverter No-3 During The period of 10:45 to 10:55, WO# |  | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
97 | 2017-04-05 | 1035 | 1204 | 1187 | 1280 | 39.54 | 4745.54 | 4549.5 | 196.04 |  |  |  | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2017-04-06 | 1080 | 1255 | 1255 | 1346 | 42.35 | 4978.35 | 4764.75 | 213.6 | 4990 | 6.71 | 0.72482 | Module cleaning done inverter -3&2, Row-L,M,N & Total module cleaning -714, |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2017-04-07 | 1124 | 1323 | 1357 | 1376 | 44.79 | 5224.79 | 5024.25 | 200.54 | 5230 | 7.13 | 0.71493 | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 WO# |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2017-04-08 | 1091 | 1295 | 1339 | 1320 | 43.81 | 5088.81 | 4902 | 186.81 | 5090 | 7.03 | 0.70569 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2017-04-09 | 1103 | 1339 | 1346 | 1341 | 43.71 | 5172.71 | 4962 | 210.71 | 5190 | 7.04 | 0.71853 | Sunday No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2017-04-10 | 1119 | 1374 | 1368 | 1235 | 43.84 | 5139.84 | 4938 | 201.84 | 5160 | 7.2 | 0.69851 | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 & Grid Failure From-10:27 to 10:32 WO# | 26844032 | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2017-04-11 | 1097 | 1351 | 1317 | 1285 | 42.09 | 5092.09 | 4867.5 | 224.59 | 5120 | 6.96 | 0.71699 | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 WO# |  | 704 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2017-04-12 | 1120 | 1346 | 1323 | 1321 | 42.26 | 5152.26 | 4935 | 217.26 | 5170 | 7.01 | 0.71883 | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 WO# |  | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2017-04-13 | 1147 | 1340 | 1312 | 1325 | 42 | 5166 | 4957.5 | 208.5 |  |  |  | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, & Grid Failure From-18:30 to 18:36 WO# |  | 690 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2017-04-14 | 1114 | 1306 | 1272 | 1306 | 40.97 | 5038.97 | 4833 | 205.97 |  |  |  | Module cleaning done inverter -3&2, Row-L,M,N & Total module cleaning -714, & Today Inverter No-3 ABB 250 KW Morning time not wake up Due to Err code Net Loss (A32) Reset The Err code Inverter started 07:32 WO# | 26846721 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2017-04-15 | 1119 | 1305 | 1278 | 1355 | 40.98 | 5097.98 | 4894.5 | 203.48 |  |  |  | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840 & L.T, PANAL P.M, WO# |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2017-04-16 | 1103 | 1284 | 1260 | 1341 | 41.57 | 5029.57 | 4814.25 | 215.32 |  |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2017-04-17 | 1085 | 1266 | 1261 | 1366 | 41.08 | 5019.08 | 4809 | 210.08 |  |  |  | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777 & Today I Replaced The 2, D.C.12Amp Fuse Link of The String-07--tive in AJB-100 of The Inverter-4 during The Period of 10:25 to 10:35 & string No3++tive line AJB No-103 Inverter No-4 During The period of 10:40 to 10:50, WO# | 26858207 | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
110 | 2017-04-18 | 113 | 1296 | 1323 | 1406 | 38.89 | 4176.89 | 4015.5 | 161.39 |  |  |  | Module cleaning done inverter -1&4 & Row-,A,B,C,D,&,A,B,C, & Total module cleaning -690 & Grid Failure From-07:45 to 07:50 & 10:13 to 10:23 & Today Morning time Grid Failure After Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal sutdown & Inverter No-1,2 P.M WO# | 26858589 26858656 26858771 | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2017-04-19 |  | 1277 | 1289 | 1381 | 40.63 | 3987.63 | 3814.5 | 173.13 |  |  |  | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704 & Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Inverter No-1,2 P.M WO# | 26858771 | 704 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2017-04-20 |  | 1266 | 1255 | 1331 | 40.02 | 3892.02 | 3717 | 175.02 |  |  |  | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Grid Failure From-15:17 to 15:29 WO# | 26859776 2688771 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2017-04-21 |  | 1289 | 1278 | 1346 | 40.13 | 3953.13 | 3790.5 | 162.63 | 3980 | 6.65 | 0.58333 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown WO# | 26858771 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2017-04-22 |  | 1250 | 1238 | 1320 | 39.33 | 3847.33 | 3667.5 | 179.83 | 3860 | 6.52 | 0.57702 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown WO# | 26858771 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2017-04-23 |  | 1147 | 1142 | 1190 | 36.97 | 3515.97 | 3360.75 | 155.22 | 3530 | 6.01 | 0.57247 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown &Grid Failure From-11:05 to 11:20 WO# | 26858771 26869751 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2017-04-24 |  | 1238 | 1221 | 1305 | 38.99 | 3802.99 | 3639 | 163.99 | 3840 | 6.39 | 0.58571 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 WO# | 26858771 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2017-04-25 |  | 1233 | 1221 | 1326 | 38.75 | 3818.75 | 3654.75 | 164 | 3840 | 6.5 | 0.5758 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, WO# | 26858771 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2017-04-26 |  | 1266 | 1227 | 1391 | 39.3 | 3923.3 | 3740.25 | 183.05 | 3935 | 6.74 | 0.56903 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -3&2, Row-L,M,N, & Total module cleaning -714, WO# | 26858771 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2017-04-27 |  | 1215 | 1209 | 1351 | 39.63 | 3814.63 | 3661.5 | 153.13 | 3840 | 6.86 | 0.54558 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -2, Row-I,J,K, & Total module cleaning -840, & Grid Failure From-11:45 to 11:55 & Today I Replaced The D.C.12Amp Fuse Link of The String-08--tive in AJB-115 of The Inverter-4 during The Period of 09:25 to 09:35 WO# | 26858771 26875944 26876163 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
120 | 2017-04-28 |  | 1182 | 1216 | 1330 | 38.96 | 3766.96 | 3609.75 | 157.21 | 3780 | 6.54 | 0.56333 | Inverter No- 1 ABB 250 KW Down at the site Due to AFPS-11C Card failure Inverter steal shutdown & Module cleaning done inverter -1, Row-,E,F,G,H, & Total module cleaning -777, & Grid Failure From-09:55 to 10:11 WO# | 26858771 26876993 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2017-04-29 | 28 | 1142 | 1187 | 1260 | 33.23 | 3650.23 | 3500.25 | 149.98 | 3670 | 6.25 | 0.57232 | Today Replased New AFPS-11C Card Resoled The Issue Inverter started 17:05 & Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, & Inverter No-3,4,& Transformer P.M, WO# | 26858771 | 624 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2017-04-30 | 945 | 1152 | 1182 | 1240 | 40.4 | 4559.4 | 4371.75 | 187.65 | 4600 | 6.38 | 0.70273 | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2017-05-01 | 961 | 1210 | 1193 | 1245 | 35.53 | 4644.53 | 4446.75 | 197.78 | 4680 | 6.5 | 0.70175 | Module cleaning done inverter -4, Row-,D,E,F,G, & Total module cleaning -704, WO# |  | 704 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2017-05-02 | 949 | 1159 | 1125 | 1179 | 36.73 | 4448.73 | 4284 | 164.73 | 4500 | 6.47 | 0.67789 | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 & Grid Failure From-07:07 to 08:08 WO# | 26886953 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2017-05-03 | 1018 | 1198 | 1164 | 1245 | 38.2 | 4663.2 | 4476.75 | 186.45 | 4710 | 6.42 | 0.71505 | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, WO# |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2017-05-04 | 1074 | 1261 | 1233 | 1326 | 38.47 | 4932.47 | 4757.25 | 175.22 | 4950 | 6.77 | 0.71264 | Module cleaning done inverter -3&2, Row-L,M,N, & Total module cleaning -714, WO# |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2017-05-05 | 1023 | 1199 | 1170 | 1255 | 37.28 | 4684.28 | 4489.5 | 194.78 | 4710 | 6.43 | 0.71394 | Module cleaning done inverter -2, Row-I,J,K, & Total module cleaning -840,WO# |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2017-05-06 | 1063 | 1249 | 1221 | 1356 | 38.06 | 4927.06 | 4732.5 | 194.56 | 4970 | 6.8 | 0.71236 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, WO# |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2017-05-07 | 1063 | 1255 | 1227 | 1341 | 39.7 | 4925.7 | 4722.75 | 202.95 | 4960 | 6.87 | 0.70368 | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2017-05-08 | 1046 | 1227 | 1232 | 1315 | 38.7 | 4858.7 | 4656.75 | 201.95 | 4890 | 6.75 | 0.70609 | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, WO# |  | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2017-05-09 | 1029 | 1210 | 1242 | 1285 | 38.72 | 4804.72 | 4617.75 | 186.97 | 4850 | 6.68 | 0.70765 | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704, WO# |  | 704 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2017-05-10 | 1023 | 1215 | 1249 | 1281 | 38.24 | 4806.24 | 4612.5 | 193.74 | 4840 | 6.64 | 0.71044 | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864 WO# |  | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2017-05-11 | 1001 | 1227 | 1221 | 1250 | 37.29 | 4736.29 | 4543.5 | 192.79 | 4780 | 6.5 | 0.71675 | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, WO# |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2017-05-12 | 1000 | 1204 | 1177 | 1194 | 35.97 | 4610.97 | 4414.5 | 196.47 | 4650 | 6.31 | 0.71825 | Module cleaning done inverter -3&2, Row-L,M,N, & Total module cleaning -714, WO# |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2017-05-13 | 300 | 385 | 378 | 378 | 10.15 | 1451.15 | 1367.25 | 83.9 | 1511 |  |  | Grid Failure From-06:54 to 13:50 WO# | 26901003 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2017-05-14 | 1001 | 1181 | 1165 | 1190 | 36.85 | 4573.85 | 4464 | 109.85 | 4620 | 6.25 | 0.72047 | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2017-05-15 | 1046 | 1238 | 1215 | 1245 | 36.7 | 4780.7 | 4510.5 | 270.2 | 4830 | 6.67 | 0.70579 | Module cleaning done inverter -2, Row-I,J,K, & Total module cleaning -840, Grid Failure From-10:49 to 10:57 WO# | 26905688 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2017-05-16 | 1012 | 1199 | 1182 | 1249 | 36.6 | 4678.6 | 4498.5 | 180.1 | 4730 | 6.45 | 0.71475 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, WO# |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2017-05-17 |  | 1057 | 1187 | 1281 | 36.08 | 3561.08 | 3428.25 | 132.83 | 3605 | 6.59 | 0.53318 | Today morning time Grid Failure after Inverter No-2 ABB 250 KW not started Due to Emergency stop inverter started Manually-09:15 & Today morning time Grid Failure after Inverter No-1 ABB 250 KW not started Due to D.C. Breaker Failure Inverter steal shut Down at the site & Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, & Grid Failure From-06:34 to 06:40 & 16:04 to 16:10 & 16:29 to 16:38 WO# | 26911932 26911933 26911934 26912030 26912031 | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2017-05-18 |  | 1187 | 1193 | 1275 | 37.5 | 3692.5 | 3538.5 | 154 | 3735 |  |  | Module cleaning done inverter -4 & Row-,D,E,F,G, & Total module cleaning -704, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,WO# | 26911934 | 704 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2017-05-19 |  | 1216 | 1255 | 1305 | 37.96 | 3813.96 | 3644.25 | 169.71 | 3855 |  |  | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,WO# | 26911934 | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2017-05-20 |  | 1244 | 1249 | 1301 | 37.64 | 3831.64 | 3658.5 | 173.14 | 3850 | 6.83 | 0.54941 | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26911934 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2017-05-21 |  | 1079 | 1063 | 1098 | 32.91 | 3272.91 | 3162 | 110.91 | 3320 | 5.82 | 0.55599 | Sunday No Module Cleaning & Grid Failure From-17:00 to 17:10 & Cloudy Day & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
145 | 2017-05-22 |  | 1188 | 1165 | 1185 | 35.64 | 3573.64 | 3399 | 174.64 | 3600 | 6.39 | 0.5491 | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,WO# | 26917427 | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2017-05-23 |  | 1192 | 1170 | 1189 | 35.51 | 3586.51 | 3438.75 | 147.76 | 3620 | 6.54 | 0.53949 | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,& Grid Failure From-14:20 to 14:26 & 15:20 to 15:30 WO# | 26917427 26919845 26919847 | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2017-05-24 |  | 1182 | 1153 | 1175 | 35.09 | 3545.09 | 3383.25 | 161.84 | 3581 | 6.58 | 0.53043 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, & Grid Failure From-08:30 to 08:41 WO# | 26917427 26919888 | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2017-05-25 |  | 1159 | 1120 | 1184 | 34.26 | 3497.26 | 3348 | 149.26 | 3535 |  |  | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624,& Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2017-05-26 |  | 1165 | 1125 | 1235 | 34.44 | 3559.44 | 3401.25 | 158.19 | 3600 |  |  | Module cleaning done inverter -4, Row-,D,E,F,G, & Total module cleaning -704,& Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 | 704 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2017-05-27 |  | 1096 | 1125 | 1240 | 36.17 | 3497.17 | 3375 | 122.17 | 3511 | 6.48 | 0.52809 | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure,& Yesterday Night time Grid Failure after morning time Inverter No-2&3 not wake up Due to Emergency Stop Reset The Err code Inverter started 08:17, WO# | 26917427 26929597 | 864 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2017-05-28 |  | 1052 | 1091 | 1134 | 33.73 | 3310.73 | 3165.75 | 144.98 | 3340 | 5.93 | 0.54896 | Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2017-05-29 |  | 921 | 955 | 968 | 27.66 | 2871.66 | 2724.75 | 146.91 | 2900 | 5.18 | 0.54566 | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, & Inverter No-1 ABB 250 KW Down at the site Due to D.C. Breaker Failure, WO# | 26917427 | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2017-05-30 | 853 | 1035 | 1035 | 1053 | 32.11 | 4008.11 | 3850.5 | 157.61 | 4075 | 5.82 | 0.68243 | Grid Failure From-11:25 to 11:47 & 13:41 to 13:46 WO# & No Module cleaning Bor Failure, | 26935692 26935694 |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2017-05-31 | 928 | 1119 | 1119 | 1190 | 35.05 | 4391.05 | 4209 | 182.05 | 4440 | 6.35 | 0.68149 | No Module cleaning Bor Failure, & Grid Failure From-07:06 to 07:15 WO# | 26935734 |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2017-06-01 | 864 | 1057 | 1029 | 1078 | 39.16 | 4067.16 | 3897.5 | 169.66 | 4100 | 5.89 | 0.67846 | No Module cleaning Bor Failure, |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2017-06-02 | 752 | 1075 | 1029 | 1090 | 27.15 | 3973.15 | 3806.25 | 166.9 | 4010 | 5.98 | 0.65358 | No Module cleaning Bor Failure, & Grid Failure From-09:28 to 09:42 & Today 11:39 Inverter No-1 ABB 250 KW Auto Trip Due to Emergency stop Reset The Err code Five time after Inverter started 12:38 WO# | 26940315 26942421 |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2017-06-03 | 860 | 1074 | 1012 | 1093 | 32.37 | 4071.37 | 3893.25 | 178.12 | 4115 | 5.85 | 0.68559 | Today I Replaced The 2, D.C.12Amp Fuse Link of The String-03--tive in AJB-100 of The Inverter-4 during The Period of 09:25 to 09:35 & string No8--tive line AJB No-103 Inverter No-4 During The period of 09:40 to 10:45,& No Module cleaning, Bor Failure,WO# |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
159 | 2017-06-04 | 904 | 1108 | 1035 | 1124 | 33.77 | 4204.77 | 4005.75 | 199.02 | 4250 | 5.96 | 0.69502 | cloudy day & Sunday No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
160 | 2017-06-05 | 820 | 983 | 938 | 1013 | 28.92 | 3782.92 | 3642 | 140.92 | 3840 | 5.8 | 0.64529 | Today shut Down the plant 14:53 for New UPS Installation Successfully Installation UPS After plant started-15:26 WO# & Cloudy Day | 26947491 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
161 | 2017-06-06 | 916 | 1018 | 950 | 1099 | 32.17 | 4015.17 | 3831.75 | 183.42 | 4060 | 5.74 | 0.68939 | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714, & Grid Failure From-07:20 to 07:26 & Grid Failure After Inverter No-2&3 not wake up Due to Emergency stop Reset the Err code Inverter started-08:23 WO# | 26948606 26948608 | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2017-06-07 | 961 | 1103 | 1040 | 1144 | 32.58 | 4280.58 | 4087.5 | 193.08 | 4325 | 6.01 | 0.7014 | Module cleaning done inverter -2 & Row-,I,J,K, & Total module cleaning -840, & Cloudy Day |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
163 | 2017-06-08 | 899 | 1034 | 973 | 1139 | 30 | 4075 | 3904.5 | 170.5 | 4110 | 5.6 | 0.71533 | Module cleaning done inverter -1 & Row-,E,F,G,H, & Total module cleaning -777, & Cloudy Day |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
164 | 2017-06-09 | 820 | 944 | 910 | 1049 | 29.89 | 3752.89 | 3614.25 | 138.64 | 3802 | 5.15 | 0.71954 | Module cleaning done inverter -1&4, Row-,A,B,C,D,&,A,B,C, & Total module cleaning -624, & Cloudy Day |  | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
165 | 2017-06-10 | 825 | 967 | 933 | 1038 | 29.04 | 3792.04 | 3597 | 195.04 | 3835 | 4.88 | 0.76595 | Cloudy & Rainy Day & Module Clean by Rain & Grid Failure From-07:27 to 07:37 WO# | 26954215 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
166 | 2017-06-11 | 995 | 1165 | 1113 | 1230 | 35.31 | 4538.31 | 4355.25 | 183.06 | 4575 | 6.3 | 0.70779 | Cloudy & Rainy Day & Module Clean by Rain & Grid Failure From-07:22 to 07:32 WO# | 26954295 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
167 | 2017-06-12 | 995 | 1176 | 1137 | 1245 | 36.28 | 4589.28 | 4374 | 215.28 | 4620 | 6.33 | 0.71136 | Cloudy & Rainy Day & Module Clean by Rain |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
168 | 2017-06-13 | 1006 | 1175 | 1136 | 1144 | 36.86 | 4497.86 | 4353.75 | 144.11 | 4525 | 6.42 | 0.68697 | Module cleaning done inverter -4 & Row-,A,B,C,D,E,F,G, & Total module cleaning -992, & Cloudy Day |  | 992 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
169 | 2017-06-14 | 990 | 1165 | 1119 | 1255 | 36.58 | 4565.58 | 4382.25 | 183.33 | 4595 | 6.42 | 0.69759 | Module cleaning done inverter -4 & Row-,H,I,J,K,L, & Total module cleaning -864, & Cloudy Day |  | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
170 | 2017-06-15 | 932 | 1091 | 1052 | 1164 | 33.12 | 4272.12 | 4087.5 | 184.62 | 4310 | 5.97 | 0.70365 | Today I Replaced The D.C.12Amp Fuse Link of The String-03++tive in AJB-112 of The Inverter-3 during The Period of 09:10 to 09:20 & string no-3++tive line AJB-117 Inverter no-3 During the period of 9:25 to 9:35 & Cloudy Day WO# |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
171 | 2017-06-16 | 905 | 1063 | 1063 | 1190 | 33.21 | 4254.21 | 4084.5 | 169.71 | 4290 | 5.91 | 0.70749 | Today I Replaced The D.C.12Amp Fuse Link of The String-04++tive in AJB-104 of The Inverter-4 during The Period of 09:00 to 09:10 & string no-2--tive line AJB-105 Inverter no-4 During the period of 9:15 to 9:25 & Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690 & Cloudy Day WO# |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
172 | 2017-06-17 | 876 | 1040 | 1051 | 1149 | 31.97 | 4147.97 | 3967.5 | 180.47 | 4175 | 5.72 | 0.7114 | Module cleaning done inverter -3&2 & Row-,L,M,N, & Total module cleaning -714,& cloudy Day |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
173 | 2017-06-18 | 860 | 1029 | 1041 | 1119 | 31.9 | 4080.9 | 3896.25 | 184.65 | 4115 | 5.68 | 0.70611 | cloudy day & Sunday No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
174 | 2017-06-19 | 836 | 995 | 994 | 1074 | 28.91 | 3927.91 | 3786.75 | 141.16 | 3970 | 5.43 | 0.7126 | Module cleaning done inverter -3 & Row-,M,N,O,P,Q,R,S,T, & Total module cleaning -992, & Cloudy Day |  | 992 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
175 | 2017-06-20 | 803 | 950 | 962 | 1013 | 29.76 | 3757.76 | 3588 | 169.76 | 3800 | 5.21 | 0.71088 | Module cleaning done inverter -2 & Row-,I,J,K,L, & Total module cleaning -1092, & Cloudy Day |  | 992 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
176 | 2017-06-21 | 820 | 961 | 961 | 1043 | 30.63 | 3815.63 | 3732.75 | 82.88 | 3860 | 5.29 | 0.71119 | Module cleaning done inverter -1 & Row-,A,B,C,D,E,F,G,H, & Total module cleaning -1113, & Grid Failure From-08:26 to 08:36 & Fully Cloudy Day | 26989259 | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
177 | 2017-06-22 | 557 | 850 | 870 | 937 | 26.62 | 3240.62 | 3214.5 | 26.12 | 3500 | 4.67 | 0.73047 | Rainy & cloudy day, No Module clean by Rain |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
178 | 2017-06-23 | 905 | 1063 | 1066 | 1140 | 33.77 | 4207.77 | 4045.5 | 162.27 | 4251 | 5.72 | 0.72435 | Rainy & cloudy day, No Module clean by Rain & Grid Failure From-08:to 08:50 & 10:15 TO 10:20 WO# |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
179 | 2017-06-24 | 910 | 1052 | 1052 | 1149 | 34.01 | 4197.01 | 3964.5 | 232.51 | 4240 | 5.63 | 0.73402 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
180 | 2017-06-25 | 842 | 972 | 978 | 1018 | 29.84 | 3839.84 | 3745.5 | 94.34 | 3884 | 5.21 | 0.7266 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
181 | 2017-06-26 | 781 | 882 | 893 | 932 | 28.95 | 3516.95 | 3300.75 | 216.2 | 3563 | 4.75 | 0.7311 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
182 | 2017-06-27 | 384 | 430 | 430 | 409 | 13.49 | 1666.49 | 1613.25 | 53.24 | 1734 | 2.34 | 0.72225 | Rainy & cloudy day & Grid Failure From-11:01 to 11:11 & 13:18 to 13:47 & 13:53 to 14:33 & 14:42 to 16:01 & 16:57 to 17:54 WO# | 26997787 26997809 26997810 26997811 26997888 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
183 | 2017-06-28 | 673 | 769 | 774 | 816 | 22.68 | 3054.68 | 2889 | 165.68 | 3101 | 4.11 | 0.73538 | Rainy & cloudy day & Grid Failure From-11:08 to 11:26 WO# | 27002161 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
184 | 2017-06-29 | 565 | 639 | 645 | 670 | 19.1 | 2538.1 | 2412.75 | 125.35 | 2580 | 3.35 | 0.75063 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
185 | 2017-06-30 | 605 | 644 | 655 | 726 | 21.39 | 2651.39 | 2506.5 | 144.89 | 2722 | 3.61 | 0.73491 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
187 | 2017-07-01 | 277 | 305 | 300 | 313 | 8.31 | 1203.31 | 1090 | 113.31 | 1242 | 1.52 | 0.7964 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
188 | 2017-07-02 | 204 | 232 | 237 | 250 | 5.77 | 928.77 | 738 | 190.77 | 960 | 1.23 | 0.76071 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
189 | 2017-07-03 | 192 | 221 | 181 | 203 | 6.09 | 803.09 | 790.5 | 12.59 | 882 | 1.18 | 0.72852 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
190 | 2017-07-04 | 718 | 836 | 831 | 882 | 23.85 | 3290.85 | 3091.5 | 199.35 | 3332 | 4.33 | 0.75001 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
191 | 2017-07-05 | 848 | 1001 | 984 | 1064 | 32.41 | 3929.41 | 3746.25 | 183.16 | 3952 | 5.32 | 0.72403 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
192 | 2017-07-06 | 870 | 1029 | 1017 | 1089 | 31.92 | 4036.92 | 3867 | 169.92 | 4100 | 5.58 | 0.71615 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
193 | 2017-07-07 | 865 | 1023 | 1007 | 1088 | 33.01 | 4016.01 | 3863.25 | 152.76 | 4042 | 5.53 | 0.7124 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
194 | 2017-07-08 | 939 | 1114 | 1085 | 1195 | 35.47 | 4368.47 | 4224.75 | 143.72 | 4412 | 5.9 | 0.72885 | Rainy & cloudy day & Grid Failure From-09:52 to 09:56 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
195 | 2017-07-09 | 893 | 1063 | 1046 | 1134 | 38.83 | 4174.83 | 3957 | 217.83 | 4204 | 5.73 | 0.71509 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
196 | 2017-07-10 | 910 | 1068 | 1057 | 1149 | 36.46 | 4220.46 | 4077.75 | 142.71 | 4252 | 5.77 | 0.71824 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
197 | 2017-07-11 | 498 | 571 | 560 | 590 | 16.62 | 2235.62 | 2109.75 | 125.87 | 2294 | 2.8 | 0.79852 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
198 | 2017-07-12 | 435 | 503 | 486 | 519 | 14.08 | 1957.08 | 1851.75 | 105.33 | 1994 | 2.47 | 0.78683 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
199 | 2017-07-13 | 628 | 730 | 724 | 771 | 25.46 | 2878.46 | 2727 | 151.46 | 2932 | 3.82 | 0.74809 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
200 | 2017-07-14 | 378 | 441 | 424 | 459 | 13.28 | 1715.28 | 1611 | 104.28 | 1772 | 2.17 | 0.7959 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
201 | 2017-07-15 | 328 | 429 | 418 | 448 | 13.27 | 1636.27 | 1557 | 79.27 | 1742 | 2.21 | 0.76826 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
202 | 2017-07-16 | 368 | 379 | 368 | 368 | 10.02 | 1493.02 | 1332 | 161.02 | 1482 | 1.83 | 0.78931 | Rainy & cloudy day & Grid Failure From-16:50 to 17:18 & 17:26 to 17:33 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
203 | 2017-07-17 | 712 | 837 | 825 | 882 | 24.94 | 3280.94 | 3123 | 157.94 | 3322 | 4.52 | 0.71633 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
204 | 2017-07-18 | 871 | 1029 | 989 | 1099 | 35.06 | 4023.06 | 3848.25 | 174.81 | 4062 | 5.56 | 0.71206 | Rainy & cloudy day & Grid Failure From-15:00 to 15:03 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
205 | 2017-07-19 | 848 | 989 | 956 | 1058 | 30.44 | 3881.44 | 3720.75 | 160.69 | 3922 | 5.35 | 0.71451 | Rainy & cloudy day & Grid Failure From-09:44 to 09:47 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
206 | 2017-07-20 | 480 | 560 | 537 | 585 | 15.73 | 2177.73 | 2083.5 | 94.23 | 2242 | 2.92 | 0.74835 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
207 | 2017-07-21 | 848 | 995 | 955 | 1079 | 29.25 | 3906.25 | 3735 | 171.25 | 3942 | 5.34 | 0.7195 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
208 | 2017-07-22 | 74 | 96 | 91 | 80 | 1.42 | 342.42 | 243.75 | 98.67 | 398 | 0.61 | 0.63592 | Rainy & cloudy day & Grid Failure From-09:02 to 09:19 & 15:24 to 15:27 & 15:43 to 15:48 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
209 | 2017-07-23 | 231 | 277 | 265 | 278 | 4.95 | 1055.95 | 941 | 114.95 | 1112 | 1.38 | 0.78538 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
210 | 2017-07-24 | 102 | 124 | 125 | 121 | 1.54 | 473.54 | 375 | 98.54 | 523 | 0.716 | 0.71194 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
211 | 2017-07-25 | 142 | 170 | 164 | 166 | 2.64 | 644.64 | 543 | 101.64 | 693 | 0.907 | 0.7447 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
212 | 2017-07-26 | 73 | 90 | 85 | 86 | 1 | 335 | 231.75 | 103.25 | 386 | 0.59 | 0.63766 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
213 | 2017-07-27 | 136 | 176 | 169 | 166 | 2.57 | 649.57 | 537.75 | 111.82 | 703 | 0.981 | 0.69846 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
214 | 2017-07-28 | 543 | 650 | 628 | 680 | 14.4 | 2515.4 | 2379.75 | 135.65 | 2560 | 3.26 | 0.76538 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
215 | 2017-07-29 | 774 | 932 | 893 | 988 | 29.06 | 3616.06 | 3416.25 | 199.81 |  |  |  | Rainy & cloudy day & 11 KV Switch yard Site GOD Switch Repleced 'R' Phase cable & Luges, |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
216 | 2017-07-30 | 577 | 690 | 690 | 731 | 20.53 | 2708.53 | 2618.25 | 90.28 |  |  |  | Today I Replaced The 2 D.C.12Amp Fuse Link of The String-04--tive in AJB-113 of The Inverter-3 during The Period of 09:40 to 09:50 & string no-2++tive line AJB-101 Inverter no-4 During the period of 10:50 to 11:00 &Today Replaced 1 MC4 Connecter string No-8 AJB No-117 Inverter No-3 Durring The period 9:30 to 9:40 & Grid Failure From-14:23 to 14:36 & Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
217 | 2017-07-31 | 497 | 594 | 593 | 620 | 17.94 | 2321.94 | 2181 | 140.94 |  |  |  | Grid Failure From-16:49 to 17:02 & Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
219 | 2017-08-01 | 769 | 910 | 910 | 988 | 24.13 | 3601.13 | 3447.75 | 153.38 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
220 | 2017-08-02 | 560 | 661 | 667 | 685 | 19.08 | 2592.08 | 2469.75 | 122.33 |  |  |  | Grid Failure From-11:20 to 17:24,16:41 to 16:44 & 16:47 to 16:57 & Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
221 | 2017-08-03 | 842 | 990 | 996 | 1069 | 31.45 | 3928.45 | 3745.5 | 182.95 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
222 | 2017-08-04 | 775 | 916 | 910 | 978 | 29.92 | 3608.92 | 3451.5 | 157.42 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
223 | 2017-08-05 | 531 | 616 | 616 | 635 | 19.24 | 2417.24 | 2292 | 125.24 |  |  |  | Grid Failure From-8:53 to 9:33 & Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
224 | 2017-08-06 | 871 | 1023 | 1023 | 1073 | 31.91 | 4021.91 | 3849 | 172.91 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
225 | 2017-08-07 | 537 | 633 | 639 | 323 | 19.19 | 2151.19 | 2013 | 138.19 |  |  |  | Today Morning time Inverter No:-4 not wake up due to error code (Run Disable:-8194).five time reset the Err code After Inverter started 14:50 & Rainy & cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
226 | 2017-08-08 | 718 | 843 | 842 | 897 | 25.89 | 3325.89 | 3187.5 | 138.39 |  |  |  | Rainy & cloudy day & Morning time plant checking time 1 module crack found . Inverter-4 Row-D Up Line module No-5 Sr No :-BPC10BU1109685(By mistack Module Crack by garden boy) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
227 | 2017-08-09 | 808 | 944 | 945 | 1023 | 30.01 | 3750.01 | 3581.25 | 168.76 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
228 | 2017-08-10 | 797 | 950 | 949 | 1039 | 30.76 | 3765.76 | 3603.75 | 162.01 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
229 | 2017-08-11 | 611 | 780 | 781 | 851 | 25.85 | 3048.85 | 2908.5 | 140.35 |  |  |  | Today Inverter No :-1 ABB 250kw morning time not wake up due to emergency stop reset the Errore code Inverter started at:-09:14 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 2017-08-12 | 576 | 678 | 683 | 721 | 20.57 | 2678.57 | 2542.5 | 136.07 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
231 | 2017-08-13 | 611 | 712 | 719 | 751 | 21.35 | 2814.35 | 2669.25 | 145.1 |  |  |  | Grid Failure From-09:23 to 09:33 & Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
232 | 2017-08-14 | 690 | 815 | 813 | 857 | 26.64 | 3201.64 | 3047.25 | 154.39 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
233 | 2017-08-15 | 791 | 921 | 922 | 968 | 28.76 | 3630.76 | 3444.75 | 186.01 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
234 | 2017-08-16 | 910 | 1074 | 1080 | 1157 | 33.53 | 4254.53 | 4101.75 | 152.78 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
235 | 2017-08-17 | 843 | 995 | 995 | 1058 | 32.07 | 3923.07 | 3759 | 164.07 |  |  |  | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
236 | 2017-08-18 | 904 | 1069 | 1063 | 1144 | 34.3 | 4214.3 | 4039.5 | 174.8 |  |  |  | Module cleaning has Been done In Row-A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -792 |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 2017-08-19 | 588 | 690 | 689 | 731 | 21.17 | 2719.17 | 2600.25 | 118.92 |  |  |  | Module cleaning has Been done In Row-G,H,I,J,K,L Inverter N0-4 & Total module cleaning -1122 |  | 1122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 2017-08-20 | 249 | 293 | 300 | 308 | 5.67 | 1155.67 | 1033.5 | 122.17 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
239 | 2017-08-21 | 876 | 1046 | 1040 | 1129 | 31.99 | 4122.99 | 3929.25 | 193.74 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
240 | 2017-08-22 | 809 | 944 | 939 | 1043 | 30 | 3765 | 3600 | 165 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
241 | 2017-08-23 | 356 | 413 | 418 | 428 | 12.3 | 1627.3 | 1509.75 | 117.55 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
242 | 2017-08-24 | 885 | 1018 | 1012 | 1109 | 33.27 | 4057.27 | 3861.75 | 195.52 |  |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
243 | 2017-08-25 | 955 | 1125 | 1120 | 1225 | 35.7 | 4460.7 | 4288.5 | 172.2 | 4512 | 6.13 | 0.7174 | Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
244 | 2017-08-26 | 820 | 949 | 961 | 1013 | 30.23 | 3773.23 | 3609 | 164.23 | 3800 | 4.95 | 0.74822 | Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
245 | 2017-08-27 | 616 | 730 | 723 | 771 | 23.09 | 2863.09 | 2723.25 | 139.84 | 2900 |  |  | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
246 | 2017-08-28 | 639 | 752 | 752 | 812 | 26.44 | 2981.44 | 2808.75 | 172.69 | 3032 | 4.12 | 0.71727 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
247 | 2017-08-29 | 565 | 661 | 667 | 705 | 21.72 | 2619.72 | 2478 | 141.72 | 2674 | 3.48 | 0.74892 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
248 | 2017-08-30 | 560 | 650 | 656 | 711 | 20.61 | 2597.61 | 2433 | 164.61 | 2642 | 3.54 | 0.72741 | Grid Failure From 11:14 to 11:24 , Rainy & Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
249 | 2017-08-31 | 430 | 498 | 497 | 509 | 15.37 | 1949.37 | 1849 | 100.37 | 2000 | 2.55 | 0.76444 | Grid Failure From 10:02 to 10:07 & 11:15 to 11:18 ,Rainy & Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
251 | 2017-09-01 | 836 | 983 | 978 | 1074 | 32.97 | 3903.97 | 3729.75 | 174.22 | 3942 | 5.43 | 0.70757 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
252 | 2017-09-02 | 402 | 470 | 475 | 489 | 14.53 | 1850.53 | 1736 | 114.53 | 1910 | 2.44 | 0.76295 | Grid Failure From 07:36 to 07:39, Rainy & Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
253 | 2017-09-03 | 594 | 689 | 696 | 725 | 21.33 | 2725.33 | 2566 | 159.33 | 2772 | 3.64 | 0.74224 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
254 | 2017-09-04 | 678 | 798 | 797 | 847 | 25.36 | 3145.36 | 2998 | 147.36 | 3190 | 4.21 | 0.73852 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
255 | 2017-09-05 | 899 | 1062 | 1057 | 1129 | 35.63 | 4182.63 | 4013.25 | 169.38 | 4230 | 5.78 | 0.71329 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
256 | 2017-09-06 | 910 | 1069 | 1074 | 1129 | 35.61 | 4217.61 | 4013.25 | 204.36 | 4242 | 5.83 | 0.70918 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
257 | 2017-09-07 | 1001 | 1187 | 1182 | 1240 | 39.49 | 4649.49 | 4482 | 167.49 | 4690 | 6.6 | 0.6926 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
258 | 2017-09-08 | 916 | 1080 | 1091 | 1109 | 36.1 | 4232.1 | 4046 | 186.1 | 4255 | 5.89 | 0.7041 | Module cleaning has Been done In Row-A,B,C Inverter N0-4 & Total module cleaning -288 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2017-09-09 | 994 | 1142 | 1136 | 1230 | 38.96 | 4540.96 | 4362 | 178.96 | 4581 | 6.89 | 0.64803 | Module cleaning has Been done In Row-D,E,F Inverter N0-4 & Total module cleaning -504 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 2017-09-10 | 792 | 933 | 933 | 963 | 31.61 | 3652.61 | 3489 | 163.61 | 3685 | 5.05 | 0.71121 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
261 | 2017-09-11 | 826 | 972 | 967 | 1028 | 33.28 | 3826.28 | 3656.25 | 170.03 | 3860 | 5.38 | 0.69929 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
262 | 2017-09-12 | 842 | 1001 | 1001 | 1063 | 34.7 | 3941.7 | 3779 | 162.7 | 3965 | 5.6 | 0.69009 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
263 | 2017-09-13 | 667 | 780 | 780 | 807 | 28.03 | 3062.03 | 2924 | 138.03 | 3120 | 4.41 | 0.68955 | Grid Failure From 14:31 to 14:35 & 14:42 to 14:49 ,Rainy & Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
264 | 2017-09-14 | 893 | 1052 | 1045 | 1093 | 34.21 | 4117.21 | 3937 | 180.21 | 4153 | 5.71 | 0.70889 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
265 | 2017-09-15 | 922 | 1085 | 1080 | 1139 | 36.73 | 4262.73 | 4089 | 173.73 | 4290 | 5.98 | 0.69921 | Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
266 | 2017-09-16 | 565 | 656 | 662 | 701 | 22.62 | 2606.62 | 2460.75 | 145.87 |  |  |  | Grid Failure From 10:38 to 10:43 ,Rainy & Cloudy day & Today Night Many Time Grid Failure After High Voltage, 2 Power supply Failure, 1 SEEDS, & 2. SCADA |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
267 | 2017-09-17 | 775 | 899 | 893 | 922 | 29.03 | 3518.03 | 3362.25 | 155.78 |  |  |  | Grid Failure From 14:08 to 14:14 ,Rainy & Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
268 | 2017-09-18 | 904 | 1051 | 1046 | 1109 | 36.52 | 4146.52 | 3972 | 174.52 |  |  |  | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
269 | 2017-09-19 | 669 | 780 | 774 | 776 | 25.19 | 3024.19 | 2889 | 135.19 |  |  |  | Grid Failure From 10:35 to 10:40 , 11:33 to 12:44 , 14:20 to 15:14, Cloudy day & Grid Failure After High voltage MOXA SEEDA Unit power supply Failure, |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
270 | 2017-09-20 | 990 | 1182 | 1176 | 1215 | 39.44 | 4602.44 | 4429.5 | 172.94 | 4643 |  |  | Grid Failure From 08:43 to 08:49 & 10:17 to 10:22 ,Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
271 | 2017-09-21 | 707 | 690 | 690 | 822 | 27.14 | 2936.14 | 2793.75 | 142.39 | 2994 |  |  | Grid Failure From 17:25 to 17:27, Fully Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
272 | 2017-09-22 | 587 | 638 | 667 | 736 | 24.22 | 2652.22 | 2526 | 126.22 | 2710 |  |  | Today AMC MaintanCe for ABB Inverter no-1,2,3, |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 2017-09-23 | 1001 | 1188 | 1182 | 1240 | 40.33 | 4651.33 | 4463.25 | 188.08 | 4700 |  |  | GrId Failure From-17:13 to 17:18 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 2017-09-24 | 808 | 944 | 944 | 967 | 32.16 | 3695.16 | 3526.5 | 168.66 | 3734 |  |  | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
275 | 2017-09-25 | 962 | 1063 | 1062 | 1144 | 38.4 | 4269.4 | 4098 | 171.4 | 4321 |  |  | Module cleaning has Been done In Row-A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -792 |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 2017-09-26 | 921 | 1091 | 1086 | 1165 | 36.28 | 4299.28 | 4119 | 180.28 | 4332 |  |  | Module cleaning has Been done In Row-,G,H,I,J,K,L, Inverter N0-4 & Total module cleaning -1062 & Grid Failure From-10:42 to 10:50 & 12:01 to 12:06 |  | 1062 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2017-09-27 | 995 | 1181 | 1187 | 1255 | 40.28 | 4658.28 | 4471.5 | 186.78 | 4681 |  |  | Module cleaning done inverter -3&Trackers, Row-O,P,Q,R,S,T & Total module cleaning -690, |  | 690 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 2017-09-28 | 1018 | 1154 | 1170 | 1290 | 41.02 | 4673.02 | 4491 | 182.02 | 4704 |  |  | Module cleaning done inverter -3, Row-M,N & Total module cleaning -462, Grid Failure from 8:25 to 8:45,12:00 to 12:04, 16:33 to 16:36 |  | 462 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2017-09-29 | 1051 | 1249 | 1267 | 1326 | 42.18 | 4935.18 | 4725.75 | 209.43 | 4980 |  |  | Module cleaning done inverter -2, Row-K,L & Total module cleaning -525, Grid Failure from 7:20 to 7:30 |  | 525 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 2017-09-30 | 1040 | 1215 | 1210 | 1290 | 41.82 | 4796.82 | 4598.25 | 198.57 | 4840 |  |  | Module cleaning done inverter -2, Row-J,I & Total module cleaning -567, |  | 567 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 2017-10-01 | 1041 | 1267 | 1249 | 1290 | 41.64 | 4888.64 | 4690.5 | 198.14 | 4934 |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2017-10-02 | 1034 | 1249 | 1227 | 1240 | 41.01 | 4791.01 | 4596 | 195.01 | 4830 |  |  | Today I Replaced The 3 D.C.12Amp Fuse, Link of The String-02++tive in AJB-101 of The Inverter-4 during The Period of 17:45 to 17:50 & string no-6--tive line AJB-104 Inverter no-4 During the period of 18:00 to 18:05 & string 02--tive line AJB-105 Inverter No-4 Durring The period 18:10 to 18:15 & Module cleaning done inverter -1, Row-A,B,C,D,E,F,G,H, & Total module cleaning -1113, |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 2017-10-03 | 1012 | 1187 | 1170 | 1230 | 39.47 | 4638.47 | 4429.5 | 208.97 | 4771 |  |  | Module cleaning has Been done In Row-A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -792 |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2017-10-04 | 1035 | 1210 | 1193 | 1300 | 40.13 | 4778.13 | 4596 | 182.13 | 4814 |  |  | Module cleaning has Been done In Row-G,H,I,J, Inverter N0-4 & Total module cleaning -774 & Grid Failure from 17:10 to 17:19 |  | 774 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2017-10-05 | 1012 | 1193 | 1170 | 1296 | 40.13 | 4711.13 | 4516.5 | 194.63 | 4744 |  |  | Module cleaning has Been done In Row-K,L, & R,S,T, & trackers ,Inverter N0-4,3, & Total module cleaning -516 & Grid Failure from 10:45 to 10:47 |  | 516 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2017-10-06 | 859 | 989 | 990 | 1063 | 34.67 | 3935.67 | 3773.25 | 162.42 | 3985 |  |  | Module cleaning has Been done In Row-,M,N,O,P,Q, Inverter N0-3 & Total module cleaning -924 & Grid Failure from 13:08 to 13:35 |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2017-10-07 | 972 | 1160 | 1159 | 1235 | 39.25 | 4565.25 | 4379.25 | 186 | 4610 |  |  | Module cleaning has Been done In Row-J,K,L, Inverter N0-2 & Total module cleaning -819 & Grid Failure from 10:46 to 10:50 |  | 819 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 2017-10-08 | 1007 | 1209 | 1193 | 1260 | 40.65 | 4709.65 | 4513.5 | 196.15 | 4750 |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 2017-10-09 | 887 | 1063 | 1040 | 1089 | 35.85 | 4114.85 | 3950.25 | 164.6 | 4170 |  |  | Module cleaning has Been done In Row-F,G,H,I, Inverter N0-1,2 & Total module cleaning -903 & Grid Failure from 13:08 to 13:11 |  | 903 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2017-10-10 | 860 | 1006 | 983 | 1043 | 35.41 | 3927.41 | 3753.75 | 173.66 | 3970 |  |  | Module cleaning has Been done In (Row-A,B,C,D,E Inverter N0-1), (Row-A,B Inverter N0-4) & Total module cleaning -642 & Grid Failure from-11:13 to 11:18 & 13:46 to 14:26 |  | 642 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 2017-10-11 | 429 | 486 | 481 | 494 | 15.43 | 1905.43 | 1788 | 117.43 | 1960 |  |  | Fully cloudy day & Borwall Failure No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
293 | 2017-10-12 | 402 | 453 | 447 | 459 | 13.96 | 1774.96 | 1650 | 124.96 | 1830 |  |  | Fully cloudy day & Borwall Failure No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
294 | 2017-10-13 | 667 | 769 | 752 | 801 | 26 | 3015 | 2880 | 135 | 3082 |  |  | Fully cloudy day & Borwall Failure No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
295 | 2017-10-14 | 949 | 1119 | 1096 | 1164 | 37.57 | 4365.57 | 4182.25 | 183.32 | 4411 |  |  | Fully cloudy day & Borwall Failure No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
296 | 2017-10-15 | 933 | 1097 | 1069 | 1134 | 36.94 | 4269.94 | 4091.25 | 178.69 | 4320 |  |  | Sunday No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2017-10-16 | 990 | 1165 | 1136 | 1220 | 39.46 | 4550.46 | 4369.5 | 180.96 | 4600 |  |  | Module cleaning has Been done In Row-G,H,I, Inverter N0-4& Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2017-10-17 | 1017 | 1198 | 1164 | 1275 | 40.26 | 4694.26 | 4498.5 | 195.76 | 4740 |  |  | No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2017-10-18 | 1029 | 1221 | 1188 | 1306 | 41.25 | 4785.25 | 4588.5 | 196.75 | 4830 |  |  | No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 2017-10-19 | 973 | 1142 | 1114 | 1209 | 39.84 | 4477.84 | 4285.5 | 192.34 | 4523 |  |  | Holiday No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2017-10-20 | 842 | 984 | 961 | 1008 | 35.17 | 3830.17 | 3669.75 | 160.42 | 3890 |  |  | Grid Failure from :- 9:07 to 9:10, 9:33 to 9:36, 11:20 to 11:32, 12:44 to 12:48, 13:30 to 13:37, 14:11 to 14:17 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2017-10-21 | 848 | 989 | 961 | 998 | 35.91 | 3831.91 | 3660.75 | 171.16 | 3880 |  |  | Grid Failure from:-8:13 to 8:29, 9:23 to 9:34, 13:45 to 13:54 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2017-10-22 | 984 | 1153 | 1125 | 1245 | 40.7 | 4547.7 | 4356.75 | 190.95 | 4590 |  |  | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
304 | 2017-10-23 | 966 | 1148 | 1125 | 1240 | 40.78 | 4519.78 | 4334.25 | 185.53 | 4565 |  |  | Module cleaning has Been done In Row-O,P,Q,R,S,T, Inverter N0-3 & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 2017-10-24 | 950 | 1119 | 1136 | 1210 | 39.82 | 4454.82 | 4266 | 188.82 | 4492 |  |  | Module cleaning has Been done In Row-L,M,N, Inverter N0-3,2 & Total module cleaning -714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2017-10-25 | 973 | 1176 | 1199 | 1240 | 40.74 | 4628.74 | 4442.25 | 186.49 | 4670 |  |  | No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2017-10-26 | 938 | 1125 | 1147 | 1169 | 39.59 | 4418.59 | 4230 | 188.59 | 4460 |  |  | Module cleaning has Been done In Row-,I,J,K, Inverter N0-2 & Total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2017-10-27 | 871 | 1069 | 1057 | 1069 | 37.1 | 4103.1 | 3926.25 | 176.85 | 4150 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2017-10-28 | 876 | 1091 | 1069 | 1073 | 37.37 | 4146.37 | 3976.5 | 169.87 | 4200 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2017-10-29 | 848 | 1057 | 1024 | 1028 | 36.24 | 3993.24 | 3825.75 | 167.49 | 4042 |  |  | GrId Failure From-08:14 to 08:18 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2017-10-30 | 888 | 1103 | 1074 | 1084 | 38.01 | 4187.01 | 4006.5 | 180.51 | 4230 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2017-10-31 | 898 | 1108 | 1074 | 1089 | 37.84 | 4206.84 | 4022.25 | 184.59 | 4243 |  |  | Module cleaning has Been done In Row-E,F,G,H, Inverter N0-1 & Total module cleaning -777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 2017-11-01 | 888 | 1040 | 1001 | 993 | 36.39 | 3958.39 | 3790.5 | 167.89 | 4020 |  |  | Module cleaning has Been done In Row-A,B,C,D, Inverter N0-1 & Total module cleaning -336 & Grid Failure From :-16:33 to 16:36 & Replaced New Earthnet Moxa switch |  | 336 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2017-11-02 | 882 | 1029 | 995 | 993 | 36.01 | 3935.01 | 3756 | 179.01 | 3980 |  |  | Module cleaning has Been done In Row-A,B,C,D, Inverter N0-4 & Total module cleaning -432 |  | 432 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2017-11-03 | 921 | 1080 | 1040 | 1071 | 37.2 | 4149.2 | 3971.25 | 177.95 | 4202 |  |  | Module cleaning has Been done In Row-,E,F,G,H, Inverter N0-4 & Total module cleaning -756 |  | 756 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2017-11-04 | 865 | 921 | 888 | 1025 | 35.3 | 3734.3 | 3559.5 | 174.8 | 3790 |  |  | Module cleaning has Been done In Row-I,J, Inverter N0-4 & Total module cleaning -378 |  | 378 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2017-11-05 | 815 | 938 | 910 | 968 | 33.2 | 3664.2 | 3498 | 166.2 | 3710 |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 2017-11-06 | 915 | 1075 | 1029 | 1144 | 37.53 | 4200.53 | 4012.5 | 188.03 | 4240 |  |  | Inverter 1 &2 & Main transformer replaced new silica gel ,Today install new cable for ups to scada. |  |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2017-11-07 | 888 | 1017 | 978 | 1104 | 36.57 | 4023.57 | 3853.5 | 170.07 | 4080 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2017-11-08 | 876 | 1029 | 983 | 1099 | 37.36 | 4024.36 | 3837.75 | 186.61 | 4060 |  |  | Module cleaning has Been done In Row-K,L, & Trackers Inverter N0-4 & Total module cleaning -348 |  | 348 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2017-11-09 | 814 | 944 | 922 | 993 | 35.58 | 3708.58 | 3540 | 168.58 | 3750 |  |  | Today Replaced New Plus Din Rail power supply For AJB & SCADA,& Module cleaning has Been done In Row-,O,P,Q,R,S,T, & Trackers Inverter N0-3 & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2017-11-10 | 797 | 922 | 944 | 962 | 35.34 | 3660.34 | 3496.5 | 163.84 | 3710 |  |  | Module cleaning has Been done In Row-K,L,M, & Trackers Inverter N0-2&3 & Total module cleaning -777 & Grid Failure From-16:46 to 16:52 |  | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2017-11-11 | 798 | 955 | 955 | 963 | 35.28 | 3706.28 | 3533.25 | 173.03 | 3740 |  |  | Module cleaning has Been done In Row-I,J,K, & Inverter N0-2 & Total module cleaning -840 & Grid Failure From-17:04 to 17:12 |  | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2017-11-12 | 785 | 967 | 939 | 933 | 35.13 | 3659.13 | 3498.75 | 160.38 | 3710 |  |  | Sunday No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2017-11-13 | 792 | 961 | 933 | 927 | 34.95 | 3647.95 | 3486 | 161.95 | 3700 |  |  | Module cleaning has Been done In Row-E,F,G,H, & Inverter N0-1 & Total module cleaning -777 & Grid Failure From-13:57 to 14:01 |  | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2017-11-14 | 729 | 848 | 825 | 796 | 31.14 | 3229.14 | 3076 | 153.14 | 3260 |  |  | Module cleaning has Been done In Row-A,B,C,D, Inverter N0-1 & Row A,B, Inverter no -4 & Total module cleaning -498 |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2017-11-15 | 831 | 967 | 939 | 948 | 34.49 | 3719.49 | 3546 | 173.49 | 3780 |  |  | Module cleaning has Been done In Row-C,D,E, Inverter N0-4 & Total module cleaning -432 |  | 432 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2017-11-16 | 871 | 1023 | 989 | 1043 | 36.57 | 3962.57 | 3791.25 | 171.32 | 4010 |  |  | Module cleaning has Been done In Row-F,G,H, Inverter N0-4 & Total module cleaning -574 |  | 574 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2017-11-17 | 803 | 933 | 905 | 953 | 34.02 | 3628.02 | 3465 | 163.02 | 3680 |  |  | Module cleaning has Been done In Row-I,J,K, Inverter N0-4 & Total module cleaning -540 |  | 540 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2017-11-18 | 780 | 910 | 882 | 932 | 33.62 | 3537.62 | 3372 | 165.62 | 3580 |  |  | Module cleaning has Been done In Row-L, Inverter N0-4 & Solar Trakers & Row-Q,R,S,T, Inverter no-3 , Total module cleaning -480 & Grid Failur From 8:30 to 8:35 |  | 480 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2017-11-19 | 763 | 888 | 876 | 918 | 33.28 | 3478.28 | 3315 | 163.28 | 3530 |  |  | Sunday No Module Cleaning & Grid failure from 10:20 to 10:38 |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2017-11-20 | 735 | 848 | 853 | 846 | 32.24 | 3314.24 | 3157.5 | 156.74 | 3370 |  |  | Module cleaning has Been done In Row-M,N,O,P, Inverter N0-3 & Total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2017-11-21 | 746 | 887 | 882 | 898 | 32.71 | 3445.71 | 3283.5 | 162.21 | 3500 |  |  | Module cleaning has Been done In Row - J,K,L, Inverter N0-2 & Total module cleaning -819 & Grid Failure from 11:00 to 11:25 |  | 819 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2017-11-22 | 842 | 1024 | 995 | 1003 | 36.98 | 3900.98 | 3726.75 | 174.23 | 3950 |  |  | Module cleaning has Been done In Row - ,G,H,I, Inverter N0-2&1 & Total module cleaning -714 & Grid Failure from 11:10 to 11:14 & 11:54 to 11:58 |  | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2017-11-23 | 899 | 1085 | 1040 | 1068 | 38.59 | 4130.59 | 3945.75 | 184.84 | 4170 |  |  | Module cleaning has Been done In Row - ,A,B,C,D,E,F, Inverter N0-1 & Total module cleaning -672 |  | 672 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2017-11-24 | 922 | 1086 | 1052 | 1059 | 38.94 | 4157.94 | 4032 | 125.94 | 4200 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2017-11-25 | 950 | 1125 | 1085 | 1124 | 39.86 | 4323.86 | 4070.25 | 253.61 | 4370 |  |  | Module cleaning has Been done In Row - ,A,B,C,D,E, Inverter N0-4 & Total module cleaning -592 |  | 592 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2017-11-26 | 910 | 1079 | 1035 | 1108 | 38.57 | 4170.57 | 3988.5 | 182.07 | 4220 |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2017-11-27 | 899 | 1063 | 1023 | 1104 | 38.46 | 4127.46 | 3951 | 176.46 | 4160 |  |  | Module cleaning has Been done In Row - F,G,H, Inverter N0-4 & Total module cleaning -594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2017-11-28 | 887 | 1046 | 1018 | 1081 | 38.53 | 4070.53 | 3879 | 191.53 | 4110 |  |  | Module cleaning has Been done In Row - ,I,J,K,L, & Trackers, Inverter N0-4 & Total module cleaning -726 |  | 726 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2017-11-29 | 848 | 1000 | 1001 | 1026 | 37.26 | 3912.26 | 3738 | 174.26 | 3970 |  |  | Module cleaning has Been done In Row - ,O,P,Q,R,S,T, Inverter N0-3 & Total module cleaning -630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2017-11-30 | 831 | 990 | 983 | 1003 | 36.53 | 3843.53 | 3666.75 | 176.78 | 3890 |  |  | Module cleaning has Been done In Row - J,K,L, Inverter N0-2 & Total module cleaning -819 & Grid Failure From :-8:58 to 9:08 |  | 819 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 2017-12-01 | 860 | 1046 | 1012 | 1038 | 37.9 | 3993.9 | 3816.75 | 177.15 | 4050 |  |  | Module cleaning has Been done In Row - G,H,I, Inverter N0-1 & Inverter-2 & Total module cleaning -714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2017-12-02 | 763 | 904 | 877 | 882 | 32.34 | 3458.34 | 3309 | 149.34 | 3520 |  |  | Module cleaning has Been done In Row - A,B,C,D,E,F, Inverter N0-1 & Total module cleaning -672 |  | 672 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 2017-12-03 | 548 | 622 | 610 | 595 | 23.1 | 2398.1 | 2263.5 | 134.6 | 2450 |  |  | Sunday No Module Cleaning & Day was fully cloudy |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
348 | 2017-12-04 | 340 | 390 | 379 | 373 | 13.35 | 1495.35 | 1380.75 | 114.6 | 1550 |  |  | Module cleaning has Been done In Row - A,B,C,D,E,F, Inverter N0-4 & Total module cleaning -772 & Fully Cloudy Day |  | 772 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
349 | 2017-12-05 | 39 | 46 | 45 | 45 | 1.16 | 176.16 | 86.25 | 89.91 | 239 |  |  | Module clean by Rain & Grid Failure From :-10:25 to 11:46, 13:15 to 13:23, 14:24 to 14:28, 15:25 to 16:49, 17:26 to 17:29 & Rainy & Fully Cloudy Day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
350 | 2017-12-06 | 79 | 84 | 85 | 81 | 2.41 | 331.41 | 174 | 157.41 | 379 |  |  | Module clean by Rain & Grid Failure From :-09:37 to 12:40, & Rainy & Fully Cloudy Day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
351 | 2017-12-07 | 605 | 696 | 695 | 691 | 25.27 | 2712.27 | 2640 | 72.27 | 2761 |  |  | Module clean by Rain & Rainy and cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
352 | 2017-12-08 | 662 | 774 | 764 | 766 | 28.45 | 2994.45 | 2848.5 | 145.95 | 3040 |  |  | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
353 | 2017-12-09 | 684 | 797 | 785 | 786 | 29.81 | 3081.81 | 2934 | 147.81 | 3123 |  |  | Module cleaning has been done in Row-A,B,C,D,E, Inverter no-4 & Total module cleaning-594 & Fully Cloudy Day |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
354 | 2017-12-10 | 695 | 809 | 797 | 801 | 30.78 | 3132.78 | 2994 | 138.78 | 3190 |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2017-12-11 | 526 | 616 | 605 | 625 | 23.11 | 2395.11 | 2262 | 133.11 | 2450 |  |  | Fully cloudy weather & Grid failure from-15:48 to 15:53 & Module cleaning by rain |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
356 | 2017-12-12 | 871 | 1040 | 1012 | 1069 | 38.1 | 4030.1 | 3846.75 | 183.35 | 4063 |  |  | Module cleaning has been done in Row-A,B,C,D,E,F, Inverter no-4 & Total module cleaning-772 & Grid failure from 16:53 to 16:57 |  | 772 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2017-12-13 | 927 | 1108 | 1091 | 1149 | 40.26 | 4315.26 | 4122.75 | 192.51 | 4350 |  |  | Module cleaning has been done in Row-,G,H,I, Inverter no-4 & Total module cleaning-594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2017-12-14 | 814 | 962 | 939 | 978 | 36.15 | 3729.15 | 3559.5 | 169.65 | 3770 |  |  | Module cleaning has been done in Row-,J,K,L, & Trackers Inverter no-4 & Total module cleaning-528 |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2017-12-15 | 673 | 774 | 775 | 771 | 28.78 | 3021.78 | 2868.75 | 153.03 | 3063 |  |  | Module cleaning has been done in Row-P,Q,R,S,T, &Inverter no-3 & Total module cleaning-441 |  | 441 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2017-12-16 | 774 | 922 | 915 | 927 | 34.92 | 3572.92 | 3411 | 161.92 | 3614 |  |  | Module cleaning has been done in Row-M,N,O, &Inverter no-3 & Total module cleaning-651 & Grid failure from-9:31 to 9:48 |  | 651 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2017-12-17 | 741 | 859 | 865 | 852 | 33.07 | 3350.07 | 3189.75 | 160.32 | 3394 |  |  | Sunday no module cleaning & Grid failure from-9:22 to 9:27 |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2017-12-18 | 831 | 1006 | 996 | 1033 | 37.28 | 3903.28 | 3723.75 | 179.53 | 3942 |  |  | Module cleaning has been done in Row-J,K,L, & Inverter no-2 & Total module cleaning-819 |  | 819 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2017-12-19 | 480 | 526 | 508 | 540 | 20.08 | 2074.08 | 1956.75 | 117.33 | 2133 |  |  | Module cleaning has been done in Row-F,G,H,I, & Inverter no-1,2 & Total module cleaning-903 |  | 930 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2017-12-20 | 464 | 531 | 509 | 519 | 18.74 | 2041.74 | 1916.25 | 125.49 | 2091 |  |  | Module cleaning has been done in Row-A,B,C,D,E & A,B & Inverter no-1,4 & Total module cleaning-645 |  | 645 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2017-12-21 | 593 | 684 | 656 | 675 | 24.33 | 2632.33 | 2502 | 130.33 | 2690 |  |  | Today I Replaced The 1 D.C.12 Amp Fuse, Link of The String-09++tive in AJB-113 of The Inverter-3 during The Period of 15:10 to 15:15 & Module cleaning done inverter -4 Row-,C,D,E,F,G, & Total module cleaning -808 |  | 808 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 2017-12-22 | 515 | 583 | 571 | 590 | 21.25 | 2280.25 | 2149.5 | 130.75 | 2331 |  |  | Module cleaning has been done in Row-H,I,J,K,L, & Inverter no-4 & Total module cleaning-864 |  | 864 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 2017-12-23 | 842 | 994 | 967 | 1043 | 37.47 | 3883.47 | 3702.75 | 180.72 | 3930 |  |  | Module cleaning has been done in Row-Q,R,S,T, & Inverter no-3 & Total module cleaning-294 & Grid failure from-14:55 to 15:02 & Color working to AJB structure box-100 to 111 |  | 294 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 2017-12-24 | 894 | 1075 | 1051 | 1079 | 39.46 | 4138.46 | 3952.5 | 185.96 | 4180 |  |  | Sunday no module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 2017-12-25 | 921 | 1096 | 1068 | 1104 | 40.75 | 4229.75 | 4039.5 | 190.25 | 4270 |  |  | Color working to AJB box & structure -112 to 118 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 2017-12-26 | 955 | 1149 | 1125 | 1164 | 42.17 | 4435.17 | 4240.5 | 194.67 | 4471 |  |  | Module cleaning has been done in Row-M,N,O,P &Inverter no-3 & Total module cleaning-798 & Grid failure from-9:03 to 9:10 |  | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 2017-12-27 | 945 | 1135 | 1131 | 1159 | 41.45 | 4411.45 | 4215 | 196.45 | 4450 |  |  | PDPU BOR Failure No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 2017-12-28 | 915 | 1092 | 1092 | 1099 | 39.93 | 4237.93 | 4034.25 | 203.68 | 4265 |  |  | Plant shut down for switchgear testing at 17:29 to 11:00 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 2017-12-29 | 849 | 1023 | 1005 | 993 | 37.61 | 3907.61 | 3773.25 | 134.36 | 3960 |  |  | Module cleaning has been done in Row-K,L, & Inverter no-2 & Total module cleaning-525 |  | 525 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 2017-12-30 | 836 | 1018 | 990 | 968 | 36.88 | 3848.88 | 3677.25 | 171.63 | 3890 |  |  | Today I Replaced The 1 D.C.12 Amp Fuse, Link of The String-08--tive in AJB-101 of The Inverter-4 during The Period of 10:50 to 10:55 & Module cleaning done inverter -1,2 Row-H,I,J, & Total module cleaning -798 & Grid failure from:-9:49 to 9:53 |  | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 2017-12-31 | 786 | 949 | 916 | 892 | 34.68 | 3577.68 | 3414.75 | 162.93 | 3630 |  |  | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2018
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2018-01-01 | 740 | 888 | 859 | 821 | 32.39 | 3340.39 | 3174 | 166.39 | 3424 |  |  | Module cleaning has been done in Row-A,B,C,D,E,F,G, & Inverter no-1 & Total module cleaning-882 & Grid failure from-13:22 to 13:51 |  | 882 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2018-01-02 | 871 | 1023 | 984 | 953 | 37.57 | 3868.57 | 3697.5 | 171.07 | 3900 |  |  | Module cleaning has been done in Row-A,B,C,D,E, & Inverter no-4 & Total module cleaning-594 |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2018-01-03 | 893 | 1063 | 598 | 1033 | 38.39 | 3625.39 | 3467.25 | 158.14 | 3643 |  |  | Inverter-3 cut off at-13:10 due to installing a new inverter & Grid failure from-17:05 to 19:00 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2018-01-04 | 831 | 1023 | 0 | 1008 | 36.96 | 2898.96 | 2772 | 126.96 | 2940 |  |  | Module cleaning has been done in Row-F,G,H,I, & Inverter no-4 & Total module cleaning-772 & Grid Failure from-16:14 to 16:18 |  | 772 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2018-01-05 | 328 | 385 | 0 | 388 | 11.4 | 1112.4 | 1024.5 | 87.9 | 1151 |  |  | Grid Failure From-9:35 to 14:10 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2018-01-06 | 718 | 848 | 1 | 847 | 32.59 | 2446.59 | 2331 | 115.59 | 2500 |  |  | Today inverter no-3 new ABB 250KW inverter commissioning by ABB Mr. Slimbhai Dadu , Inverter started-5:00PM & Grid Failure from-14:05 to 15:35 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2018-01-07 | 843 | 1006 | 849 | 993 | 36.67 | 3727.67 | 3563.25 | 164.42 | 3775 |  |  | Sunday no module cleaning & Grid Failure From-10:8 to 10:23 , 10:32 to 10:38 |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2018-01-08 | 853 | 1006 | 184 | 948 | 36.5 | 3027.5 | 2856.75 | 170.75 | 3062 |  |  | Inverter No-3 Morning time not wakeup due to Error CH2 COM LOSS (7052) Inverter started at 14:40, |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2018-01-09 | 786 | 927 | 907 | 902 | 35.11 | 3557.11 | 3393.75 | 163.36 | 3600 |  |  | Module cleaning has been done in Row-K,L, & Row-Q,R,S,T, & Solar traker Inverter no-4,3 & Total module cleaning-642 |  | 642 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2018-01-10 | 780 | 917 | 916 | 907 | 35.04 | 3555.04 | 3378 | 177.04 | 3590 |  |  | Module cleaning has been done in Row-M,N,O,P, Inverter no-3 & Total module cleaning-798 & Grid Failure From-15:19 to 15:27 |  | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2018-01-11 | 786 | 938 | 943 | 912 | 35.98 | 3614.98 | 3459 | 155.98 | 3670 |  |  | Module cleaning has been done in Row-K,L, Inverter no-2 & Total module cleaning-525 |  | 525 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2018-01-12 | 662 | 802 | 795 | 772 | 29.73 | 3060.73 | 2901 | 159.73 | 3100 |  |  | Module cleaning has been done in Row-H,I,J, Inverter no-2&1 & Total module cleaning-798 & Day was cloudy |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
12 | 2018-01-13 | 633 | 763 | 749 | 720 | 28.22 | 2893.22 | 2723.25 | 169.97 | 2940 |  |  | Day was cloudy |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
13 | 2018-01-14 | 797 | 865 | 939 | 918 | 35.61 | 3554.61 | 3409.5 | 145.11 | 3610 |  |  | Today morning time Inverter -2 not wakeup due to grid failure night time Reset the Err code Than Inverter started 10:05 & Sunday No Module Cleaning |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2018-01-15 | 859 | 1046 | 1024 | 1003 | 37.44 | 3969.44 | 3787.5 | 181.94 |  |  |  | Grid Failure From-16:47 to 16:55 & No Module cleaning |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2018-01-16 | 899 | 1091 | 576 | 978 | 39.04 | 3583.04 | 3412.5 | 170.54 |  |  |  | Today visited Abb Engineer Mr.salimbhai Inverter -3 perameter setting & Grid Failure From-11:30 to 11:35 & Module cleaning has been done in Row-D,E,F,G, Inverter No-1 & Total module cleaning-672 |  | 672 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2018-01-17 | 950 | 1130 | 1099 | 1073 | 39.76 | 4291.76 | 4098.75 | 193.01 |  |  |  | Module cleaning has been done in Row-A,B,C,&A,B,C,D,E, Inverter No-1&4 & Total module cleaning-804 |  | 804 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2018-01-18 | 1001 | 1205 | 1173 | 1240 | 42.17 | 4661.17 | 4470.75 | 190.42 |  |  |  | Module cleaning has been done in Row-,F,G,H,I, Inverter No-4 & Total module cleaning-792 |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2018-01-19 | 951 | 1153 | 1116 | 1149 | 40.76 | 4409.76 | 4218.75 | 191.01 |  |  |  | Module cleaning has been done in Row-,J,K,L,& Trackers Inverter No-4 & Total module cleaning-528 |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2018-01-20 | 915 | 1091 | 1072 | 1104 | 39.88 | 4221.88 | 4038.75 | 183.13 |  |  |  | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2018-01-21 | 877 | 1040 | 1008 | 1043 | 38.23 | 4006.23 | 3861.75 | 144.48 |  |  |  | Sunday No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2018-01-22 | 831 | 989 | 967 | 968 | 36.32 | 3791.32 | 3645.75 | 145.57 |  |  |  | Module cleaning has been done in Row-,L,M,N, & Inverter No-2&3 & Total module cleaning-714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2018-01-23 | 938 | 1148 | 1114 | 1154 | 41.04 | 4395.04 | 4237.5 | 157.54 |  |  |  | Module cleaning has been done in Row-,I,J,K, & Inverter No-2 & Total module cleaning-840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2018-01-24 | 950 | 1171 | 1109 | 1124 | 41.3 | 4395.3 | 4241.25 | 154.05 |  |  |  | Module cleaning has been done in Row-,F,G,H, & Inverter No-1 & Total module cleaning-630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2018-01-25 | 950 | 1154 | 1084 | 1094 | 40.57 | 4322.57 | 4161.75 | 160.82 |  |  |  | Module cleaning has been done in Row-,A,B,C,D,&A,B,C, & Inverter No-1&4 & Total module cleaning-642 & Grid Failure From-16:22 to 16:26 |  | 642 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2018-01-26 | 978 | 1175 | 1104 | 1119 | 41.41 | 4417.41 | 4264.5 | 152.91 |  |  |  | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2018-01-27 | 927 | 1113 | 1053 | 1079 | 39.22 | 4211.22 | 4062.75 | 148.47 |  |  |  | Module cleaning has been done in Row-,H,I,J, & Inverter No-4 & Total module cleaning-576 & Grid Failure From-16:44 to 16:55 |  | 576 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2018-01-28 | 927 | 1114 | 1048 | 1069 | 39.28 | 4197.28 | 4045.5 | 151.78 |  |  |  | Sunday No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2018-01-29 | 933 | 1114 | 1054 | 1104 | 39.27 | 4244.27 | 4092.75 | 151.52 |  |  |  | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2018-01-30 | 938 | 1125 | 1073 | 1129 | 40.15 | 4305.15 | 4154.25 | 150.9 |  |  |  | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2018-01-31 | 882 | 1063 | 1039 | 1068 | 38.92 | 4090.92 | 3947.25 | 143.67 |  |  |  | Module cleaning has been done in Row-,I,J,K, & Inverter No-4 & Total module cleaning-840 & Grid Failure From-14:13 to 14:17 & 14:46 to 14:50 & 15:10 to 15:20 |  | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2018-02-01 | 877 | 1074 | 1028 | 1034 | 37.71 | 4050.71 | 3898.5 | 152.21 |  |  |  | Module cleaning has been done in Row-,E,F,G,H,& Inverter No-1 & Total module cleaning-777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2018-02-02 | 910 | 1097 | 1038 | 1048 | 38.1 | 4131.1 | 3988.5 | 142.6 |  |  |  | Module cleaning has been done in Row-,A,B,C,D,& A,B,C, & Inverter No-1&4 & Total module cleaning-624 |  | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2018-02-03 | 961 | 1153 | 1099 | 1119 | 40.11 | 4372.11 | 4218 | 154.11 |  |  |  | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2018-02-04 | 955 | 1153 | 1089 | 1154 | 40.26 | 4391.26 | 4281.75 | 109.51 |  |  |  | Today I Replaced The D.C.12Amp Fuse Link of The String-08++tive in AJB-105 of The Inverter-4 During The Period of 10:00 To 10:10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
36 | 2018-02-05 | 566 | 645 | 620 | 650 | 23.03 | 2504.03 | 2350.5 | 153.53 |  |  |  | Module cleaning has been done in Row-,H,I,J,K,L,& Trackers & Inverter No-4 & Total module cleaning-924 & cloudy Day |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
37 | 2018-02-06 | 326 | 373 | 352 | 368 | 11.94 | 1430.94 | 1320 | 110.94 |  |  |  | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 & Fully cloudy Day |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
38 | 2018-02-07 | 870 | 1040 | 1003 | 1064 | 37.16 | 4014.16 | 3873.75 | 140.41 |  |  |  | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2018-02-08 | 984 | 1188 | 1160 | 1219 | 42.02 | 4593.02 | 4434 | 159.02 |  |  |  | Module cleaning has been done in Row-,I,J,K, & Inverter No-2&3 & Total module cleaning-840, |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2018-02-09 | 984 | 1192 | 1179 | 1220 | 42.17 | 4617.17 | 4467 | 150.17 |  |  |  | Module cleaning has been done in Row-,E,F,G,H,& Inverter No-1 & Total module cleaning-777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2018-02-10 | 774 | 950 | 922 | 892 | 34.59 | 3572.59 | 3452.25 | 120.34 |  |  |  | Module cleaning has been done in Row-,A,B,C,D,& A,B,C, & Inverter No-1&4 & Total module cleaning-624 & Grid Failure From-14:05 to 14:35 |  | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2018-02-11 | 831 | 1029 | 973 | 1003 | 36.34 | 3872.34 | 3738.75 | 133.59 |  |  |  | Sunday No Module cleaning & Today started SCADA Work. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2018-02-12 | 944 | 1142 | 1094 | 1119 | 38.91 | 4337.91 | 4183.5 | 154.41 |  |  |  | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2018-02-13 | 990 | 1187 | 1129 | 1165 | 40.63 | 4511.63 | 4365.75 | 145.88 |  |  |  | Grid Failure From-9:32 to 09:41 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2018-02-14 | 582 | 679 | 650 | 650 | 24.97 | 2585.97 | 2470.5 | 115.47 |  |  |  | Grid Failure From-8:30 to 09:20 & 13:10 TO 15:15 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2018-02-15 | 1063 | 1288 | 1220 | 1295 | 44 | 4910 | 4745.25 | 164.75 |  |  |  | Module cleaning has been done in Row-,H,I,J, & Inverter No-4 & Total module cleaning-576 |  | 576 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2018-02-16 | 983 | 1187 | 1129 | 1220 | 40.35 | 4559.35 |  | 4559.35 |  |  |  | Grid Failure From-17:20 to 18:20 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2018-02-17 | 978 | 1182 | 1124 | 1230 | 40.39 | 4554.39 | 4385.25 | 169.14 |  |  |  | Module cleaning has been done in Row-,K,L, & Trackers & Inverter No-4 & Total module cleaning-528 |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2018-02-18 | 935 | 1080 | 1056 | 1090 | 37.26 | 4198.26 | 4026 | 172.26 |  |  |  | Grid Failure From-17:10 to 17:25 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2018-02-19 | 945 | 1090 | 1055 | 1100 | 40.88 | 4230.88 | 4068 | 162.88 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2018-02-20 | 933 | 1114 | 1074 | 1164 | 40.24 | 4325.24 | 4173 | 152.24 |  |  |  | Grid Failure From-10:05 to 10:10 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2018-02-21 | 939 | 1125 | 1144 | 1185 | 40.03 | 4433.03 | 4275 | 158.03 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2018-02-22 | 938 | 1136 | 1104 | 1179 | 39.82 | 4396.82 | 4242.75 | 154.07 | 4424 | 4.926 | 0.87533 | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2018-02-23 | 893 | 1120 | 1079 | 1109 | 38.55 | 4239.55 | 4092.75 | 146.8 | 4280 | 4.977 | 0.83816 | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 & Grid Failure From-09:12 to 09:20 |  | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2018-02-24 | 956 | 1215 | 1159 | 1199 | 40.65 | 4569.65 | 4412.25 | 157.4 | 4580 | 5.019 | 0.88941 | Today Inverter no-4 AJB-100, string no-9 Down, Due to cable Falt Replaced 30 meter cable string started 18:00. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2018-02-25 | 989 | 1261 | 1194 | 1291 | 41.9 | 4776.9 | 4611.75 | 165.15 | 4780 | 5.926 | 0.78617 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2018-02-26 | 950 | 1210 | 1149 | 1224 | 40.97 | 4573.97 | 4422 | 151.97 | 4580 | 5.331 | 0.83735 | Module cleaning has been done in Row-,I,J,K, & Inverter No-2&3 & Total module cleaning-840, |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2018-02-27 | 888 | 1113 | 1054 | 1094 | 37.8 | 4186.8 | 4041 | 145.8 | 4190 | 5.08 | 0.8039 | Module cleaning has been done in Row-,E,F,G,H,& Inverter No-1 & Total module cleaning-777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2018-02-28 | 786 | 961 | 912 | 938 | 34.06 | 3631.06 | 3489 | 142.06 | 3640 | 4.679 | 0.75823 | Today I Replaced The D.C.12Amp Fuse Link of The String-08++tive in AJB-101 of The Inverter-1 during The Period of 17:00 To 17:05 & Module cleaning has been done in Row-,A,B,C,D,& A,B,C, Inverter No-1&4 & Total module cleaning-624 |  | 624 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
61 | 2018-03-01 | 859 | 1012 | 958 | 972 | 34.7 | 3835.7 | 3698.25 | 137.45 | 3840 | 4.882 | 0.76663 | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4 & Total module cleaning-702 |  | 702 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2018-03-02 | 972 | 1159 | 1094 | 1140 | 38.87 | 4403.87 | 4254.75 | 149.12 | 4410 | 5.646 | 0.76129 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2018-03-03 | 1006 | 1193 | 1134 | 1189 | 40.05 | 4562.05 | 4395 | 167.05 | 4570 | 5.313 | 0.83836 | Module cleaning has been done in Row-,H,I,J, & Inverter No-4 & Total module cleaning-576 |  | 576 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2018-03-04 | 961 | 1148 | 1088 | 1205 | 38.65 | 4440.65 | 4290.75 | 149.9 | 4450 | 5.551 | 0.78134 | Sunday No Module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2018-03-05 | 1007 | 1210 | 1144 | 1310 | 40.43 | 4711.43 | 4551.75 | 159.68 | 4720 | 5.79 | 0.79454 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2018-03-06 | 1012 | 1136 | 1175 | 1331 | 41.96 | 4695.96 | 4524 | 171.96 | 4705 | 6.232 | 0.73584 | Module cleaning has been done in Row-K,L,& Trackers, & ,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-978 & Grid Failure From-12:00 to 12:05 & 13:00 to 13:08 |  | 978 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2018-03-07 | 921 | 647 | 1083 | 1144 | 39.06 | 3834.06 | 3703.5 | 130.56 | 3840 | 5.357 | 0.69865 | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 &Today Inverter no-2 ABB Auto Trip Due to Err code Auto Reset (056) 13:30 to 18:00 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2018-03-08 | 899 | 1117 | 1074 | 1124 | 38.1 | 4252.1 | 4118.25 | 133.85 | 4250 | 5.301 | 0.78142 | Today I Replaced The D.C.12Amp Fuse Link of The String-03++tive in AJB-103 of The Inverter-4 during The Period of 12:40 To 12:45 & Module cleaning has been done in Row-,H,I,J, & Inverter No-1&2 & Total module cleaning-798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
69 | 2018-03-09 | 933 | 1165 | 1119 | 1184 | 39.38 | 4440.38 | 4286.25 | 154.13 | 4450 | 5.516 | 0.7863 | Module cleaning has been done in Row-,D,E,F,G, & Inverter No-1 & Total module cleaning-672 & Grid Failure From-15:28 to 15:32 |  | 672 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2018-03-10 | 995 | 1226 | 1164 | 1260 | 41.39 | 4686.39 | 4533 | 153.39 | 4695 | 6.127 | 0.74686 | Module cleaning has been done in Row-,A,B,C,& A,B,C, Inverter No-1&4 & Total module cleaning-498 & Grid Failure From-10:18 to 10:32 |  | 498 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2018-03-11 | 1018 | 1267 | 1200 | 1316 | 41.73 | 4842.73 | 4683 | 159.73 | 4850 | 6.018 | 0.78549 | Today I Replaced The D.C.12Amp Fuse Link of The String-03++tive in AJB-103 of The Inverter-4 during The Period of 18:10 To 18:15 & Grid Failure From-08:10 to 08:16 & 08:38 to 08:52 & Sunday No Module Cleaning |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
72 | 2018-03-12 | 514 | 605 | 1245 | 1351 | 43.1 | 3758.1 | 3633 | 125.1 |  |  |  | Today start Tranformer 1&2 overalling work 12:30 & Transformer-3,4& MainTransformer start-18:00 & Total Module Cleaning - 682 |  | 682 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2018-03-13 | 0 | 0 | 0 | 0 | 39 | 39 | 0 | 39 | 0 |  |  | Module Cleaning Done - 198 |  | 198 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2018-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | As per P.O. Of pdpu solar plant All 5 Nos Transformer overalling work done from-12-3-18 12:30 to 14-3-18, 18:00, |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2018-03-15 | 1040 | 1272 | 1209 | 1386 | 41 | 4948 | 4759.5 | 188.5 | 4960 | 6.243 | 0.77436 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2018-03-16 | 1018 | 1221 | 1185 | 1371 | 41.29 | 4836.29 | 4678.5 | 157.79 | 4845 | 6.186 | 0.76337 | Today morning time inverter no - 2 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:15 am & Total Module has been done in Row I,J,K,L, Inverter no-4 & Trackers, Total Module Cleaning-726 |  | 726 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2018-03-17 | 989 | 1198 | 1154 | 1330 | 41.92 | 4712.92 | 4558.5 | 154.42 | 4769 | 6.078 | 0.76475 | Module cleaning has been done in Row-,O,P,Q,R,S,T,& Inverter No-3 & Total module cleaning-630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2018-03-18 | 860 | 1007 | 1013 | 1114 | 37.62 | 4031.62 | 3898.5 | 133.12 | 4089 | 4.775 | 0.83463 | Today morning time inverter no - 2 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:21 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2018-03-19 | 712 | 842 | 862 | 907 | 30.38 | 3353.38 | 3214.5 | 138.88 | 3380 | 3.885 | 0.84797 | Module cleaning has been done in Row-,L,M,N,& Inverter No-3&2 & Total module cleaning-714 & Grid Failure From-09:15 to 09:21 & Day was cloudy |  | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
80 | 2018-03-20 | 1034 | 1283 | 1290 | 1407 | 43.91 | 5057.91 | 4893.75 | 164.16 | 5070 | 6.13 | 0.80612 | Module cleaning has been done in Row-,I,J,K, & Inverter No-2 & Total module cleaning-840, |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2018-03-21 | 1001 | 1300 | 1255 | 1371 | 44.85 | 4971.85 | 4815.75 | 156.1 | 5090 | 5.551 | 0.89372 | Module cleaning has been done in Row-,G,H, & Inverter No-1&2 & Total module cleaning-441 & Replaced New Door Handle of Inverter No - 1 ABB |  | 441 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2018-03-22 | 1046 | 1295 | 1245 | 1350 | 42.71 | 4978.71 | 4803.75 | 174.96 | 5025 | 5.75 | 0.85177 | Module cleaning has been done in Row-A,B,C,D,E,F & Inverter No-1 & Total module cleaning-672 |  | 672 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2018-03-23 | 1057 | 1295 | 1245 | 1341 | 42.58 | 4980.58 | 4825.5 | 155.08 | 5040 | 6.205 | 0.79166 | Today I Replaced The D.C.12Amp Fuse Link of The String-08--tive in AJB-101 of The Inverter-1 during The Period of 18:05 To 18:10 & Module cleaning has been done in Row-A,B,C,D,E,F & Inverter No-4 & Total module cleaning-792 & Today replaced New SPD & Blower Fan & Ac side Auxiliary Fan Inverter No-1 ABB |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
84 | 2018-03-24 | 1018 | 1209 | 1170 | 1346 | 40.83 | 4783.83 | 4629.75 | 154.08 | 4840 | 6.01 | 0.78492 | Grid Failure From-15:22 to 15:38 & Module cleaning has been done in Row-G,H,I,J & Inverter No-4 & Total module cleaning-808 |  | 808 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2018-03-25 | 1040 | 1250 | 1209 | 1396 | 41.51 | 4936.51 | 4783.5 | 153.01 | 4999 | 6.369 | 0.76501 | Today Painting Work of all 5 Nos of Transformers Started & Inverter N0-4 Tripped at 18:00 due to AP Message 1 |  |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2018-03-26 | 1035 | 1238 | 1205 | 1401 | 42.72 | 4921.72 | 4779 | 142.72 | 4967 | 6.103 | 0.79324 | Module cleaning has been done in Row-,K,L, & Inverter No-4 & Trackers, Total module cleaning-314 |  | 314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2018-03-27 | 1034 | 1244 | 1220 | 1406 | 42.9 | 4946.9 | 4797 | 149.9 | 4997 | 5.372 | 0.90662 | Module cleaning has been done in Row-,P,Q,R,S,T, & Inverter No-3, Total module cleaning-465 |  | 465 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2018-03-28 | 1012 | 1210 | 1229 | 1356 | 42.15 | 4849.15 | 4691.25 | 157.9 | 4903 | 5.548 | 0.86135 | Module cleaning has been done in Row-,L,M,N,O, & Inverter No-2&3, Total module cleaning-903 |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2018-03-29 | 1001 | 1237 | 1240 | 1336 | 41.77 | 4855.77 | 4701.75 | 154.02 | 4903 | 6.217 | 0.76866 | Module cleaning has been done in Row-,I,J,K, & Inverter No-1&2, Total module cleaning-840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2018-03-30 | 1012 | 1272 | 1230 | 1325 | 41.74 | 4880.74 | 4728.75 | 151.99 | 4943 | 6.177 | 0.77995 | Inverter No-4 PM & Module cleaning has been done in Row-E,F,G,H, & Inverter No-1, Total module cleaning-777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2018-03-31 | 723 | 1154 | 1084 | 1240 | 38.02 | 4239.02 | 4110 | 129.02 | 4286 | 6.526 | 0.64011 | Grid Failure From-9:37 to 9:42 & 11:37 to 12:08, After Grid Failure at 9:37, inverter no - 1 ABB 250 kw not wake up due to Err Grid MOMFLT (8189) & Reset the Err 6 Times, inverter started at 11:30 & Module cleaning has been done in Row-,A,B,C,D,A,B,C, & Inverter No-1&4, Total module cleaning-624 |  | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2018-04-01 | 1041 | 1249 | 1209 | 1336 | 41.5 | 4876.5 | 4714.5 | 162 | 4922 | 6.644 | 0.72205 | Grid Failure From-10:44 to 10:48 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2018-04-02 | 955 | 1125 | 1099 | 1179 | 38.97 | 4396.97 | 4254 | 142.97 | 4444 | 5.919 | 0.73178 | Today morning time inverter no - 4 ABB 250 kw Tripped at 9:05 due to Err Auto Reset F (8185) & Reset Manually inverter started at 9:25 & Grid Failure From-9:25 to 9:30 & Module cleaning has been done in Row-,D,E,F,G, & Inverter No-4, Total module cleaning-666 |  | 666 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2018-04-03 | 1001 | 1194 | 1159 | 1351 | 39.85 | 4744.85 | 4592 | 152.85 | 4802 | 6.186 | 0.7566 | Module cleaning has been done in Row-H,I,J & Inverter No-4, Total module cleaning-576 & Inverter No-1 PM |  | 576 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2018-04-04 | 899 | 1074 | 1044 | 1255 | 36.67 | 4308.67 | 4157 | 151.67 | 4343 | 6.2 | 0.68273 | Inverter No-1,2,3,4 ABB 250 kw not wake up due to Grid MONFLT (8189) & ISU fault (8185)(Tripping of ACB & VCB),Started by Switching on, LT outgoing ACB & HT Outdoor VCB at 9:23 & Module cleaning has been done in Row-K,L,P,Q,R,S,T & Inverter No-3&4 & Trackers, Total module cleaning-717 |  | 717 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2018-04-05 | 791 | 938 | 942 | 1089 | 34.58 | 3794.58 | 3673.5 | 121.08 | 3836 | 5.472 | 0.68326 | Night time Grid Failure due to high Frequency VCB trip,(Plant Started) Started at 9:33 & Module cleaning has been done in Row-M,N,O & Inverter No-3, Total module cleaning-723 |  | 723 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2018-04-06 | 967 | 1187 | 1185 | 1346 | 39.95 | 4724.95 | 4576 | 148.95 | 4780 | 6.07 | 0.76752 | Module cleaning has been done in Row-J,K,L & Inverter No-2, Total module cleaning-900 & Inverter No-2 PM |  | 900 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2018-04-07 | 1001 | 1227 | 1189 | 1355 | 40.62 | 4812.62 | 4658 | 154.62 | 4869 | 6.261 | 0.75796 | Module cleaning has been done in Row-E,F,G,H,I & Inverter No-1&2, Total module cleaning-900 |  | 900 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2018-04-08 | 949 | 1142 | 1104 | 1235 | 38 | 4468 | 4317 | 151 | 4516 | 5.841 | 0.75356 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2018-04-09 | 990 | 1170 | 1134 | 1165 | 38.96 | 4497.96 | 4349 | 148.96 | 4545 | 5.969 | 0.74214 | Module cleaning has been done in Row-A,B,C,D,A,B,C & Inverter No-1&4, Total module cleaning-700 & Inverter No-4 ABB 250 kw not Wake up Due to Err Auto Reset F (8185),Reset Manually, Inverter Started at 9:19 |  | 700 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2018-04-10 | 966 | 1142 | 1104 | 1240 | 35.15 | 4487.15 | 4352 | 135.15 | 4547 | 5.944 | 0.74559 | Module cleaning has been done in Row-D,E,F & Inverter No-4, Total module cleaning-544 & Grid Failure From-9:39 to 9:44 |  | 544 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2018-04-11 | 905 | 1057 | 1033 | 1224 | 36.5 | 4255.5 | 4109 | 146.5 | 4303 | 5.222 | 0.80313 | Module cleaning has been done in Row-G,H,I,J & Inverter No-4, Total module cleaning-814 & LT Panel Conzerv EM6400 Energy meter of Incomer-3 fail |  | 814 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2018-04-12 | 967 | 1148 | 1119 | 1331 | 38.98 | 4603.98 | 4435 | 168.98 | 4651 | 6.031 | 0.75164 | Grid Failure From 8:23 to 8:36 & From 10:34 to 10:38 & Module cleaning has been done in Row-K,L,Q,R,S,T & Inverter No-3&4 & Total module cleaning-582 |  | 582 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2018-04-13 | 916 | 1080 | 1079 | 1220 | 37.34 | 4332.34 | 4217 | 115.34 | 4379 | 5.643 | 0.75634 | Module cleaning has been done in Row-M,N,O,P & Inverter No-3, Total module cleaning-800 & Today Replaced The D.C.12 Amp Fuse Link of The String-09--tive in AJB-107 of The Inverter-2 during The Period of 18:00 To 18:05 |  | 800 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
106 | 2018-04-14 | 983 | 1181 | 1189 | 1340 | 39.51 | 4732.51 | 4589 | 143.51 | 4780 | 6.322 | 0.73693 | Today morning time inverter no - 2 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:10 & Module cleaning has been done in Row-J,K,L & Inverter No-2, Total module cleaning-819 |  | 819 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2018-04-15 | 922 | 1142 | 1099 | 1250 | 37.74 | 4450.74 | 4304 | 146.74 | 4496 | 5.825 | 0.75229 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2018-04-16 | 995 | 1255 | 1210 | 1391 | 39.93 | 4890.93 | 4729 | 161.93 | 4938 | 6.436 | 0.7478 | Module cleaning has been done in Row-I,A,B,C,D & Inverter No-2&4, Total module cleaning-562 & Grid Failure From-7:54 to 08:00 AM |  | 562 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2018-04-17 | 1029 | 1289 | 1240 | 1417 | 40.95 | 5015.95 | 4855 | 160.95 | 5060 | 6.519 | 0.75652 | Module cleaning has been done in Row-E,F,G,H & Inverter No-4, Total module cleaning-800 |  | 800 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2018-04-18 | 1000 | 1256 | 1199 | 1401 | 40.21 | 4896.21 | 4733 | 163.21 | 4942 | 6.427 | 0.74946 | Module cleaning has been done in Row-I,J,K,L, Inverter No-4 & Trackers, Total module cleaning-726 & Grid Failure From-18:10 to 18:15 |  | 726 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2018-04-19 | 950 | 1187 | 1149 | 1361 | 38.73 | 4685.73 | 4541 | 144.73 | 4730 | 6.362 | 0.72464 | Module cleaning has been done in Row-Q,R,S,T, Inverter No-3, Total module cleaning-294 & Grid Failure From 10:34 to 10:38 & 11:15 to 11:35 & 15:08 to 15:12 & 16:49 to 16:52 |  | 294 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2018-04-20 | 1001 | 1249 | 1230 | 1431 | 40.54 | 4951.54 | 4794 | 157.54 | 4996 | 6.312 | 0.77145 | Module cleaning has been done in Row-M,N,O,P, Inverter No-3, Total module cleaning-800 |  | 800 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2018-04-21 | 1040 | 1323 | 1296 | 1467 | 41.84 | 5167.84 | 5003 | 164.84 | 5214 | 6.565 | 0.77409 | Module cleaning has been done in Row-J,K,L, Inverter No-2, Total module cleaning-819 |  | 819 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2018-04-22 | 984 | 1261 | 1219 | 1366 | 40.04 | 4870.04 | 4724 | 146.04 | 4915 | 6.579 | 0.72814 | Grid Failure From 8:36 to 8:56 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2018-04-23 | 932 | 1175 | 1134 | 1255 | 37.49 | 4533.49 | 4382 | 151.49 | 4580 | 6.682 | 0.66805 | Module cleaning has been done in Row-F,G,H,I, Inverter No-1&2, Total module cleaning-903 & Grid Failure From 10:30 to 10:34 & from 10:50 to 11:33 |  | 903 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2018-04-24 | 1063 | 1295 | 1240 | 1381 | 40.58 | 5019.58 | 4861 | 158.58 | 5065 | 6.794 | 0.72662 | Module cleaning has been done in Row-A,B,C,D,E,A,B,C,D, Inverter No-1&4, Total module cleaning-915 & Grid Failure From 16:20 to 16:24 |  | 915 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2018-04-25 | 1086 | 1312 | 1250 | 1381 | 40.69 | 5069.69 | 4904 | 165.69 | 5115 | 6.829 | 0.73003 | Module cleaning has been done in Row-E,F,G,H,I, Inverter No-4, Total module cleaning-954 |  | 954 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2018-04-26 | 1040 | 1249 | 1200 | 1431 | 39.12 | 4959.12 | 4807 | 152.12 | 5004 | 6.575 | 0.74178 | Module cleaning has been done in Row-J,K,L,& Trackers Inverter No-4, Total module cleaning-528 |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2018-04-27 | 978 | 1182 | 1144 | 1356 | 38 | 4698 | 4544 | 154 | 4744 | 6.28 | 0.73627 | Module cleaning has been done in Row-P,Q,R,S,T, Inverter No-3, Total module cleaning-450 |  | 450 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2018-04-28 | 1006 | 1209 | 1210 | 1391 | 39.02 | 4855.02 | 4700 | 155.02 | 4900 | 6.338 | 0.75352 | Module cleaning has been done in Row-M,N,O, Inverter No-3, Total module cleaning-651 |  | 651 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2018-04-29 | 1006 | 1211 | 1214 | 1371 | 39.51 | 4841.51 | 4691 | 150.51 | 4886 | 6.499 | 0.73276 | Grid Failure From-10:05 to 10:09 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2018-04-30 | 979 | 1130 | 1170 | 1341 | 38.5 | 4658.5 | 4514 | 144.5 | 4703 | 6.116 | 0.74948 | Today morning time inverter no - 2 ABB 250 kw not Wake up due to Err Auto Reset F (8185), Reset Manually, inerter started at 8:10 AM & Module cleaning has been done in Row-L,A,B,C,D, & Inverter No-2&4, Total module cleaning-684 |  | 684 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2018-05-01 | 995 | 1249 | 1199 | 1376 | 38.59 | 4857.59 | 4701 | 156.59 | 4904 | 6.392 | 0.74777 | Module cleaning has been done in Row-I,J,K, Inverter No-2, Total module cleaning-901 |  | 901 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2018-05-02 | 1017 | 1261 | 1195 | 1376 | 38.47 | 4887.47 | 4736 | 151.47 | 4930 | 6.285 | 0.76453 | Module cleaning has been done in Row-C,D,E,F,G,H, Inverter No-1, Total module cleaning-902 |  | 902 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2018-05-03 | 1018 | 1221 | 1159 | 1320 | 37.75 | 4755.75 | 4595 | 160.75 | 4800 | 6.456 | 0.72465 | Module cleaning has been done in Row-A,B,A,B,C,D,E, Inverter No-1&4, Total module cleaning-774 & Grid Failure From 16:53 PM to 17:00 PM |  | 774 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2018-05-04 | 961 | 1154 | 1094 | 1195 | 35.78 | 4439.78 | 4301 | 138.78 | 4459 | 6.055 | 0.71775 | Inverter No - 4 ABB 250 kw not Wake up due to Err DC GND fault (108), Reset Manually, Inverter started at 8:44 AM & The same Inverter tripped due to Err DC GND fault (108) at 16:00, Started Manually at 16:12, Grid Failure from 13:56 to 14:00, Module cleaning has been done in Row-F,G,H, Inverter No-4, Total module cleaning-604 |  | 604 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2018-05-05 | 724 | 876 | 836 | 892 | 23.65 | 3351.65 | 3232 | 119.65 | 3371 | 6.285 | 0.52276 | Inverter No - 4 ABB 250 kw Tripped due to Error DC GND fault (108) at 9:30 AM, Started Manually at 10:10 AM, Grid Failure from 11:30 to 13:30, Module cleaning done in Row-I,J, Inverter No-4, Total module cleaning-368 |  | 368 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2018-05-06 | 989 | 1204 | 1139 | 1366 | 37.25 | 4735.25 | 4585 | 150.25 | 4760 | 6.394 | 0.72558 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2018-05-07 | 984 | 1210 | 1155 | 1396 | 39 | 4784 | 4625 | 159 | 4804 | 6.333 | 0.73934 | Module cleaning has been done in Row-Q,R,S,T,K,L, Inverter No-3&4 & Trackers, Total module cleaning-642 & Grid Failure from 14:45 to 14:49, from 16:59 to 17:05 & from 17:59 to 18:06 |  | 642 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2018-05-08 | 944 | 1159 | 1149 | 1341 | 38.3 | 4631.3 | 4488 | 143.3 | 4655 | 6.149 | 0.73785 | Module cleaning has been done in Row-M,N,O,P, Inverter No-3, Total module cleaning-798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2018-05-09 | 961 | 1210 | 1204 | 1366 | 38.28 | 4779.28 | 4627 | 152.28 | 4800 | 6.262 | 0.7471 | Module cleaning has been done in Row-J,K,L, Inverter No-2, Total module cleaning-819 |  | 819 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2018-05-10 | 955 | 1238 | 1185 | 1335 | 37.89 | 4750.89 | 4596 | 154.89 | 4773 | 6.259 | 0.74326 | Module cleaning has been done in Row-G,H,I, Inverter No-1&2, Total module cleaning-714 |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2018-05-11 | 905 | 1153 | 1104 | 1250 | 35.74 | 4447.74 | 4312 | 135.74 | 4470 | 6.292 | 0.69242 | Grid Failure from 9:40 to 9:44 & from 15:55 to 16:35, No Module Cleaning done due to Absence of Manpower |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2018-05-12 | 1000 | 1250 | 1194 | 1346 | 38.21 | 4828.21 | 4664 | 164.21 | 4850 | 6.492 | 0.72814 | Module cleaning done in Row-A,B,C,D,E,F, Inverter No-1, Total module cleaning-672 & Grid Failure from 14:10 to 14:13 & from 16:16 to 16:18 |  | 672 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2018-05-13 | 995 | 1226 | 1175 | 1296 | 37.64 | 4729.64 | 4581 | 148.64 | 4748 | 6.395 | 0.72364 | Inverter No-4 ABB 250 KW not wake up due to Err Auto Reset F (8185), Reset Manually, Inverter Started at 8:00, Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2018-05-14 | 809 | 978 | 962 | 1083 | 32.41 | 3864.41 | 3740 | 124.41 | 3885 | 5.747 | 0.65887 | Today I Replaced The D.C.12 Amp Fuse Link of The String-03, +ve in AJB-101 of The Inverter-1 during The Period of 18:10 To 18:15 & Module cleaning done in Row-A,B,C, Inverter No-4 & Total module cleaning-288 & Grid Failure from 11:05 to 11:25 & from 14:23 to 14:46 & Inverter No-1&2 ABB 250 KW Not Wake up due to Err Auto Reset F (8185), Reset Manually, Inverters started at 7:40 |  | 288 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
138 | 2018-05-15 | 232 | 272 | 262 | 287 | 7.529 | 1060.529 | 1026 | 34.529 | 1081.35 | 5.645 | 0.1867 | Grid Failure from 6:50 AM to 2:20 PM,Module Cleaning has been done in Row-D,E,Inverter No-4 & Total Module Cleaning-306 |  | 306 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2018-05-16 | 921 | 1091 | 1049 | 1204 | 34.8 | 4299.8 | 4181.25 | 118.55 | 4308.6 | 5.744 | 0.7311 | Grid Failure from 2:19 to 2:24 PM,Module Cleaning has been done in Row-F,G Inverter No-4 & Total Module Cleaning-396 |  | 396 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2018-05-17 | 899 | 1074 | 1033 | 1159 | 34.36 | 4199.36 | 4090.5 | 108.86 | 4213.8 | 5.773 | 0.71142 | Inverter No. 4 has stopped around 30 minutes(9:50 to 10:20) due to ground fault,Grid failure from 1:40 to 1:45, Module Cleaning has been done in Row-H,I,J,K & tracker's 60 PV Modules, Inverter No-4 & total module cleaning-924 |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2018-05-18 | 842 | 984 | 943 | 1150 | 33.73 | 3952.73 | 3879.75 | 72.98 | 3955.65 | 5.364 | 0.71876 | Grid failure from 4:50 to 4:55 PM, Module cleaning has not done because of water tank cleaning. |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2018-05-19 | 922 | 1092 | 1048 | 1280 | 35.74 | 4377.74 | 4251 | 126.74 | 4391.65 | 5.886 | 0.72721 | Grid failure from 5:47 to 5:52, Module cleaning has not done due to absence of manpower |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2018-05-20 | 868 | 1023 | 978 | 1129 | 33.61 | 4031.61 | 3921 | 110.61 | 4044.22 | 5.546 | 0.71073 | Today morning time inverter no - 4 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:12. |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2018-05-21 | 885 | 1057 | 1028 | 1125 | 34.65 | 4129.65 | 4122.75 | 6.9 | 4147.3 | 5.816 | 0.69501 | Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No-3 & total module cleaning-441, No Grid failure,Replace 400 W halogen lamp & fix new LED light(150 W-5 peace). |  | 441 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2018-05-22 | 859 | 1017 | 1068 | 1159 | 34.02 | 4137.02 | 4025.55 | 111.47 | 4152.6 | 5.7 | 0.71006 | Module Cleaning has been done in Row-N,O Inverter No-3 & total module cleaning-399, No Grid failure. |  | 399 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2018-05-23 | 842 | 1046 | 1094 | 1044 | 33.225 | 4059.225 | 3935.25 | 123.975 | 4080 | 5.575 | 0.71329 | Today morning time inverter no - 4 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:55, Module Cleaning has been done in Row-J,K,L,M Inverter No-2,3 & total module cleaning-1071, No Grid failure. |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2018-05-24 | 882 | 1182 | 1134 | 1179 | 34.203 | 4411.203 | 4296.75 | 114.453 | 4429 | 5.495 | 0.78558 | Module Cleaning has been done in Row-J,K,L Inverter No-1,2 & total module cleaning-721,Today morning time inverter no - 4 ABB 250 kw not wake up due to Err Auto Reset F (8185) & Reset Manually inerter started at 8:10 |  | 721 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2018-05-25 | 990 | 1210 | 1149 | 1250 | 33.946 | 4632.946 | 4476 | 156.946 | 4652 | 5.844 | 0.77586 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1,2 & total module cleaning-483,No Grid failure. |  | 483 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2018-05-26 | 1005 | 1188 | 1129 | 1225 | 33.196 | 4580.196 | 4429.5 | 150.696 | 4600 | 5.882 | 0.76223 | Module Cleaning has been done in Row-C,D,E Inverter No-4 & total module cleaning-483,No Grid failure. |  | 483 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2018-05-27 | 950 | 1147 | 1089 | 1184 | 32.21 | 4402.21 | 4266.75 | 135.46 | 4422 | 5.791 | 0.74425 | Sunday No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2018-05-28 | 939 | 1114 | 1058 | 1185 | 31.45 | 4327.45 | 4216.5 | 110.95 | 4347 | 5.529 | 0.76629 | Inverter No. 4 has stopped around 30 minutes(09:42 to 09:53 & 11:06 to 11:17) due to ground fault, Module Cleaning has been done in Row-F,G,H,I Inverter No-4 & total module cleaning-792,No Grid failure. |  | 792 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2018-05-29 | 931 | 1097 | 1049 | 1250 | 30.76 | 4357.76 | 4246.5 | 111.26 | 4370 | 5.46 | 0.78008 | Module Cleaning has been done in Row-J,K,L & tracker's 60 PV Modules, Inverter No-4 & total module cleaning-528,No Grid failure. |  | 528 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2018-05-30 | 866 | 1018 | 1003 | 1189 | 33.048 | 4109.048 | 4001.25 | 107.798 | 4129 | 5.141 | 0.7828 | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3 & total module cleaning-630,No Grid failure. |  | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2018-05-31 | 857 | 1007 | 1043 | 1175 | 32.964 | 4114.964 | 3981 | 133.964 | 4134 | 5.246 | 0.76806 | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2,3 & total module cleaning-987,No Grid failure. |  | 987 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2018-06-01 | 805 | 1012 | 978 | 1083 | 30.894 | 3908.894 | 3792 | 116.894 | 3928 | 4.897 | 0.7818 | Module Cleaning has been done in Row-G,H,I,J, Inverter No-1,2 & total module cleaning-1008,No Grid failure. |  | 1008 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2018-06-02 | 899 | 1091 | 1043 | 1164 | 32.653 | 4229.653 | 4112.25 | 117.403 | 4249 | 5.468 | 0.75737 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & total module cleaning-672,No Grid failure. |  | 672 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2018-06-03 | 924 | 1097 | 1054 | 1169 | 32.185 | 4276.185 | 4156.5 | 119.685 | 4296 | 5.41 | 0.77396 | Sunday No Module Cleaning,No Grid failure. |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2018-06-04 | 478 | 572 | 549 | 610 | 20.54 | 2229.54 | 2148.75 | 80.79 | 2250 | 5.617 | 0.39042 | Inverter has stopped due to Grid failure from 8.30 AM to 12.40 PM & 5.22 to 6.10 PM Module Cleaning has been done in Row-A,B,C Inverter No-1,2 & total module cleaning-288 |  | 288 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2018-06-05 | 945 | 1141 | 1094 | 1230 | 33.329 | 4443.329 | 4301.25 | 142.079 | 4465 | 5.655 | 0.76956 | Module Cleaning has been done in Row-D,E,F,G,H Inverter No-4 & total module cleaning-900 ,No Grid failure. |  | 900 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2018-06-06 | 407 | 464 | 464 | 539 | 13.57 | 1887.57 | 1808.25 | 79.32 | 1207 | 5.389 | 0.2183 | Inverter has stopped due to Grid failure from 8.58 AM to 1.30 PM,Module Cleaning has been done in Row-I,J Inverter No-4 & total module cleaning-378 |  | 378 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2018-06-07 | 927 | 1114 | 1089 | 1306 | 34.412 | 4470.412 | 4336.5 | 133.912 | 4490 | 5.583 | 0.78385 | Module Cleaning has been done in Row-K,L & tracker's Inverter No-4(Thin Film Area) Row-O,P,Q,R,S,T Inverter No. 3 & total module cleaning-978 ,No Grid failure. |  | 978 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2018-06-08 | 865 | 1034 | 1038 | 1204 | 33.065 | 4174.065 | 4055.25 | 118.815 | 4194 | 5.287 | 0.77316 | Module Cleaning has been done in Row-L,M,N Inverter No. 2,3 & total module cleaning-714 ,No Grid failure. |  | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2018-06-09 | 752 | 916 | 912 | 1024 | 30.25 | 3634.25 | 3510.75 | 123.5 | 3655 | 4.7 | 0.75795 | Module Cleaning has been done in Row-J,K Inverter No. ,2 & total module cleaning-820 ,No Grid failure & cloudy day |  | 567 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
165 | 2018-06-10 | 774 | 933 | 933 | 1053 | 30.96 | 3723.96 | 3615 | 108.96 | 3745 | 4.735 | 0.77088 | No module cleaning due to holiday & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
166 | 2018-06-11 | 758 | 933 | 912 | 1033 | 28.56 | 3664.56 | 3540.75 | 123.81 | 3675 | 4.547 | 0.78774 | Module Cleaning has been done in Row-H,I, Inverter No. 1,2 & total module cleaning-399,No Grid failure. & cloudy day |  | 504 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
167 | 2018-06-12 | 825 | 1017 | 993 | 1119 | 31.05 | 3985.05 | 3848.25 | 136.8 | 4000 | 4.993 | 0.78082 | No Module cleaning (No Man power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
168 | 2018-06-13 | 729 | 899 | 882 | 993 | 26.3 | 3529.3 | 3392.25 | 137.05 | 3545 | 5.209 | 0.66331 | Grid Failure From-12:44 to 13:50. No Module Cleaning (No Man Power) & cloudy day |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
169 | 2018-06-14 | 696 | 847 | 837 | 943 | 26.3 | 3349.3 | 3252 | 97.3 | 3365 | 4.994 | 0.65673 | Grid Failure From-15:18 to 17:25. No Module Cleaning (No Man Power) & cloudy day |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
170 | 2018-06-15 | 786 | 950 | 937 | 1063 | 29.12 | 3765.12 | 3626.25 | 138.87 | 3780 | 4.733 | 0.77841 | No Module Cleaning (No Man Power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
171 | 2018-06-16 | 893 | 1096 | 1079 | 1260 | 33.1 | 4361.1 | 4221.75 | 139.35 | 4370 | 5.549 | 0.76757 | No Module Cleaning (No Man Power) & Grid Failure From-18:24 to 18:28 & Today replaced New MFM Meter for LT panel Incomer Feeder No.3 (conzerve 6400NG) & cloudy day |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
172 | 2018-06-17 | 774 | 928 | 917 | 1074 | 29.65 | 3722.65 | 3612 | 110.65 | 3740 | 4.895 | 0.74468 | Grid Failure From-10:50 to 10:56. No Module Cleaning (No Man Power) & cloudy day |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
173 | 2018-06-18 | 826 | 994 | 983 | 1124 | 31.18 | 3958.18 | 3807.75 | 150.43 | 3970 | 5.202 | 0.74383 | No Module Cleaning (No Man Power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
174 | 2018-06-19 | 825 | 1004 | 968 | 1114 | 31.71 | 3942.71 | 3792.75 | 149.96 | 3955 | 5.166 | 0.74618 | No Module Cleaning (No Man Power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
175 | 2018-06-20 | 905 | 1080 | 1053 | 1209 | 33.49 | 4280.49 | 4137.75 | 142.74 | 4290 | 5.826 | 0.71769 | No Module Cleaning (No Man Power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
176 | 2018-06-21 | 899 | 1074 | 1053 | 1210 | 33.1 | 4269.1 | 4129.5 | 139.6 | 4280 | 5.793 | 0.7201 | No Module Cleaning (No Man Power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
177 | 2018-06-22 | 859 | 1001 | 978 | 1144 | 31.75 | 4013.75 | 3901.5 | 112.25 | 4015 | 5.472 | 0.71514 | No Module Cleaning (No Man Power) & cloudy day |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
178 | 2018-06-23 | 701 | 803 | 786 | 887 | 22.71 | 3199.71 | 3111 | 88.71 | 3110 | 4.326 | 0.70069 | Module Cleaning has been done in Row-,A,B,C,D,E,F, Inverter No-4 & total module cleaning-792, & Cloudy Day,No Grid failure. |  | 792 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
179 | 2018-06-24 | 515 | 588 | 580 | 600 | 16.67 | 2299.67 | 2160 | 139.67 | 2310 | 2.894 | 0.77798 | Today Morning Time Inverter No-4 Thinfilm Note wake up, Due to Ground Fault by Modules crack, Reset the Err Then Inverter started- 11:05. Rainy & cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
180 | 2018-06-25 | 616 | 718 | 711 | 816 | 24.02 | 2885.02 | 2794.5 | 90.52 | 2900 | 3.985 | 0.70929 | Module clean By Rain & Grid Failure From-11:07 to 11:17, 14:47 to 14:46, 15:17 to 16:52, 17:24 to 17:31,& Module clean by Rain, Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
181 | 2018-06-26 | 656 | 752 | 746 | 792 | 24.47 | 2970.47 | 2818.5 | 151.97 | 2980 | 3.798 | 0.76474 | Today Morning Time Inverter No-4 Thinfilm Note wake up, Due to Ground Fault by Modules crack, Reset the Err (GND CLOSE ER 8196)Then Inverter started- 09:40. Module clean by Rain & Rainy & cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
182 | 2018-06-27 | 730 | 826 | 821 | 922 | 26.25 | 3325.25 | 3173.25 | 152 | 3336 | 4.184 | 0.77712 | Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
183 | 2018-06-28 | 774 | 894 | 887 | 1023 | 28.48 | 3606.48 | 3497.25 | 109.23 | 3595 | 4.539 | 0.77195 | Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
184 | 2018-06-29 | 588 | 678 | 681 | 766 | 23.01 | 2736.01 | 2625 | 111.01 | 2745 | 3.65 | 0.733 | Grid Failure From-11:55 to 12:07 & Module clean by Rain & Rainy & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
185 | 2018-06-30 | 712 | 820 | 846 | 983 | 28.56 | 3389.56 | 3243 | 146.56 | 3400 | 4.406 | 0.75212 | Today replaced The New MC4 Connector String No-6,AJB-106,Inverter-No-2, During The Period of 17:30 & Module clean by Rain & Rainy & cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
187 | 2018-07-01 | 848 | 989 | 978 | 1154 | 33.55 | 4002.55 | 3843 | 159.55 | 4010 | 5.242 | 0.74559 | Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
188 | 2018-07-02 | 622 | 775 | 776 | 903 | 24.76 | 3100.76 | 3023.25 | 77.51 | 3110 | 4.02 | 0.75403 | Today Morning time inverter No-1 ABB 250KW not wake up Due to Auto reset 'F' Reset The Err Then Inverter started-08:48. & Module clean by Rain & Rainy & cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
189 | 2018-07-03 | 407 | 452 | 454 | 509 | 13.15 | 1835.15 | 1761.75 | 73.4 | 1840 | 2.18 | 0.82265 | Today Monkey Broke a one Module Thin film site AJB-101, Inverter No-4, & Module clean by Rain. Cloudy & Rainy Day |  |  | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
190 | 2018-07-04 | 243 | 271 | 277 | 247 | 7.8 | 1045.8 | 951 | 94.8 | 1050 | 1.465 | 0.69856 | Fully cloudy & Heavy Rainy Day |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
191 | 2018-07-05 | 865 | 996 | 983 | 1139 | 32.92 | 4015.92 | 3810 | 205.92 | 4015 | 5.104 | 0.7667 | Fully cloudy & Rainy Day |  |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
192 | 2018-07-06 | 774 | 892 | 887 | 1018 | 29.71 | 3600.71 | 3521.25 | 79.46 | 3610 | 4.671 | 0.75327 | Grid Failure From-10:20 to 10:28 & Module clean by Rain & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
193 | 2018-07-07 | 860 | 1001 | 998 | 1159 | 32.52 | 4050.52 | 3902.25 | 148.27 | 4060 | 5.267 | 0.7513 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
194 | 2018-07-08 | 689 | 775 | 786 | 897 | 27.82 | 3174.82 | 3080.25 | 94.57 | 3180 | 4.111 | 0.75393 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
195 | 2018-07-09 | 713 | 803 | 817 | 923 | 27.69 | 3283.69 | 3168.75 | 114.94 | 3290 | 4.292 | 0.74712 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 & total module cleaning-792, & Fully cloudy day |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
196 | 2018-07-10 | 571 | 627 | 640 | 705 | 20.69 | 2563.69 | 2460.75 | 102.94 | 2575 | 3.195 | 0.78552 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
197 | 2018-07-11 | 441 | 486 | 494 | 550 | 15.72 | 1986.72 | 1913.25 | 73.47 | 1995 | 2.357 | 0.82497 | Module clean by Rain & Fully Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
198 | 2018-07-12 | 367 | 396 | 408 | 453 | 12.44 | 1636.44 | 1547.25 | 89.19 | 1644 | 1.96 | 0.81752 | Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
199 | 2018-07-13 | 633 | 712 | 721 | 827 | 24.24 | 2917.24 | 2784 | 133.24 | 2925 | 3.779 | 0.7544 | Grid Faiure From-08:50 to 09:27 & Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
200 | 2018-07-14 | 317 | 345 | 363 | 383 | 11.31 | 1419.31 | 1329.75 | 89.56 | 1425 | 2.244 | 0.61893 | Grid Faiure From-11:15 to 13:07 & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for Inport-xport meter, (Replaced total cable 80 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
201 | 2018-07-15 | 328 | 357 | 363 | 358 | 10.72 | 1416.72 | 1314 | 102.72 | 1425 | 1.802 | 0.77075 | Grid Faiure From-14:52 to 15:05 & 15:48 to 15:57, 16:52 to 17:25 & Module clean by Rain & Rainy & Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
202 | 2018-07-16 | 486 | 537 | 554 | 625 | 18.31 | 2220.31 | 2127 | 93.31 | 2230 | 2.554 | 0.85101 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 101 to SMB No-1, (Replaced total cable 70 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
203 | 2018-07-17 | 430 | 475 | 484 | 544 | 15.57 | 1948.57 | 1818.75 | 129.82 | 1960 | 2.406 | 0.79399 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 100 to AJB-101, (Replaced total cable 25 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
204 | 2018-07-18 | 384 | 423 | 433 | 474 | 13.17 | 1727.17 | 1655.25 | 71.92 | 1740 | 2.114 | 0.80223 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 101 to AJB-102, (Replaced total cable 25 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
205 | 2018-07-19 | 294 | 317 | 328 | 358 | 10.21 | 1307.21 | 1247.25 | 59.96 | 1315 | 1.762 | 0.7274 | Grid Failure From-15:43 to 17:17, & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 102 to AJB-103, (Replaced total cable 25 meter) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
206 | 2018-07-20 | 277 | 317 | 323 | 358 | 9.69 | 1284.69 | 1175.25 | 109.44 | 1295 | 1.544 | 0.81748 | Grid Failure From-15:43 to 17:17, & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 103 to AJB-104, (Replaced total cable 25 meter) & Today I Replaced The D.C.12Amp Fuse Link of The String-07++tive in AJB-109 of The Inverter-2 during The Period of 17:30 To 17:40 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
207 | 2018-07-21 | 334 | 373 | 378 | 403 | 11.77 | 1499.77 | 1398 | 101.77 | 1510 | 1.817 | 0.80998 | Grid Failure From-15:43 to 17:17, & Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 104 to AJB-105, (Replaced total cable 25 meter) |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
208 | 2018-07-22 | 520 | 604 | 604 | 675 | 19.52 | 2422.52 | 2302.5 | 120.02 | 2430 | 2.965 | 0.79879 | Module clean by Rain & Rainy & Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
209 | 2018-07-23 | 333 | 384 | 383 | 418 | 11.67 | 1529.67 | 1433.25 | 96.42 | 1540 | 1.837 | 0.81708 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 105 to AJB-106, (Replaced total cable 25 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
210 | 2018-07-24 | 210 | 243 | 247 | 162 | 7.16 | 869.16 | 788.25 | 80.91 | 880 | 1.296 | 0.66181 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 106 to AJB-107, (Replaced total cable 25 meter) & Grid Failure From-09:05 to 09:25, 10:27 to 10:36, 14:47 to 15:02, 15:56 to 16:31 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
211 | 2018-07-25 | 350 | 396 | 404 | 368 | 12.19 | 1530.19 | 1373.25 | 156.94 | 1540 | 1.935 | 0.7757 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 107 to AJB-108, (Replaced total cable 25 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
212 | 2018-07-26 | 469 | 543 | 544 | 584 | 18.12 | 2158.12 | 2117.25 | 40.87 | 2160 | 2.665 | 0.78997 | Module clean by Rain & Rainy & Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
213 | 2018-07-27 | 396 | 452 | 454 | 479 | 14.22 | 1795.22 | 1683.75 | 111.47 | 1800 | 2.239 | 0.78356 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 108 to AJB-109, (Replaced total cable 50 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
214 | 2018-07-28 | 650 | 763 | 761 | 852 | 25.97 | 3051.97 | 2922 | 129.97 | 3060 | 3.976 | 0.75011 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 109 to AJB-110, (Replaced total cable 25 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
215 | 2018-07-29 | 413 | 487 | 484 | 494 | 15.84 | 1893.84 | 1814.25 | 79.59 | 1905 | 2.491 | 0.74537 | Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
216 | 2018-07-30 | 656 | 768 | 725 | 857 | 25.18 | 3031.18 | 2904 | 127.18 | 3040 | 3.948 | 0.7505 | Module clean by Rain & Rainy & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
217 | 2018-07-31 | 695 | 820 | 817 | 922 | 28.52 | 3282.52 | 3161.25 | 121.27 | 3170 | 4.252 | 0.72664 | Grid Failure From-11:41 to 11:48 & Module clean by Rain & cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
219 | 2018-08-01 | 656 | 774 | 766 | 857 | 25.86 | 3078.86 | 2979.75 | 99.11 | 2990 | 4.036 | 0.72206 | Grid Failure From-15:04 to 15:10 & Module clean by Rain & cloudy day & Today Replaced 2 MC4 Connecter for string No-2 positive & Negative line, AJB No-102, Inverter-1 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
220 | 2018-08-02 | 627 | 719 | 721 | 791 | 24.27 | 2882.27 | 2787 | 95.27 | 2890 | 3.677 | 0.76605 | Grid Failure From-15:04 to 15:10 & Module clean by Rain & cloudy day & Grid Failure From-08:30 to 08:43 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
221 | 2018-08-03 | 696 | 813 | 801 | 908 | 28.78 | 3246.78 | 3153.75 | 93.03 | 3250 | 4.232 | 0.7485 | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 110 to AJB-111, (Replaced total cable 40 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
222 | 2018-08-04 | 684 | 787 | 781 | 856 | 26.65 | 3134.65 | 3003.75 | 130.9 | 3140 | 4.107 | 0.74517 | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 111 to AJB-112, (Replaced total cable 40 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
223 | 2018-08-05 | 605 | 695 | 691 | 772 | 23.84 | 2786.84 | 2675.25 | 111.59 | 2790 | 3.612 | 0.75285 | Module clean by Rain & Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
224 | 2018-08-06 | 497 | 577 | 569 | 640 | 19.64 | 2302.64 | 2220 | 82.64 | 2310 | 2.968 | 0.75858 | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 112 to AJB-113, (Replaced total cable 40 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
225 | 2018-08-07 | 537 | 610 | 610 | 675 | 20.08 | 2452.08 | 2339.25 | 112.83 | 2460 | 3.144 | 0.76261 | Module clean by Rain & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 113 to AJB-114, (Replaced total cable 40 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
226 | 2018-08-08 | 300 | 339 | 338 | 272 | 10.06 | 1259.06 | 1187.25 | 71.81 | 1300 | 1.695 | 0.74753 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 114 to AJB-115, (Replaced total cable 40 meter) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
227 | 2018-08-09 | 610 | 702 | 701 | 791 | 23.32 | 2827.32 | 2700 | 127.32 | 2835 | 3.52 | 0.78499 | Module clean by Rain & Rainy & Fully cloudy day & Today Replaced New cat 6 communication cable for AJB 115 to AJB-116, (Replaced total cable 40 meter) & Grid Failure From-11:36 to 11:42, 12:00 to 12:05 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
228 | 2018-08-10 | 933 | 1102 | 1098 | 1266 | 37.24 | 4436.24 | 4258.5 | 177.74 | 4440 | 5.728 | 0.7555 | Module clean by Rain & Rainy & cloudy day & Today Replaced New cat 6 communication cable for AJB 116 to AJB-117, (Replaced total cable 40 meter) & Grid Failure From-14:55 to 15:05, |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
229 | 2018-08-11 | 724 | 848 | 837 | 957 | 27.23 | 3393.23 | 3275.25 | 117.98 | 3400 | 4.168 | 0.79507 | Module clean by Rain & Rainy & cloudy day, |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
230 | 2018-08-12 | 543 | 627 | 630 | 706 | 22.48 | 2528.48 | 2440.5 | 87.98 | 2530 | 3.239 | 0.76131 | Module clean by Rain & Rainy & cloudy day, |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
231 | 2018-08-13 | 576 | 662 | 660 | 721 | 22.27 | 2641.27 | 2517 | 124.27 | 2650 | 3.239 | 0.79742 | Module clean by Rain & Rainy & cloudy day, |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
232 | 2018-08-14 | 532 | 610 | 605 | 650 | 20.79 | 2417.79 | 2304 | 113.79 | 2420 | 3.034 | 0.77741 | Module clean by Rain & Rainy & cloudy day, |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
233 | 2018-08-15 | 554 | 634 | 635 | 680 | 20.72 | 2523.72 | 2418.75 | 104.97 | 2530 | 3.244 | 0.76014 | Module clean by Rain & cloudy day & Grid Failure From-14:02 to 14:10, |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
234 | 2018-08-16 | 706 | 825 | 817 | 928 | 28.75 | 3304.75 | 3180.75 | 124 | 3310 | 4.219 | 0.76466 | Module clean by Rain & Rainy & cloudy day, |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
235 | 2018-08-17 | 68 | 79 | 85 | 80 | 2 | 314 | 241.5 | 72.5 | 320 | 0.451 | 0.69155 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-09:44 to 09:55, |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
236 | 2018-08-18 | 475 | 548 | 545 | 620 | 17.28 | 2205.28 | 2078.25 | 127.03 | 2210 | 2.741 | 0.78584 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-13:51 to 13:56, |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
237 | 2018-08-19 | 300 | 334 | 343 | 363 | 9.74 | 1349.74 | 1231.5 | 118.24 | 1350 | 1.651 | 0.79697 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
238 | 2018-08-20 | 610 | 723 | 715 | 822 | 24.62 | 2894.62 | 2797.5 | 97.12 | 2900 | 3.694 | 0.76516 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
239 | 2018-08-21 | 306 | 345 | 348 | 257 | 10.63 | 1266.63 | 1191.75 | 74.88 | 1270 | 1.621 | 0.76361 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
240 | 2018-08-22 | 378 | 430 | 433 | 474 | 13.65 | 1728.65 | 1599.75 | 128.9 | 1730 | 2.108 | 0.79989 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-09:45 to 09:50 & 14:50 to 14:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
241 | 2018-08-23 | 696 | 814 | 812 | 942 | 28.93 | 3292.93 | 3170.25 | 122.68 | 3300 | 4.234 | 0.75965 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
242 | 2018-08-24 | 593 | 696 | 696 | 791 | 24.72 | 2800.72 | 2676 | 124.72 | 2810 | 3.581 | 0.76481 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
243 | 2018-08-25 | 515 | 599 | 599 | 661 | 20.22 | 2394.22 | 2306.25 | 87.97 | 2400 | 3.042 | 0.76896 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
244 | 2018-08-26 | 616 | 734 | 731 | 816 | 26.13 | 2923.13 | 2781.75 | 141.38 | 2930 | 3.811 | 0.74934 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-12:23 to 12:28 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
245 | 2018-08-27 | 543 | 640 | 635 | 711 | 20.38 | 2549.38 | 2438.25 | 111.13 | 2550 | 3.214 | 0.7733 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
246 | 2018-08-28 | 757 | 899 | 897 | 1028 | 32.57 | 3613.57 | 3501.75 | 111.82 | 3620 | 4.566 | 0.77273 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
247 | 2018-08-29 | 385 | 446 | 444 | 494 | 14.93 | 1783.93 | 1686 | 97.93 | 1790 | 2.141 | 0.81487 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-17:30 to 17:43 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
248 | 2018-08-30 | 379 | 430 | 433 | 479 | 13.69 | 1734.69 | 1627 | 107.69 | 1740 | 2.001 | 0.84753 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
249 | 2018-08-31 | 407 | 469 | 469 | 514 | 16.31 | 1875.31 | 1793.25 | 82.06 | 1880 | 2.852 | 0.64248 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-10:57 to 12:30 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
251 | 2018-09-01 | 576 | 678 | 670 | 771 | 24.58 | 2719.58 | 2597.25 | 122.33 | 2720 | 3.68 | 0.7204 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-08:47 to 09:33 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
252 | 2018-09-02 | 747 | 882 | 872 | 1008 | 28.83 | 3537.83 | 3420 | 117.83 | 3540 | 4.479 | 0.77033 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
253 | 2018-09-03 | 344 | 396 | 404 | 439 | 12.61 | 1595.61 | 1482 | 113.61 | 1600 | 1.952 | 0.7989 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
254 | 2018-09-04 | 735 | 865 | 857 | 952 | 27.51 | 3436.51 | 3303 | 133.51 | 3440 | 4.311 | 0.77774 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
255 | 2018-09-05 | 848 | 1018 | 1003 | 1134 | 35.29 | 4038.29 | 3900 | 138.29 | 4040 | 5.039 | 0.78143 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
256 | 2018-09-06 | 916 | 1102 | 1088 | 1240 | 38.12 | 4384.12 | 4236 | 148.12 | 4390 | 5.721 | 0.7479 | Module clean by Rain |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 2018-09-07 | 735 | 871 | 872 | 973 | 32.1 | 3483.1 | 3354 | 129.1 | 3490 | 4.514 | 0.75356 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
258 | 2018-09-08 | 243 | 282 | 282 | 287 | 8.41 | 1102.41 | 1027.5 | 74.91 | 1110 | 1.395 | 0.77554 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-15:45 to 15:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
259 | 2018-09-09 | 243 | 277 | 278 | 298 | 8.19 | 1104.19 | 1014.75 | 89.44 | 1110 | 1.352 | 0.8002 | Module clean by Rain & Fully Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
260 | 2018-09-10 | 294 | 328 | 337 | 358 | 21.74 | 1338.74 | 1233.75 | 104.99 | 1340 | 1.692 | 0.77189 | Module clean by Rain & Fully Rain & cloudy day & Grid Failure From-14:15 to 15:30 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
261 | 2018-09-11 | 780 | 933 | 928 | 1058 | 32.65 | 3731.65 | 3597 | 134.65 | 3735 | 4.812 | 0.75652 | Module clean by Rain & Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
262 | 2018-09-12 | 679 | 797 | 796 | 882 | 26.6 | 3180.6 | 3048 | 132.6 | 3185 | 4.119 | 0.75365 | Module clean by Rain & Fully cloudy day & Grid Failure From-09:00 to 09:03 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
263 | 2018-09-13 | 803 | 967 | 958 | 1074 | 34.4 | 3836.4 | 3708 | 128.4 | 3840 | 5.366 | 0.69748 | Module clean by Rain & Fully cloudy day & Grid Failure From-12:12 to 12:20 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
264 | 2018-09-14 | 774 | 910 | 897 | 998 | 30.7 | 3609.7 | 3483.75 | 125.95 | 3612 | 4.839 | 0.72752 | Module clean by Rain & Fully cloudy day & Grid Failure From-07:22 to 7:44 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
265 | 2018-09-15 | 797 | 950 | 942 | 1073 | 33 | 3795 | 3675 | 120 | 3800 | 4.96 | 0.74671 | Module clean by Rain & Fully cloudy day & Grid Failure From-15:32 to 15:35 and 17:58 to 18:08 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
266 | 2018-09-16 | 814 | 978 | 963 | 1099 | 34.8 | 3888.8 | 3747.75 | 141.05 | 3895 | 5.321 | 0.71346 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
267 | 2018-09-17 | 826 | 995 | 982 | 1068 | 33.46 | 3904.46 | 3767.25 | 137.21 | 3910 | 5.308 | 0.71796 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
268 | 2018-09-18 | 893 | 1068 | 1053 | 1220 | 38.84 | 4272.84 | 4095.75 | 177.09 | 4280 | 5.9 | 0.70704 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
269 | 2018-09-19 | 944 | 1142 | 1124 | 1301 | 39.95 | 4550.95 | 4430.25 | 120.7 | 4555 | 6.211 | 0.71479 | Module clean by Rain & cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
270 | 2018-09-20 | 967 | 1176 | 1154 | 1370 | 40.3 | 4707.3 | 4560 | 147.3 | 4711 | 6.409 | 0.71643 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 & total module cleaning-792, |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 2018-09-21 | 978 | 1188 | 1180 | 1392 | 41.53 | 4779.53 | 4604.25 | 175.28 | 4783 | 6.457 | 0.72198 | Module Cleaning has been done in Row-,G,H,I,J,, Inverter No-4 & total module cleaning-774, |  | 774 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 2018-09-22 | 447 | 520 | 534 | 604 | 18.03 | 2123.03 | 2037.75 | 85.28 | 2127 | 2.785 | 0.74438 | Module clean by Rainy & Fully cloudy day & Grid Failure From-15:01 to 15:07 and 18:01 to 18:10. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
273 | 2018-09-23 | 367 | 424 | 429 | 469 | 13.35 | 1702.35 | 1613.25 | 89.1 | 1706 | 2.119 | 0.78469 | Module clean by Rain & Fully cloudy day & Grid Failure From-7:44 to 7:50,7:53 to 7:59,8:02 to 8:10,9:16 to 9:24 and 11:56 to 11:59. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
274 | 2018-09-24 | 492 | 570 | 579 | 630 | 18.78 | 2289.78 | 2191.5 | 98.28 | 2293 | 2.968 | 0.753 | Module clean by Rain & Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
275 | 2018-09-25 | 944 | 1143 | 1129 | 1285 | 39.86 | 4540.86 | 4395 | 145.86 | 4545 | 6.264 | 0.70719 | Module clean by Rain & cloudy day & Grid Failure From-09:06 to 09:12, |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
276 | 2018-09-26 | 983 | 1198 | 1180 | 1346 | 41.08 | 4748.08 | 4595.25 | 152.83 | 4752 | 6.545 | 0.70765 | Module clean by Rain |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2018-09-27 | 973 | 1204 | 1194 | 1351 | 41 | 4763 | 4603.5 | 159.5 | 4767 | 6.541 | 0.71032 | Module Cleaning has been done in Row-N,O,P,Q,R,S,T., Inverter No-3 & total module cleaning-840,Grid Failure From-17:32 to 17:37, |  | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 2018-09-28 | 989 | 1210 | 1210 | 1361 | 41.3 | 4811.3 | 4650 | 161.3 | 4815 | 6.621 | 0.7088 | Module Cleaning has been done in Row-M,L,K,J, Inverter No-2 and 3 & total module cleaning-1071. |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2018-09-29 | 967 | 1210 | 1184 | 1320 | 40.64 | 4721.64 | 4576.5 | 145.14 | 4725 | 6.501 | 0.70839 | Module Cleaning has been done in Row-I,H,G,F, Inverter No-1 and 2 & total module cleaning-903. |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 2018-09-30 | 978 | 1210 | 1180 | 1306 | 40.53 | 4714.53 | 4552.5 | 162.03 | 4719 | 6.423 | 0.71609 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 2018-10-01 | 978 | 1193 | 1164 | 1280 | 40.15 | 4655.15 | 4502.25 | 152.9 | 4660 | 6.4 | 0.70967 | Module Cleaning has been done in Row-A,B,C,D,E,& A,B,C,D, Inverter No-1 and 4, total module cleaning-915. |  | 915 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2018-10-02 | 927 | 1119 | 1094 | 1189 | 38.46 | 4367.46 | 4220.25 | 147.21 | 4370 | 6.003 | 0.70952 | Module Cleaning has been done in Row-,E,F,G,H,I, Inverter No-4, total module cleaning-954. |  | 954 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 2018-10-03 | 809 | 967 | 947 | 1054 | 34.32 | 3811.32 | 3687 | 124.32 | 3815 | 5.19 | 0.71644 | Module Cleaning has been done in Row-,J,K,L, & Q,R,S,T and Tracker ,Inverter No-3 and 4, total module cleaning-822. |  | 822 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2018-10-04 | 882 | 1063 | 1054 | 1189 | 37.72 | 4225.72 | 4078.5 | 147.22 | 4229 | 5.788 | 0.71213 | Module Cleaning has been done in Row-,L,M,N,O ,Inverter No-2 and 3, total module cleaning-1050. |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2018-10-05 | 915 | 1125 | 1119 | 1250 | 39.57 | 4448.57 | 4308 | 140.57 | 4452 | 5.197 | 0.83494 | Module Cleaning has been done in Row-I,J,K, Inverter No-2 , total module cleaning-840.Grid Failure From-11:10 to 11:15, |  | 840 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2018-10-06 | 950 | 1176 | 1139 | 1281 | 40.11 | 4586.11 | 4424 | 162.11 | 4590 | 6.169 | 0.72519 | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-1 , total module cleaning-903. |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2018-10-07 | 927 | 1131 | 1099 | 1224 | 39.25 | 4420.25 | 4274.25 | 146 | 4424 | 6.122 | 0.70433 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 2018-10-08 | 843 | 1011 | 987 | 1079 | 34.8 | 3954.8 | 3824 | 130.8 | 3958 | 5.437 | 0.70953 | Module Cleaning has been done in Row-A,B,C, & A,B,C,D,E , Inverter No-1 and 4 , total module cleaning-804. |  | 804 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 2018-10-09 | 871 | 1052 | 1024 | 1124 | 37.73 | 4108.73 | 3956 | 152.73 | 4112 | 5.701 | 0.703 | Module Cleaning has been done in Row-F,G,H, Inverter No-4 , total module cleaning-574. |  | 574 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2018-10-10 | 876 | 1063 | 1033 | 1134 | 37.34 | 4143.34 | 4004.2 | 139.14 | 4147 | 5.747 | 0.70331 | Module Cleaning has been done in Row-I,J,K, Inverter No-4 , total module cleaning-438. |  | 438 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 2018-10-11 | 848 | 1017 | 993 | 1119 | 36.6 | 4013.6 | 3874.5 | 139.1 | 4020 | 5.446 | 0.71945 | Module Cleaning has been done in Row-K,L, & Trackers,& O,P,Q,R,S,T., Inverter No-3&4, & total module cleaning-918,Grid Failure From-17:27 to 17:37, |  | 918 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 2018-10-12 | 825 | 995 | 998 | 1114 | 36.18 | 3968.18 | 3829.5 | 138.68 | 3972 | 5.422 | 0.71401 | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2 &3 , total module cleaning-987. |  | 987 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 2018-10-13 | 842 | 1057 | 1028 | 1149 | 36.67 | 4112.67 | 3967.5 | 145.17 | 4116 | 5.758 | 0.69672 | Module Cleaning has been done in Row-H,I,J, Inverter No-1 &2 , total module cleaning-798,Grid Failure From-16:12 to 16:49. |  | 798 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 2018-10-14 | 832 | 1035 | 998 | 1099 | 36.79 | 4000.79 | 3863.2 | 137.59 | 4004 | 5.417 | 0.72042 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2018-10-15 | 876 | 1103 | 1063 | 1174 | 38.38 | 4254.38 | 4098 | 156.38 | 4258 | 5.778 | 0.71826 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2018-10-16 | 803 | 977 | 953 | 1028 | 35.57 | 3796.57 | 3664.5 | 132.07 | 3800 | 5.209 | 0.71102 | Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 , total module cleaning-882. |  | 882 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2018-10-17 | 882 | 1058 | 1023 | 1114 | 37.68 | 4114.68 | 3974.2 | 140.48 | 4118 | 5.825 | 0.68904 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 , total module cleaning-792,Grid Failure From-15:30 to 15:35. |  | 792 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2018-10-18 | 876 | 1046 | 1008 | 1109 | 37.44 | 4076.44 | 3928.5 | 147.94 | 4080 | 5.627 | 0.7067 | Module Cleaning has been done in Row-G,H,I, Inverter No-4 , total module cleaning-594. |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 2018-10-19 | 825 | 1000 | 963 | 1074 | 36.23 | 3898.23 | 3756 | 142.23 | 3902 | 5.05 | 0.75309 | Module Cleaning has been done in Row-J,K,L & Tracker, Inverter No-4 , total module cleaning-528,Grid Failure From-13:52 to 14:22. |  | 528 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2018-10-20 | 860 | 1024 | 1003 | 1174 | 37.46 | 4098.46 | 3957 | 141.46 | 4102 | 5.739 | 0.69665 | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3 , total module cleaning-630,Grid Failure From-17:24 to 17:30. |  | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2018-10-21 | 944 | 1147 | 1139 | 1305 | 41.25 | 4576.25 | 4424.25 | 152 | 4580 | 6.366 | 0.70122 | No Moule Cleaning |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2018-10-22 | 882 | 1057 | 1069 | 1180 | 39.78 | 4227.78 | 4079.25 | 148.53 | 4230 | 5.941 | 0.69396 | Module Cleaning has been done in Row-,M,N, Inverter No-3 , total module cleaning-462, & Grid Failure From-16:30 to 16:40. |  | 462 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2018-10-23 | 882 | 1092 | 1083 | 892 | 39.22 | 3988.22 | 3839.25 | 148.97 | 3992 | 5.905 | 0.65891 | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 , total module cleaning-1092. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 2018-10-24 | 904 | 1130 | 1084 | 1210 | 39.05 | 4367.05 | 4218.75 | 148.3 | 4371 | 5.993 | 0.71087 | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-1 , total module cleaning-840. |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2018-10-25 | 910 | 1108 | 1058 | 1149 | 38.46 | 4263.46 | 4113.75 | 149.71 | 4268 | 5.991 | 0.69435 | Module Cleaning has been done in Row-A,B,C,D, and A,B,C,D,E Inverter No-1 & 4, total module cleaning-785. |  | 785 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2018-10-26 | 910 | 1103 | 1049 | 1205 | 38.46 | 4305.46 | 4158.75 | 146.71 | 4309 | 5.188 | 0.80952 | Module Cleaning has been done in Row-E,F,G,H,I, Inverter No- 4, total module cleaning-772. |  | 774 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2018-10-27 | 815 | 983 | 942 | 1098 | 35.62 | 3873.62 | 3736.5 | 137.12 | 3877 | 5.792 | 0.65241 | Module Cleaning has been done in Row-I,J,K, Inverter No-4 , total module cleaning-440, & Grid Failure From-10:07 to 10:34. |  | 442 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2018-10-28 | 864 | 1041 | 993 | 1154 | 37.31 | 4089.31 | 3945.75 | 143.56 | 4100 | 5.723 | 0.69825 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2018-10-29 | 888 | 1068 | 1028 | 1200 | 39.41 | 4223.41 | 4074 | 149.41 | 4230 | 5.884 | 0.70068 | Module Cleaning has been done in Row-,L,& Trackers, O,P,Q,R,S,T, Inverter No-4&3 , total module cleaning-814, |  | 814 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2018-10-30 | 888 | 1068 | 1079 | 1185 | 39.63 | 4259.63 | 4107.75 | 151.88 | 4263 | 5.832 | 0.71244 | Module Cleaning has been done in Row-K,L,M,N Inverter No-2 &3, total module cleaning-987. |  | 987 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2018-10-31 | 876 | 1109 | 1074 | 1174 | 39.19 | 4272.19 | 4109.25 | 162.94 | 4280 | 5.598 | 0.74518 | Module Cleaning has been done in Row-,G,H,I,J, Inverter No-1&2, total module cleaning-1008. |  | 1008 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 2018-11-01 | 910 | 1108 | 1063 | 1174 | 39.05 | 4294.05 | 4148.25 | 145.8 | 4298 | 5.932 | 0.70618 | Module Cleaning has been done in Row-A,B,C,D,E,F & A,B,C, Inverter No-1 & 4, total module cleaning-960. |  | 960 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2018-11-02 | 876 | 1062 | 1023 | 1124 | 37.68 | 4122.68 | 3969.75 | 152.93 | 4126 | 5.772 | 0.69672 | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-4 , total module cleaning-900,Grid Failure From-16:20 to 16:23. |  | 900 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2018-11-03 | 820 | 984 | 948 | 802 | 35.79 | 3589.79 | 3454.5 | 135.29 | 3593 | 5.418 | 0.64635 | Module Cleaning has been done in Row-I,J,K,L & Q,R,S,T, and Tracker, Inverter No-4 & 3, total module cleaning-1020. |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2018-11-04 | 814 | 984 | 952 | 1078 | 35.93 | 3863.93 | 3727.5 | 136.43 | 3867 | 5.398 | 0.69822 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2018-11-05 | 837 | 1000 | 988 | 1104 | 37.29 | 3966.29 | 3817 | 149.29 | 3970 | 5.521 | 0.70085 | Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 & 3 , total module cleaning-924,Grid Failure From-10:06 to 10:08 and 15:23 to 15:30. |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 2018-11-06 | 870 | 1064 | 1054 | 1164 | 39.01 | 4191.01 | 4045.5 | 145.51 | 4195 | 5.785 | 0.70678 | Grid Failure From - 08:52 to 08:58. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2018-11-07 | 894 | 1090 | 1073 | 1160 | 40.36 | 4257.36 | 4110.75 | 146.61 | 4261 | 5.9 | 0.7039 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2018-11-08 | 854 | 1024 | 1023 | 1063 | 38.91 | 4002.91 | 3864 | 138.91 | 4006 | 5.599 | 0.69735 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2018-11-09 | 813 | 983 | 973 | 1038 | 37.05 | 3844.05 | 3702.75 | 141.3 | 3848 | 5.415 | 0.69261 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2018-11-10 | 826 | 1001 | 988 | 1039 | 37.49 | 3891.49 | 3761.25 | 130.24 | 3895 | 5.503 | 0.68986 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2018-11-11 | 843 | 1018 | 1008 | 1109 | 38.12 | 4016.12 | 3879.75 | 136.37 | 4020 | 5.674 | 0.69054 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2018-11-12 | 814 | 983 | 973 | 1063 | 36.92 | 3869.92 | 3729 | 140.92 | 3873 | 5.036 | 0.74957 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2018-11-13 | 757 | 899 | 892 | 958 | 34.63 | 3540.63 | 3416.25 | 124.38 | 3540 | 5.031 | 0.68581 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2018-11-14 | 746 | 905 | 892 | 947 | 34.45 | 3524.45 | 3379.5 | 144.95 | 3530 | 5.034 | 0.68346 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2018-11-15 | 792 | 955 | 943 | 1049 | 36.11 | 3775.11 | 3646.5 | 128.61 | 3779 | 5.399 | 0.68221 | Grid Failure From - 10:02 to 10:09. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2018-11-16 | 752 | 893 | 887 | 942 | 35.01 | 3509.01 | 3378.75 | 130.26 | 3513 | 5.043 | 0.67896 | Grid Failure From - 09:55 to 09:58. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2018-11-17 | 45 | 51 | 40 | 45 | 2.32 | 183.32 | 118.5 | 64.82 | 190 | 5.458 | 0.033929 | Grid Failure From - 07:29 to 16:00. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2018-11-18 | 797 | 961 | 953 | 999 | 36.83 | 3746.83 | 3608.25 | 138.58 | 3750 | 5.53 | 0.66094 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2018-11-19 | 797 | 973 | 947 | 1002 | 36.54 | 3755.54 | 3625.5 | 130.04 | 3760 | 5.56 | 0.65912 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2018-11-20 | 792 | 950 | 933 | 1059 | 36.34 | 3770.34 | 3634.5 | 135.84 | 3774 | 5.477 | 0.6716 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2018-11-21 | 740 | 882 | 872 | 978 | 33.87 | 3505.87 | 3379.5 | 126.37 | 3509 | 4.869 | 0.70242 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2018-11-22 | 712 | 859 | 841 | 902 | 32.98 | 3346.98 | 3222.75 | 124.23 | 3350 | 5.005 | 0.65237 | Grid Failure From - 13:04 to 13:07. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2018-11-23 | 752 | 893 | 882 | 998 | 34.57 | 3559.57 | 3435.75 | 123.82 | 3563 | 5.163 | 0.67261 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2018-11-24 | 741 | 887 | 867 | 968 | 23.25 | 3486.25 | 3363.75 | 122.5 | 3367 | 5.105 | 0.64284 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2018-11-25 | 741 | 894 | 877 | 967 | 45.62 | 3524.62 | 3390 | 134.62 | 3530 | 5.153 | 0.66768 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2018-11-26 | 661 | 775 | 761 | 847 | 28.93 | 3072.93 | 2958 | 114.93 | 3076 | 4.428 | 0.67707 | Couldy Day & Grid Failure From - 17:12 to 17:50. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2018-11-27 | 633 | 740 | 731 | 812 | 28.95 | 2944.95 | 2819.25 | 125.7 | 2949 | 4.198 | 0.68468 | Couldy Day & No Module cleaning. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2018-11-28 | 532 | 616 | 605 | 655 | 24.67 | 2432.67 | 2325 | 107.67 | 2440 | 3.559 | 0.66821 | Couldy Day & No Module cleaning. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2018-11-29 | 752 | 893 | 857 | 963 | 34.72 | 3499.72 | 3361.5 | 138.22 | 3503 | 4.833 | 0.70644 | No Module Cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2018-11-30 | 706 | 843 | 806 | 897 | 33.16 | 3285.16 | 3174 | 111.16 | 3289 | 4.548 | 0.70485 | Today Replaced The D.C.12 Amp Fuse Link of The String-03--tive in AJB-114 of The Inverter-3 during The Period of 16:40 To 16:45 and Inverter No -1 ,ABB Primary Maintenance Done & No Module Cleaning. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
345 | 2018-12-01 | 645 | 763 | 736 | 766 | 30.2 | 2940.2 | 2820 | 120.2 | 2944 | 4.465 | 0.64264 | Module Cleaning has been done in Row-A,B,C,D,E,F. Inverter No-4 , total module cleaning-792,Grid Failure From-10:32 to 10:40. |  | 792 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2018-12-02 | 593 | 695 | 676 | 761 | 27.31 | 2752.31 | 2637 | 115.31 | 2756 | 3.923 | 0.68472 | Couldy Day & No Module cleaning. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 2018-12-03 | 667 | 780 | 756 | 872 | 31.03 | 3106.03 | 2975.25 | 130.78 | 3110 | 4.609 | 0.65767 | Module Cleaning has been done in Row-G,H,I,J,K. Inverter No-4 , total module cleaning-936 ,today Inverter No -2 , ABB Primary Maintenance Done. |  | 936 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2018-12-04 | 532 | 617 | 604 | 766 | 27.21 | 2546.21 | 2436 | 110.21 | 2550 | 3.677 | 0.67593 | Module Cleaning has been done in Row-L, & P,Q,R,S,T & Tracker. Inverter No-4 and 3 , total module cleaning-627,Grid Failure From-11:21 to 11:27. |  | 627 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2018-12-05 | 616 | 718 | 777 | 877 | 32.54 | 3020.54 | 2900.25 | 120.29 | 3024 | 4.337 | 0.67959 | Today Replaced The D.C.12 Amp Fuse Link of The String-02 ++tive in AJB-113 of The Inverter-3 during The Period of 16:55 To 17:00 and Module Cleaning has been done in Row-L,M,N,O. Inverter No-2 & 3 , total module cleaning-803, Inverter No -3 ,ABB Primary Maintanance Done. |  | 803 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
350 | 2018-12-06 | 639 | 819 | 882 | 892 | 34.25 | 3266.25 | 3141.75 | 124.5 | 3270 | 4.278 | 0.74501 | Module Cleaning has been done in Row-J,K,L. Inverter No-2 , total module cleaning-667, Inverter No-4 , ABB Primary Maintanance Done. |  | 667 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2018-12-07 | 679 | 950 | 912 | 968 | 35.77 | 3544.77 | 3408 | 136.77 | 3549 | 4.725 | 0.73208 | Module Cleaning has been done in Row-G,H,I. Inverter No-1 and 2 , total module cleaning-714. |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2018-12-08 | 745 | 944 | 902 | 957 | 34.98 | 3582.98 | 3438.75 | 144.23 | 3590 | 4.684 | 0.74702 | Module Cleaning has been done in Row-A,B,C,D,E,F. Inverter No-1 , total module cleaning-672. |  | 672 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2018-12-09 | 809 | 972 | 928 | 993 | 36.42 | 3738.42 | 3605.25 | 133.17 | 3740 | 4.987 | 0.73095 | No module cleaning |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2018-12-10 | 775 | 928 | 887 | 782 | 34.75 | 3406.75 | 3264.75 | 142 | 3410 | 4.828 | 0.6884 | Module Cleaning has been done in Row-A,B,C,D,E,F,G. Inverter No-4 , total module cleaning-990. |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2018-12-11 | 678 | 808 | 776 | 821 | 31.67 | 3114.67 | 2986.5 | 128.17 | 3119 | 4.213 | 0.72157 | Module Cleaning has been done in Row-H,I,J,K,L and Tracker. Inverter No-4 , total module cleaning-924. |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2018-12-12 | 741 | 882 | 857 | 978 | 33.74 | 3491.74 | 3354.75 | 136.99 | 3495 | 4.584 | 0.74311 | Module Cleaning has been done in Row-O,P,Q,R,S,T. Inverter No-3 , total module cleaning-630. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2018-12-13 | 802 | 962 | 962 | 1038 | 38.3 | 3802.3 | 3654 | 148.3 | 3806 | 4.986 | 0.74399 | Module Cleaning has been done in Row-K,L,M,N. Inverter No-2 and 3 , total module cleaning-987. |  | 987 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2018-12-14 | 803 | 994 | 968 | 1028 | 37.79 | 3830.79 | 3682.5 | 148.29 | 3835 | 5.136 | 0.72777 | Grid Failure From-13:04 to 13:16, Module Cleaning has been done in Row-G,H,I,J. Inverter No-1 and 2 , total module cleaning-1008. |  | 1008 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2018-12-15 | 837 | 1012 | 978 | 1039 | 38.01 | 3904.01 | 3758 | 146.01 | 3908 | 4.959 | 0.76809 | Module Cleaning has been done in Row-A,B,C,D,E,F & A,B,C. Inverter No-1 and 4 , total module cleaning-960. |  | 960 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2018-12-16 | 735 | 871 | 842 | 922 | 33.61 | 3403.61 | 3261.75 | 141.86 | 3407 | 4.47 | 0.74288 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2018-12-17 | 797 | 967 | 927 | 968 | 37.56 | 3696.56 | 3550.5 | 146.06 | 3700 | 4.859 | 0.74218 | Module Cleaning has been done in Row-D,E,F,G,H,I. Inverter No-4 , total module cleaning-1098. |  | 1098 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2018-12-18 | 865 | 1057 | 1013 | 1109 | 38.96 | 4082.96 | 3927 | 155.96 | 4090 | 5.444 | 0.73225 | Module Cleaning has been done in Row-,J,K,L,&,P,Q,R,S,T,&Trackers. Inverter No-4 & 3 , total module cleaning-969. |  | 969 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2018-12-19 | 853 | 1034 | 1018 | 1098 | 39.9 | 4042.9 | 3900 | 142.9 | 4046 | 5.458 | 0.72251 | Module Cleaning has been done in Row-L,M,N,O. Inverter No-2 & 3 , total module cleaning-903. |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2018-12-20 | 854 | 1063 | 1033 | 1114 | 39.56 | 4103.56 | 3952.5 | 151.06 | 4107 | 5.511 | 0.72635 | Module Cleaning has been done in Row-H,I,J,K. Inverter No-1 & 2 , total module cleaning-955. & Main Transformer (1250 KVA) primary maintenace Done. |  | 955 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2018-12-21 | 876 | 1086 | 1039 | 1134 | 40.58 | 4175.58 | 4021.5 | 154.08 | 4179 | 5.7 | 0.71458 | Grid Failure From-08:02 to 08:08, Module Cleaning has been done in Row-A,B,C,D,E,F,G,H and A, Inverter No-1 and 4 , total module cleaning-1070, Today Breakedown of VCB on 17:34 to 18:40 due to Spring charged motor remove. |  | 1070 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 2018-12-22 | 826 | 1006 | 968 | 973 | 36.72 | 3809.72 | 3660.75 | 148.97 | 3813 | 5.335 | 0.6966 | Grid Failure From-08:44 to 08:48, Module Cleaning has been done in Row-,B,C,D,E,F, Inverter No-4 , total module cleaning-720 |  | 720 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 2018-12-23 | 842 | 1018 | 977 | 1069 | 36.46 | 3942.46 | 3801 | 141.46 | 3946 | 5.482 | 0.70157 | Grid Failure From-14:01 to 14:06. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 2018-12-24 | 808 | 977 | 256 | 846 | 36.51 | 2923.51 | 2799 | 124.51 | 2930 | 5.171 | 0.55226 | Today morning time Inverter No :-3 ,ABB 250KW not wake up due to error " CH2 COM LOSS (7520)" ,Reset manually Inverter started 14:00.& Grid Failure From-17:47 to 18:07, Module Cleaning has been done in Row-,H,I,J,K,L, & Trackers, Inverter No-4 , total module cleaning-1122. |  | 1122 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 2018-12-25 | 837 | 1018 | 988 | 1089 | 38.89 | 3970.89 | 3831.75 | 139.14 | 3974 | 5.276 | 0.73413 | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3 , total module cleaning-630. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 2018-12-26 | 849 | 1030 | 1013 | 1084 | 36.14 | 4012.14 | 3859.5 | 152.64 | 4016 | 5.219 | 0.75 | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2 & 3 , total module cleaning-814. |  | 814 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 2018-12-27 | 853 | 1073 | 1039 | 1124 | 40.29 | 4129.29 | 3979.5 | 149.79 | 4133 | 5.747 | 0.70093 | Grid Failure From-12:17 to 12:22 and 15:17 to 15:24 , Module Cleaning has been done in Row-H,I,J,K, Inverter No-1 & 2 , total module cleaning-971. |  | 971 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 2018-12-28 | 904 | 1114 | 1063 | 1144 | 41.5 | 4266.5 | 4108.5 | 158 | 4270 | 5.689 | 0.73155 | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A. Inverter No-1 and 4 , total module cleaning-954. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 2018-12-29 | 809 | 978 | 938 | 973 | 34.03 | 3732.03 | 3582 | 150.03 | 3736 | 5.834 | 0.62416 | Grid Failure From-11:21 to 12:17 , Module Cleaning has been done in Row-B,C,D,E,F, Inverter No-4 , total module cleaning-720. |  | 720 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 2018-12-30 | 814 | 1074 | 1018 | 1119 | 38.88 | 4063.88 | 3914.25 | 149.63 | 4067 | 5.584 | 0.70987 | Today morning time Inverter No-1, ABB 250KW not wake up Due to error of " EXT DI1 ALM (1089)",Reset manually Inverter started-09:27. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 2018-12-31 | 876 | 1063 | 1018 | 1098 | 38.9 | 4093.9 | 3936.75 | 157.15 | 4100 | 5.635 | 0.70916 | Grid Failure From-12:00 to 12:05, Module Cleaning has been done in Row-,G,H,I,J,K,L, & Trackers, Inverter No-4 , total module cleaning-1122. |  | 1122 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2019
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2019-01-01 | 814 | 990 | 947 | 1024 | 37.94 | 3812.94 | 3658.5 | 154.44 | 3816 | 5.357 | 0.69429 | Grid Failure From-15:49 to 15:56, Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-4 , total module cleaning-524. |  | 524 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2019-01-02 | 809 | 1023 | 988 | 1063 | 37.74 | 3920.74 | 3779.25 | 141.49 | 3924 | 5.38 | 0.71089 | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " GND CLOSER ER (8196)" ,Reset manually Inverter started 9:05.& Grid Failure From-16:03 to 16:07, Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No-3 , total module cleaning-441. |  | 441 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2019-01-03 | 859 | 1046 | 1049 | 1119 | 40.45 | 4113.45 | 3995.25 | 118.2 | 4117 | 5.598 | 0.7168 | Grid Failure From-17:19 to 17:20, Module Cleaning has been done in Row-L,M,N,O, Inverter No-2 & 3 , total module cleaning-903. |  | 903 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2019-01-04 | 803 | 1006 | 978 | 1048 | 38.59 | 3873.59 | 3717.75 | 155.84 | 3877 | 5.136 | 0.73574 | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-1 & 2 , total module cleaning-1281. |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2019-01-05 | 775 | 944 | 907 | 943 | 34.61 | 3603.61 | 3465 | 138.61 | 3607 | 4.808 | 0.7312 | Module Cleaning has been done in Row-A,B,C,D,E,F & A,B, Inverter No-1 & 4 , total module cleaning-792. |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2019-01-06 | 944 | 1153 | 1109 | 1154 | 41.37 | 4401.37 | 4240.5 | 160.87 | 4405 | 5.946 | 0.72206 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2019-01-07 | 842 | 1007 | 972 | 993 | 38.56 | 3852.56 | 3697.5 | 155.06 | 3860 | 5.184 | 0.72573 | Module Cleaning has been done in Row-C,D,E,F Inverter No- 4 , total module cleaning-630. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2019-01-08 | 842 | 1017 | 978 | 1038 | 38.55 | 3913.55 | 3768 | 145.55 | 3920 | 5.26 | 0.72636 | Module Cleaning has been done in Row-,G,H,I,J,K, Inverter No- 4 , total module cleaning-936. |  | 936 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2019-01-09 | 798 | 955 | 928 | 1013 | 37.08 | 3731.08 | 3588.75 | 142.33 | 3735 | 5.008 | 0.72691 | Grid Failure From-12:28 to 12:35, Module Cleaning has been done in Row-L, &O,P,Q,R,S,T, and Trackers, Inverter No-4 & 3 , total module cleaning-816. |  | 816 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2019-01-10 | 847 | 1035 | 1033 | 1104 | 39.75 | 4058.75 | 3912 | 146.75 | 4062 | 5.336 | 0.74195 | Module Cleaning has been done in Row-K,L,M,N, Inverter No- 2 & 3 , total module cleaning-987. |  | 987 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2019-01-11 | 843 | 1063 | 1028 | 1104 | 39.43 | 4077.43 | 3929.25 | 148.18 | 4081 | 5.35 | 0.74347 | Today Inverter No:1(17:13 to 17:55) Breakdown due to Primary Maintenance by AMC (ABB). Module Cleaning has been done in Row G,H,I,J , Inverter No-1 & 2, total module cleaning-1008 |  | 1008 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2019-01-12 | 842 | 1023 | 988 | 1033 | 37.99 | 3923.99 | 3786.75 | 137.24 | 3927 | 5.08 | 0.75344 | Grid Failure From-11:11 to 11:14, Module Cleaning has been done in Row-A,B,C,D,E,F, &A,B,C,D, Inverter No-1 & 4 , total module cleaning-1104. |  | 1104 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2019-01-13 | 763 | 922 | 892 | 933 | 34.94 | 3544.94 | 3403.5 | 141.44 | 3549 | 5.241 | 0.66 | Grid Failure From-14:24 to 14:35 and 14:36 to 15:04. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2019-01-14 | 741 | 899 | 862 | 650 | 32.01 | 3184.01 | 3063 | 121.01 | 3188 | 5.096 | 0.60974 | Grid Failure From-11:16 to 11:23,12:47 to 12:58,13:48 to 13:58,14:28 to 14:33 and 16:30 to 17:18.Today Inverter No:4 are wake up after grid failure from 13:58, Due to Error ">RUN DISABLE (8194)" Reset manually inverter started 16:05. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2019-01-15 | 814 | 978 | 942 | 968 | 36.13 | 3738.13 | 3584.25 | 153.88 | 3740 | 5.259 | 0.69314 | Grid Failure From-12:48 to 12:58. & Module cleaning has been done in row- E,F,G,H, Inveter No-4, Total module cleaning-756. |  | 756 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2019-01-16 | 871 | 1063 | 1024 | 1124 | 39.14 | 4121.14 | 3966 | 155.14 | 4125 | 5.594 | 0.71871 | ꟷ |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2019-01-17 | 859 | 1045 | 1008 | 1063 | 38.75 | 4013.75 | 3878.25 | 135.5 | 4017 | 5.315 | 0.73663 | Module Cleaning has been done in Row-I,J,K,L, &,Q,R,S,T, and Trackers, Inverter No-4 & 3 , total module cleaning-1020. |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2019-01-18 | 876 | 1069 | 1063 | 1159 | 40.29 | 4207.29 | 4037.25 | 170.04 | 4211 | 5.435 | 0.75516 | Today Installed new energy meter by UGVCL.it connect to series connection of old meter and only purpose of measuring of HVAR and LVAR parameter.Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 & 3 , total module cleaning-1050. |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2019-01-19 | 899 | 1136 | 1109 | 1190 | 41.61 | 4375.61 | 4209.75 | 165.86 | 4379 | 5.506 | 0.77516 | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-1&2 , total module cleaning-1281. |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2019-01-20 | 809 | 1012 | 973 | 1003 | 37.01 | 3834.01 | 3682.5 | 151.51 | 3838 | 5.087 | 0.73535 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2019-01-21 | 780 | 939 | 907 | 897 | 34.79 | 3557.79 | 3428.25 | 129.54 | 3561 | 4.963 | 0.69933 | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " GND CLOSER ER (8196)" ,Reset manually Inverter started 9:05.& Grid Failure From-16:40 to 17:50, Module Cleaning has been done in Row-A,B,C,D,E,F & A,B. Inverter No-1 & 4 , total module cleaning-834. |  | 834 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2019-01-22 | 820 | 984 | 948 | 912 | 37.02 | 3701.02 | 3546.75 | 154.27 | 3710 | 4.942 | 0.73168 | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " GND CLOSER ER (8196)" ,Reset manually Inverter started 9:04.& Module Cleaning has been done in Row-C,D,E,F,G. Inverter No-4 , total module cleaning-828. |  | 828 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2019-01-23 | 819 | 989 | 952 | 1029 | 34.9 | 3823.9 | 3682.5 | 141.4 | 3827 | 5.214 | 0.71539 | Module Cleaning has been done in Row-H,I,J,K,L, &,T, and Trackers, Inverter No-4 & 3 , total module cleaning-945.Grid Failure From-12:50 to 13:02 |  | 945 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2019-01-24 | 910 | 1108 | 1094 | 1189 | 41.6 | 4342.6 | 4194.75 | 147.85 | 4346 | 5.726 | 0.73976 | Module Cleaning has been done in Row-M,N,O,P,Q,R,S, Inverter No- 3 , total module cleaning-1071. |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2019-01-25 | 910 | 1131 | 1109 | 1179 | 41.45 | 4370.45 | 4208.25 | 162.2 | 4375 | 5.856 | 0.72816 | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 , total module cleaning -1092.Grid Failure From-11:35 to 11:40 and 12:24 to 12:33 & 14:46 to 14:52 & 17:31 to 17:35. |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2019-01-26 | 956 | 1187 | 1144 | 1210 | 43.54 | 4540.54 | 4366.5 | 174.04 | 4544 | 5.775 | 0.7669 | Grid Failure From-16:09 to 16:14, Module Cleaning has been done in Row-F,G,H, Inverter No-1 , total module cleaning-630. |  | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2019-01-27 | 978 | 1204 | 1164 | 1240 | 43.45 | 4629.45 | 4464 | 165.45 | 4633 | 5.712 | 0.79055 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 2019-01-28 | 939 | 1153 | 1109 | 1169 | 42.47 | 4412.47 | 4251.75 | 160.72 | 4416 | 6.152 | 0.69963 | Grid Failure From-9:49 to 10:18, Module Cleaning has been done in Row-A,B,C,D,E & A,B,C,D, Inverter No-1 & 4 , total module cleaning-915. |  | 915 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2019-01-29 | 1000 | 1221 | 1179 | 1245 | 43.67 | 4688.67 | 4517.25 | 171.42 | 4690 | 6.029 | 0.75819 | Module Cleaning has been done in Row-,E,F,G,H,I,J, Inverter No- 4 , total module cleaning-1134. |  | 1134 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2019-01-30 | 972 | 1193 | 1155 | 1275 | 43.88 | 4638.88 | 4485 | 153.88 | 4642 | 6.157 | 0.73483 | Module Cleaning has been done in Row-K,L, &,Q,R,S,T, and Trackers, Inverter No-4 & 3 , total module cleaning-642. |  | 642 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2019-01-31 | 736 | 871 | 872 | 903 | 33.14 | 3415.14 | 3274.5 | 140.64 | 3419 | 4.369 | 0.76273 | Today atmosphere was cloudy ,Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 & 3, Total module cleaning-1050. |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
31 | 2019-02-01 | 898 | 1125 | 1098 | 1174 | 40.42 | 4335.42 | 4188 | 147.42 | 4340 | 5.721 | 0.73938 | Grid Failure From-13:00 to 13:05,Module Cleaning has been done in Row-,H,I,J,K, Inverter No-1 & 2, Total module cleaning-1071. |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2019-02-02 | 984 | 1216 | 1175 | 1255 | 43.29 | 4673.29 | 4500 | 173.29 | 4680 | 6.012 | 0.75872 | Module Cleaning has been done in Row-,A,B,C,D,E,F,G, Inverter No-1, Total module cleaning-882. |  | 882 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2019-02-03 | 837 | 1006 | 973 | 993 | 36.94 | 3845.94 | 3702.75 | 143.19 | 3850 | 5.126 | 0.73204 | Grid Failure From-15:13 to 15:24. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2019-02-04 | 650 | 763 | 746 | 706 | 27.78 | 2892.78 | 2770.5 | 122.28 | 2896 | 3.963 | 0.71224 | Grid Failure From-12:07 to 12:13.Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-4, Total module cleaning-990 and cloudy Day. |  | 990 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
35 | 2019-02-05 | 633 | 746 | 725 | 685 | 28.14 | 2817.14 | 2699.25 | 117.89 | 2821 | 3.87 | 0.71047 | Module Cleaning has been done in Row-H,I,J,K, Inverter No-4, Total module cleaning-738 and cloudy Day. |  | 738 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
36 | 2019-02-06 | 803 | 972 | 938 | 1033 | 34.47 | 3780.47 | 3637.5 | 142.97 | 3784 | 5.41 | 0.68172 | Grid Failure From- 13:10 to 13:42.Today we are using new 220 Nos cable tie, change and replace old Crack Cable tie .No Module Cleaning due to water are not available in tank.( Water Bor are under maintenance At. PDPU). |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2019-02-07 | 938 | 1143 | 1114 | 1235 | 42.88 | 4472.88 | 4308 | 164.88 | 4476 | 5.879 | 0.74206 | Module Cleaning has been done in Row-N,O,P,Q,R,S,T, and L ,Trackers. Inverter No-3 & 4 , total module cleaning-1026.Grid Failure From-12:50 to 12:57 |  | 1026 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2019-02-08 | 934 | 1136 | 1139 | 1200 | 42.68 | 4451.68 | 4290 | 161.68 | 4370 | 5.842 | 0.72908 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2019-02-09 | 989 | 1233 | 1214 | 1285 | 45.13 | 4766.13 | 4595.25 | 170.88 | 4770 | 6.299 | 0.73807 | Module Cleaning has been done in Row-J,K,L,M. Inverter No-2 & 3 , total module cleaning-1071. |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2019-02-10 | 927 | 1192 | 1155 | 1220 | 43.42 | 4537.42 | 4375.5 | 161.92 | 4541 | 6.291 | 0.70353 | Grid Failure From- 15:43 to 15:46 and 15:51 to 16:40. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2019-02-11 | 978 | 1238 | 1179 | 1250 | 44.11 | 4689.11 | 4513.5 | 175.61 | 4695 | 6.065 | 0.7545 | Module Cleaning has been done in Row-D,E,F,G,H,I. Inverter No-1 & 2 , total module cleaning-1176. |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2019-02-12 | 944 | 1159 | 1104 | 1104 | 40.4 | 4351.4 | 4194.75 | 156.65 | 4355 | 5.936 | 0.71507 | Module Cleaning has been done in Row-A,B,C & A,B,C,D,E. Inverter No-1 & 4 , total module cleaning-804. |  | 804 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2019-02-13 | 752 | 887 | 857 | 907 | 32.45 | 3435.45 | 3304.5 | 130.95 | 3440 | 4.83 | 0.69417 | Grid Failure From- 11:20 to 11:28 and 12:03 to 16:10. Module Cleaning has been done in Row-F,G,H,I,J,K. Inverter No-4 , total module cleaning-1134. |  | 1134 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2019-02-14 | 848 | 1030 | 1003 | 1078 | 34.83 | 3993.83 | 3847.5 | 146.33 | 3997 | 5.327 | 0.73131 | Grid Failure From- 16:55 to 17:42.Module Cleaning has been done in Row-O,P,Q,R,S,T & L,Tracker. Inverter No-3 & 4 , total module cleaning-727. |  | 727 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2019-02-15 | 876 | 1057 | 1058 | 1099 | 38.73 | 4128.73 | 3985.5 | 143.23 | 4132 | 5.458 | 0.73787 | Grid Failure From- 11:05 to 11:12.Module Cleaning has been done in Row-K,L,M,N,O. Inverter No-2 & 3 , total module cleaning-1076. |  | 1076 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2019-02-16 | 1012 | 1278 | 1245 | 1321 | 43.6 | 4899.6 | 4722 | 177.6 | 4903 | 6.262 | 0.76314 | Module Cleaning has been done in Row-F,G,H,I,J. Inverter No-1 & 2 , total module cleaning-1197. |  | 1197 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2019-02-17 | 995 | 1238 | 1200 | 1275 | 43.07 | 4751.07 | 4590 | 161.07 | 4755 | 6.176 | 0.75041 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2019-02-18 | 894 | 1079 | 1048 | 1084 | 39.32 | 4144.32 | 3998.25 | 146.07 | 4149 | 5.618 | 0.7198 | Grid Failure From- 11:53 to 13:59.Module Cleaning has been done in Row-A,B,C,D,E & A,B,C,D,E. Inverter No-1 & 4 , total module cleaning-1077. |  | 1077 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2019-02-19 | 949 | 1165 | 1134 | 1179 | 40.69 | 4467.69 | 4299.75 | 167.94 | 4471 | 5.917 | 0.73647 | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " DC GND FLT (108)" ,Reset manually Inverter started 8:45..Module Cleaning has been done in Row-F,G,H,I,J Inverter No-4 , total module cleaning-972. |  | 972 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2019-02-20 | 961 | 1164 | 1134 | 1260 | 42.31 | 4561.31 | 4372.5 | 188.81 | 4565 | 6.196 | 0.7181 | Grid Failure From- 09:42 to 09:56.Module Cleaning has been done in Row-K,L, & O,P,Q,R,S,T, & Trackers. Inverter No-3 & 4, total module cleaning-978. |  | 978 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2019-02-21 | 984 | 1199 | 1210 | 1331 | 42.43 | 4766.43 | 4631.25 | 135.18 | 4770 | 6.166 | 0.75399 | Module Cleaning has been done in Row-L,M,N. Inverter No- 2 & 3 ,total module cleaning-714. |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2019-02-22 | 927 | 1159 | 1134 | 1219 | 41.46 | 4480.46 | 4320.75 | 159.71 | 4484 | 5.832 | 0.74938 | Today morning time Inverter No :-4 ,ABB 250KW not wake up due to error " DC GND FLT (108)" ,Reset manually Inverter started 8:40.Module Cleaning has been done in Row-H,I,J,K .Inverter No-1 & 2 , total module cleaning-1071. |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2019-02-23 | 707 | 825 | 806 | 842 | 29.9 | 3209.9 | 3086.25 | 123.65 | 3213 | 3.92 | 0.79887 | Grid Failure From- 11:53 to 13:59.Module Cleaning has been done in Row-A,B,C,D,E & A. Inverter No-1 & 4 , total module cleaning-954.Today Cloudy day. |  | 954 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
54 | 2019-02-24 | 955 | 1171 | 1129 | 1225 | 40.49 | 4520.49 | 4364.25 | 156.24 | 4524 | 5.97 | 0.73859 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2019-02-25 | 1012 | 1238 | 1205 | 1245 | 43.13 | 4743.13 | 4575.75 | 167.38 | 4747 | 6.37 | 0.72633 | Module Cleaning has been done in Row-B,C,D,E,F,G,H. Inverter No-4 , total module cleaning-1116. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2019-02-26 | 752 | 904 | 882 | 983 | 34.79 | 3555.79 | 3424.5 | 131.29 | 3560 | 5.289 | 0.65604 | Grid Failure From- 10:40 to 11:28 & 16:55 to 17:45. Module Cleaning has been done in Row-I,J,K,L and Tracker. Inverter No- 4 , total module cleaning-726.Today Cloudy day, & Today has been replaced sillicagel in main transformer (1250kva) |  | 726 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
57 | 2019-02-27 | 887 | 1069 | 1053 | 1139 | 37.23 | 4185.23 | 4021.5 | 163.73 | 4189 | 5.486 | 0.74423 | Grid Failure From- 12:45 to 12:50 & 15:34 to 15:39. .Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3, total module cleaning-630. |  | 630 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2019-02-28 | 1064 | 1306 | 1321 | 1431 | 46.59 | 5168.59 | 4997.25 | 171.34 | 5175 | 6.588 | 0.76561 | Module Cleaning has been done in Row-K,L,M,N, Inverter No-2 & 3, total module cleaning-987.Today Transformer-2 (300 KVA) Primary Maintenance Done. |  | 977 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2019-03-01 | 1005 | 1278 | 1240 | 1351 | 43.74 | 4917.74 | 4748.25 | 169.49 | 4921 | 5.999 | 0.79952 | Module Cleaning has been done in Row-G,H,I,J, Inverter No-1 and 2, total module cleaning-1008.Today evening time (13:18 to 13:32)short circuit in H pole (11KV side)by monkey fall in line .so VCB are trip, measuring P.T Fuses are blown off in R,Y,B. |  | 1008 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2019-03-02 | 854 | 1040 | 1013 | 1084 | 33.72 | 4024.72 | 3883.5 | 141.22 | 4028 | 5.276 | 0.74411 | Module Cleaning has been done in Row-A,B,C,D,E,F& A,B,C .Inverter No-1 & 4 , total module cleaning-960.Today Cloudy day. |  | 960 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
61 | 2019-03-03 | 702 | 819 | 801 | 872 | 29.14 | 3223.14 | 3094.5 | 128.64 | 3227 | 4.152 | 0.75752 | Today Cloudy day.Grid Failure From- 15:16 to 15:18. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
62 | 2019-03-04 | 1028 | 1255 | 1220 | 1325 | 42.65 | 4870.65 | 4699.5 | 171.15 | 4874 | 6.234 | 0.76203 | Grid Failure From- 7:16 to 7:21. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2019-03-05 | 989 | 1205 | 1174 | 1185 | 42.06 | 4595.06 | 4437 | 158.06 | 4601 | 6.125 | 0.73215 | Grid Failure From- 10:56 to 11:03. Module Cleaning has been done in Row-,D,E,F,G,H,I, Inverter No- 4 , total module cleaning-1098.Today Cloudy day, & Today has been replaced sillicagel in transformer No-2 (300kva). |  | 1098 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
64 | 2019-03-06 | 1024 | 1255 | 1220 | 1376 | 43.24 | 4918.24 | 4748.25 | 169.99 | 4879 | 6.461 | 0.73601 | Grid Failure From- 09:42 to 09:56.Module Cleaning has been done in Row-J,K,L, & Q,R,S,T, & Trackers. Inverter No-3 & 4, total module cleaning-822. |  | 822 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2019-03-07 | 1007 | 1232 | 1235 | 1376 | 32.29 | 4882.29 | 4719.75 | 162.54 | 4886 | 6.4 | 0.74409 | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 , total module cleaning-798.Today has been replaced sillicagel in transformer No-3 & 4 (300kva). |  | 798 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2019-03-08 | 972 | 1222 | 1215 | 1320 | 42.7 | 4771.7 | 4606.5 | 165.2 | 4775 | 6.025 | 0.77245 | Module Cleaning has been done in Row-H,I,J,K,L.Inverter No-1 & 2 , total module cleaning-1323. |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2019-03-09 | 1029 | 1277 | 1245 | 1356 | 43.78 | 4950.78 | 4794 | 156.78 | 4955 | 6.437 | 0.75026 | Module Cleaning has been done in Row-A,B,C,D,E,F,G& A,B,.Inverter No-1 & 4 , total module cleaning-1044.Today Cloudy day. |  | 1044 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
68 | 2019-03-10 | 995 | 1215 | 1179 | 1285 | 42.07 | 4716.07 | 4549.5 | 166.57 | 4720 | 6.274 | 0.73325 | No Module cleaning. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2019-03-11 | 1062 | 1306 | 1275 | 1351 | 45 | 5039 | 4872 | 167 | 5045 | 6.67 | 0.7372 | Module Cleaning has been done in Row-,C,D,E,F,G. Inverter No- 4, total module cleaning-828. |  | 828 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2019-03-12 | 1063 | 1307 | 1265 | 1396 | 45 | 5076 | 4893 | 183 | 5082 | 6.641 | 0.74585 | Module Cleaning has been done in Row-,H,I,J,K,L, & Trackers. Inverter No- 4, total module cleaning-924. |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2019-03-13 | 645 | 745 | 746 | 802 | 19 | 2957 | 2841 | 116 | 2958 | 3.796 | 0.75949 | Module Cleaning has been done in Row-,N,O,P,Q,R,S,T. Inverter No- 3, total module cleaning-840. |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2019-03-14 | 983 | 905 | 1281 | 1411 | 43.5 | 4623.5 | 4418.25 | 205.25 | 4630 | 6.646 | 0.67901 | Today Inverter No-2 ABB 250KW Auto off 12:54, Due to Err Grid mom Fault (8185) Reset The Err Inverter started 14:45. & Module Cleaning has been done in Row-,J,K,L,M. Inverter No- 3, total module cleaning-1071. Grid Failure From-16:20 to 18:02. |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2019-03-15 | 1029 | 1284 | 1250 | 1351 | 43.69 | 4957.69 | 4770.75 | 186.94 | 4961 | 6.345 | 0.76206 | Module Cleaning has been done in Row-D,E,F,G,H,I.Inverter No-1 & 2 , total module cleaning-1176. |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2019-03-16 | 984 | 1187 | 1154 | 1234 | 40.87 | 4599.87 | 4447.5 | 152.37 | 4603 | 5.969 | 0.75161 | Today replaced UPS Battery 1 Nos. due to negative terminal are linkage in battery by Change Exide Industries Ltd.Grid Failure From 16:45 to 16:48.Module Cleaning has been done in Row-A,B,C & A,B,C,D,E,.Inverter No-1 & 4 , total module cleaning-771. |  | 771 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
75 | 2019-03-17 | 1006 | 1237 | 1199 | 1316 | 42.14 | 4800.14 | 4644.75 | 155.39 | 4805 | 6.424 | 0.72902 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2019-03-18 | 1041 | 1273 | 1235 | 1361 | 43.04 | 4953.04 | 4770.75 | 182.29 | 4958 | 6.596 | 0.73262 | No Module cleaning due to water pipe crack in pdpu campus side. |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2019-03-19 | 1000 | 1227 | 1195 | 1310 | 41.49 | 4773.49 | 4623.75 | 149.74 | 4777 | 6.491 | 0.71729 | No Module cleaning due to water pipe crack in pdpu campus.Grid Failure From- 08:20 to 08:28. |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2019-03-20 | 1040 | 1272 | 1240 | 1361 | 42.77 | 4955.77 | 4779.75 | 176.02 | 4959 | 6.524 | 0.74085 | Module Cleaning has been done in Row-F,G. Inverter No- 3, total module cleaning-396. |  | 396 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2019-03-21 | 1018 | 1255 | 1219 | 1306 | 42.2 | 4840.2 | 4672.5 | 167.7 | 4845 | 6.609 | 0.71451 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2019-03-22 | 995 | 1209 | 1180 | 1310 | 41.27 | 4735.27 | 4575 | 160.27 | 4739 | 6.409 | 0.72069 | Today Morning time short circuit (7:53 to 7:57) in H Pole by pigeon Fall in line ,Grid failure from 7:53 to 7:57.Module Cleaning has been done in Row-,H,I,J,K,L, &S ,T , Trackers. Inverter No- 4 & 3, total module cleaning-1010. |  | 1010 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2019-03-23 | 967 | 1170 | 1170 | 1305 | 41.87 | 4653.87 | 4497.75 | 156.12 | 4657 | 6.256 | 0.72554 | Module Cleaning has been done in Row-O,P,Q,R Inverter No- 3, total module cleaning-546. |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2019-03-24 | 972 | 1188 | 1190 | 1346 | 42.04 | 4738.04 | 4580.25 | 157.79 | 4742 | 6.374 | 0.72511 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2019-03-25 | 933 | 1136 | 1159 | 1285 | 39.09 | 4552.09 | 4406.25 | 145.84 | 4555 | 6.002 | 0.73968 | Module Cleaning has been done in Row-J,K,L,M,N, Inverter No-2 & 3, total module cleaning-1137. |  | 1137 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2019-03-26 | 989 | 1159 | 1220 | 1336 | 43.5 | 4747.5 | 4593.75 | 153.75 | 4750 | 6.455 | 0.71722 | Today Afternoon time 13:40 Inverter No: 2 fault of " DC BRK TRIP (8188)",So safemaster relay (Emergency relay) by-pass to inverter after manually started 14:10. Module Cleaning has been done in Row-E,F,G,H,I,J, Inverter No-1 & 2, total module cleaning-1194. |  | 1194 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2019-03-27 | 1001 | 1239 | 1204 | 1291 | 42 | 4777 | 4602.75 | 174.25 | 4781 | 6.556 | 0.71078 | Module Cleaning has been done in Row-A,B,C,D & A,B,C,D,E.Inverter No-1 & 4 , total module cleaning-1044.Today Cloudy day. |  | 930 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
86 | 2019-03-28 | 967 | 1198 | 1160 | 1295 | 40.92 | 4660.92 | 4511.25 | 149.67 | 4664 | 6.49 | 0.70043 | Today Replaced The D.C.12 Amp Fuse Link of The String-07++tive in AJB-100 of The Inverter-4 during The Period of 9:30 To 9:35.Grid Failure from : 10:18 to 10:21 and 18:19 to 18:28.Module Cleaning has been done in Row-F,G,H,I,J. Inverter No-4, total module cleaning-972. |  | 972 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
87 | 2019-03-29 | 995 | 1233 | 1204 | 1391 | 42.79 | 4865.79 | 4709.25 | 156.54 | 4869 | 6.313 | 0.75172 | Module Cleaning has been done in Row-K,L, &P,Q,R,S ,T , Trackers. Inverter No- 4 & 3, total module cleaning-789 |  | 789 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2019-03-30 | 995 | 1232 | 1235 | 1386 | 42.58 | 4890.58 | 4720.5 | 170.08 | 4895 | 6.535 | 0.73006 | Module Cleaning has been done in Row-K,L,M,N,O Inverter No-2 & 3, total module cleaning-1176. |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2019-03-31 | 967 | 1221 | 1205 | 1336 | 41.97 | 4770.97 | 4611 | 159.97 | 4774 | 6.481 | 0.71795 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2019-04-01 | 927 | 1176 | 1149 | 1270 | 40.91 | 4562.91 | 4404.75 | 158.16 | 4566 | 6.209 | 0.71675 | Module Cleaning has been done in Row-H,I,J, Inverter No-1 & 2, total module cleaning-798. |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2019-04-02 | 977 | 1209 | 1174 | 1300 | 40.64 | 4700.64 | 4545 | 155.64 | 4704 | 6.486 | 0.70688 | Module Cleaning has been done in Row-C,D,E,F,G, Inverter No-1 total module cleaning-777.Grid Failure From-14:03 to 14:08. |  | 777 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2019-04-03 | 990 | 1205 | 1164 | 1265 | 40.95 | 4664.95 | 4515 | 149.95 | 4668 | 6.431 | 0.70747 | Module Cleaning has been done in Row-A,B & A,B,C,D,E,F, Inverter No-1 & 4 total module cleaning-897. |  | 897 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2019-04-04 | 984 | 1204 | 1165 | 1341 | 40 | 4734 | 4581 | 153 | 4738 | 6.536 | 0.70654 | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-4 total module cleaning-936.Grid Failure From-16:23 to 16:30. |  | 936 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2019-04-05 | 972 | 1153 | 1139 | 1341 | 41.14 | 4646.14 | 4494.75 | 151.39 | 4650 | 6.121 | 0.74043 | Module Cleaning has been done in Row- L, &N,O,P,Q,R,S ,T , Trackers. Inverter No- 4 & 3, total module cleaning-1026 |  | 1026 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2019-04-06 | 989 | 1216 | 1220 | 1371 | 42.16 | 4838.16 | 4683.75 | 154.41 | 4800 | 6.403 | 0.73065 | Module Cleaning has been done in Row-J,K,L,M Inverter No-3, total module cleaning-871. |  | 871 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2019-04-07 | 962 | 1198 | 1189 | 1345 | 40.5 | 4734.5 | 4587.75 | 146.75 | 4738 | 6.397 | 0.72189 | Grid Failure From- 17:15 to 17:30. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2019-04-08 | 995 | 1255 | 1225 | 1401 | 41.82 | 4917.82 | 4752.75 | 165.07 | 4921 | 6.52 | 0.73563 | Module Cleaning has been done in Row-G,H,I,J Inverter No-1 & 2, total module cleaning-914. |  | 914 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2019-04-09 | 1034 | 1261 | 1225 | 1356 | 41.06 | 4917.06 | 4755 | 162.06 | 4921 | 6.626 | 0.72386 | Grid Failure From-08:24 to 8:34.Module Cleaning has been done in Row-A,B,C,D,E,F,& A,B,C,D. Inverter No-4 total module cleaning-1104. |  | 1104 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2019-04-10 | 1012 | 1233 | 1204 | 1336 | 40.27 | 4825.27 | 4671 | 154.27 | 4830 | 6.616 | 0.71155 | Module Cleaning has been done in Row-E,F,G,H,I. Inverter No-4, total module cleaning-954. |  | 954 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2019-04-11 | 1012 | 1232 | 1205 | 1376 | 39.32 | 4864.32 | 4695 | 169.32 | 4868 | 6.551 | 0.72426 | Module Cleaning has been done in Row-J,K,L, & P,Q,R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-969. |  | 969 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2019-04-12 | 978 | 1199 | 1210 | 1386 | 40.61 | 4813.61 | 4664.25 | 149.36 | 4815 | 6.475 | 0.72478 | Today Replaced The D.C.12 Amp Fuse Link of The String-03--tive in AJB-102 of The Inverter-4 during The Period of 10:10 To 10:15.Module Cleaning has been done in Row-K,L,M,N,O, Inverter No-2 & 3, total module cleaning-1103. |  | 1103 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
102 | 2019-04-13 | 950 | 1215 | 1189 | 1346 | 40.59 | 4740.59 | 4585.5 | 155.09 | 4744 | 6.352 | 0.72793 | Module Cleaning has been done in Row-H,I,J Inverter No-1 & 2, total module cleaning-798. |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2019-04-14 | 921 | 1142 | 1119 | 1250 | 37.99 | 4469.99 | 4320 | 149.99 | 4473 | 6.005 | 0.726 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2019-04-15 | 849 | 1006 | 988 | 1094 | 36 | 3973 | 3816.75 | 156.25 | 3975 | 5.224 | 0.74163 | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A,B,C,D. Inverter No-1 & 4 , total module cleaning-1314.Today Cloudy Day. |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
105 | 2019-04-16 | 667 | 780 | 766 | 816 | 27.52 | 3056.52 | 2940 | 116.52 | 3060 | 4.124 | 0.72319 | Grid Failure From- 15:57 to 16:35 and 16:53 to 17:50 , Today Module clean by rain. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2019-04-17 | 876 | 1194 | 1179 | 1285 | 39.61 | 4573.61 | 4413.75 | 159.86 | 4577 | 6.443 | 0.69238 | Today Morning time Inverter No: 1 are not wake up due to fault of " DC BRK TRIP (8188)" inverter after manually started 9:10.Module Cleaning has been done in Row-A,B,C,D,E,F,G,H. Inverter No- 4 , total module cleaning-1188.Today Cloudy Day., Grid Failure From- 14:15 to 14:32 and 16:52 to 17:56. |  | 1188 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
107 | 2019-04-18 | 1046 | 1277 | 1266 | 1442 | 42.04 | 5073.04 | 4899 | 174.04 | 5077 | 6.713 | 0.73713 | Module Cleaning has been done in Row-I,J,K,L, & Q,R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-1020. |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2019-04-19 | 1051 | 1295 | 1290 | 1482 | 42.31 | 5160.31 | 4990.5 | 169.81 | 5164 | 6.84 | 0.73584 | Module Cleaning has been done in Row-K,L,M,N,O,P,Inverter No- 2 & 3, total module cleaning-1323. |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2019-04-20 | 995 | 1261 | 1235 | 1406 | 40.52 | 4937.52 | 4767 | 170.52 | 4941 | 6.697 | 0.7191 | Module Cleaning has been done in Row-F,G,H,I,J,Inverter No- 1 & 2, total module cleaning-1108.Grid Failure From- 17:23 to 17:32 |  | 1108 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2019-04-21 | 1018 | 1260 | 1235 | 1396 | 41.27 | 4950.27 | 4788.75 | 161.52 | 4954 | 6.673 | 0.72358 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2019-04-22 | 1017 | 1249 | 1219 | 1381 | 40.4 | 4906.4 | 4752 | 154.4 | 4910 | 6.828 | 0.70088 | Grid Failure From-16:37 to 16:43.Module Cleaning has been done in Row-A,B,C,D,E,& A,B,C,D,E. Inverter No-1 & 4 total module cleaning-1077. |  | 1077 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2019-04-23 | 990 | 1210 | 1185 | 1341 | 39.72 | 4765.72 | 4615.5 | 150.22 | 4770 | 6.629 | 0.70133 | Module Cleaning has been done in Row-F,G,H,Inverter No-4 , total module cleaning-594. |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2019-04-24 | 989 | 1204 | 1179 | 1361 | 39.21 | 4772.21 | 4616.25 | 155.96 | 4775 | 6.523 | 0.71347 | Module Cleaning has been done in Row-I,J,K,L, & Q,R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-1020. |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2019-04-25 | 950 | 1148 | 1159 | 1330 | 38.28 | 4625.28 | 4478.25 | 147.03 | 4530 | 6.211 | 0.71087 | Grid Failure From-12:42 to 12:48.Module Cleaning has been done in Row-,L,M,N,O,P. Inverter No-2 & 3, Total module cleaning-1050. |  | 1050 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2019-04-26 | 949 | 1181 | 1180 | 1341 | 38.92 | 4689.92 | 4524.75 | 165.17 | 4673 | 6.279 | 0.72537 | Module Cleaning has been done in Row-H,I,J,K, Inverter No- 1 & 2, total module cleaning-1071. |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2019-04-27 | 1024 | 1267 | 1235 | 1421 | 40.91 | 4987.91 | 4816.5 | 171.41 | 4991 | 6.741 | 0.72163 | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A,B,C. Inverter No-1 & 4 , total module cleaning-1170. |  | 1170 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2019-04-28 | 1046 | 1283 | 1255 | 1437 | 40.92 | 5061.92 | 4912.5 | 149.42 | 5065 | 6.91 | 0.71442 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2019-04-29 | 1006 | 1250 | 1224 | 1325 | 40.16 | 4845.16 | 4701.75 | 143.41 | 4850 | 6.785 | 0.6967 | Module Cleaning has been done in Row-D,E,F,G,H. Inverter No- 4 , total module cleaning-900. |  | 900 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2019-04-30 | 989 | 1221 | 1195 | 1396 | 39.38 | 4840.38 | 4668 | 172.38 | 4844 | 6.735 | 0.701 | Grid Failure From-7:32 to 7:40.Module Cleaning has been done in Row-I,J,K,L, & R,S ,T, Trackers. Inverter No- 4 & 3, total module cleaning-898. |  | 898 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2019-05-01 | 927 | 1125 | 1109 | 1250 | 36.95 | 4447.95 | 4299.75 | 148.2 | 4451 | 6.171 | 0.703 | Grid Failure From-15:24 to 15:28. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2019-05-02 | 934 | 1130 | 1119 | 1311 | 37.89 | 4531.89 | 4380 | 151.89 | 4535 | 6.262 | 0.70586 | Grid Failure From-8:20 to 8:29. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2019-05-03 | 768 | 922 | 912 | 1063 | 32.09 | 3697.09 | 3578.25 | 118.84 | 3701 | 6.105 | 0.59086 | Grid Failure From-10:08 to 11:28 and 16:26 to 16:35. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 2019-05-04 | 905 | 1097 | 1084 | 1271 | 36.6 | 4393.6 | 4250.25 | 143.35 | 4397 | 6.037 | 0.70988 | Grid Failure From-17:34 to 17:37. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2019-04-05 | 921 | 1102 | 1093 | 1275 | 36.77 | 4427.77 | 4286.25 | 141.52 | 4431 | 6.125 | 0.7051 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2019-05-06 | 927 | 1137 | 1119 | 1305 | 37.53 | 4525.53 | 4378.5 | 147.03 | 4529 | 6.319 | 0.69856 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2019-05-07 | 945 | 1142 | 1140 | 1331 | 37.75 | 4595.75 | 4443.75 | 152 | 4599 | 6.424 | 0.69777 | Today has been done Air filter clean of all inverter.(Cabinet door Filter) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2019-05-08 | 876 | 1068 | 1058 | 1240 | 34.21 | 4276.21 | 4176 | 100.21 | 4280 | 6.493 | 0.64247 | Grid Failure From-17:34 to 17:37 & 12:11 to 12:26 and 17:08 to 17:42. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2019-05-09 | 910 | 1097 | 1084 | 1275 | 36 | 4402 | 4261.5 | 140.5 | 4406 | 6.07 | 0.70747 | Today Cloudy day & Grid Failure From-8:37 to 8:45. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
129 | 2019-05-10 | 729 | 882 | 877 | 952 | 29.21 | 3469.21 | 3342.75 | 126.46 | 3473 | 6.336 | 0.53425 | Grid Failure From-10:04 to 11:54 and 14:42 to 14:47. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2019-05-11 | 877 | 1063 | 1053 | 1266 | 34.47 | 4293.47 | 4148.25 | 145.22 | 4297 | 6.046 | 0.69271 | Grid Failure From-16:28 to 16:58. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2019-05-12 | 882 | 1057 | 1053 | 1245 | 34.4 | 4271.4 | 4135.5 | 135.9 | 4275 | 5.955 | 0.69969 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2019-05-13 | 915 | 1102 | 1094 | 1300 | 35.62 | 4446.62 | 4329.75 | 116.87 | 4450 | 6.365 | 0.68142 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2019-05-14 | 899 | 1086 | 1079 | 1265 | 35.11 | 4364.11 | 4212 | 152.11 | 4370 | 6.283 | 0.6779 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2019-05-15 | 899 | 1091 | 1083 | 1290 | 34.74 | 4397.74 | 4237.5 | 160.24 | 4401 | 6.307 | 0.68011 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2019-05-16 | 893 | 1074 | 1064 | 1255 | 34.35 | 4320.35 | 4182.75 | 137.6 | 4325 | 6.235 | 0.67609 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2019-05-17 | 843 | 1001 | 998 | 1185 | 32.07 | 4059.07 | 3918.75 | 140.32 | 4063 | 5.798 | 0.683 | Today Cloudy weather |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
137 | 2019-05-18 | 871 | 1051 | 1043 | 1219 | 33.41 | 4217.41 | 4079.25 | 138.16 | 4221 | 6.096 | 0.67487 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2019-05-19 | 847 | 1029 | 1023 | 1185 | 31.68 | 4115.68 | 3977.25 | 138.43 | 4119 | 6.04 | 0.66467 | Grid Failure From-06:45 to 06:56 and 17:28 to 17:36 & 17:43 to 17:48. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2019-05-20 | 865 | 1051 | 1084 | 1225 | 32.53 | 4257.53 | 4106.25 | 151.28 | 4261 | 6.276 | 0.66173 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2019-05-21 | 871 | 1063 | 1134 | 1240 | 32.73 | 4340.73 | 4203.75 | 136.98 | 4344 | 6.267 | 0.67559 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2019-05-22 | 882 | 1091 | 1169 | 1245 | 32.32 | 4419.32 | 4272 | 147.32 | 4423 | 6.412 | 0.67232 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2019-05-23 | 706 | 928 | 948 | 1003 | 27.64 | 3612.64 | 3485.25 | 127.39 | 3616 | 6.158 | 0.57232 | Grid Failure From-07:54 to 09:58 and 10:04 to 10:11. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2019-05-24 | 888 | 1141 | 1144 | 1199 | 31.92 | 4403.92 | 4263 | 140.92 | 4408 | 6.176 | 0.69564 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2019-05-25 | 910 | 1109 | 1104 | 1159 | 30.9 | 4312.9 | 4178.25 | 134.65 | 4316 | 6.204 | 0.67805 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2019-05-26 | 752 | 893 | 897 | 928 | 29.92 | 3499.92 | 3366 | 133.92 | 3503 | 6.062 | 0.56322 | Grid Failure From-10:46 to 12:05. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2019-05-27 | 899 | 1091 | 1079 | 1129 | 30.21 | 4228.21 | 4098.75 | 129.46 | 4232 | 6.336 | 0.651 | Grid Failure From-06:00 to 06:35 and 13:44 to 13:54. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2019-05-28 | 911 | 1091 | 1083 | 1129 | 30.22 | 4244.22 | 4107 | 137.22 | 4249 | 6.303 | 0.65704 | Grid Failure From-10:46 to 10:54. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2019-05-29 | 915 | 1108 | 1094 | 1144 | 30.19 | 4291.19 | 4150.5 | 140.69 | 4295 | 6.287 | 0.66584 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2019-05-30 | 922 | 1114 | 1104 | 1154 | 30.33 | 4324.33 | 4180.5 | 143.83 | 4328 | 6.358 | 0.66347 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2019-05-31 | 887 | 1080 | 1068 | 1109 | 29.33 | 4173.33 | 4041 | 132.33 | 4178 | 6.163 | 0.66074 | Today Replaced The D.C.12 Amp Fuse Link of The String-03 ++tive in AJB-114 of The Inverter-3 during The Period of 7:35 To 7:40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
151 | 2019-06-01 | 826 | 983 | 978 | 1003 | 26.83 | 3816.83 | 3689.25 | 127.58 | 3820 | 6.007 | 0.61981 | Grid Failure From-10:02 to 10:21 and 16:13 to 16:39. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2019-06-02 | 893 | 1069 | 1059 | 1079 | 28.67 | 4128.67 | 3992.25 | 136.42 | 4132 | 6.18 | 0.65167 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2019-06-03 | 887 | 1057 | 1048 | 1063 | 28.54 | 4083.54 | 3951.75 | 131.79 | 4087 | 6.119 | 0.65099 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2019-06-04 | 871 | 1040 | 1038 | 1038 | 30 | 4017 | 3890.25 | 126.75 | 4010 | 6.047 | 0.64633 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 2019-06-05 | 876 | 1046 | 1039 | 1049 | 27.82 | 4037.82 | 3903.75 | 134.07 | 4041 | 6.011 | 0.65523 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2019-06-06 | 831 | 995 | 988 | 988 | 27.3 | 3829.3 | 3702.75 | 126.55 | 3833 | 5.977 | 0.62504 | comissioning and installation of 110V DC FCBC Charger and Battery set (UPST 110V AH Battery) by Servilink engineer Pvt.Ltd ,Grid Failure From-14:42 to 15:00. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
157 | 2019-06-07 | 837 | 1001 | 998 | 1003 | 27.08 | 3866.08 | 3744 | 122.08 | 3870 | 5.936 | 0.63543 | Today PM of Y Phase cable changed and replaced new phase in VCB side on 'H' pole and Measuring P.T. (3 Nos) Fuses are changed and replaced new R,Y,B Line fuse in V.C.B.(12KV HCR fuses) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2019-06-08 | 825 | 995 | 992 | 998 | 27.14 | 3837.14 | 3720.75 | 116.39 | 3840 | 6.065 | 0.6171 | Grid Failure From-11:36 to 11:40. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2019-06-09 | 826 | 1000 | 993 | 988 | 26.97 | 3833.97 | 3709.5 | 124.47 | 3837 | 6.044 | 0.61876 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2019-06-10 | 808 | 956 | 953 | 942 | 26.19 | 3685.19 | 3560.25 | 124.94 | 3689 | 5.773 | 0.62282 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2019-06-11 | 786 | 938 | 932 | 917 | 25.76 | 3598.76 | 3483.75 | 115.01 | 3602 | 5.709 | 0.61495 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2019-06-12 | 673 | 792 | 787 | 797 | 22.18 | 3071.18 | 2961.75 | 109.43 | 3075 | 4.824 | 0.62128 | Today Cloudy weather.Today Replaced The D.C.12 Amp Fuse Link of The String-02 --tive in AJB-102 of The Inverter-4 during The Period of 16:00 To 16:05. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
163 | 2019-06-13 | 430 | 774 | 771 | 907 | 26.67 | 2908.67 | 2794.5 | 114.17 | 2912 | 4.315 | 0.65775 | Grid Failure From-10:07 to 10:20 and 13:58 to 14:02. Today Inverter No.1 Auto trip from 10:48 to 14:00.Today Eight Module remove from Inverter No.1 due to testing purpose for sending Laboratory (REC Singapore (4module) and HI-PYSIX LAB (4 module) .Today Cloudy weather. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
164 | 2019-06-14 | 752 | 888 | 887 | 1023 | 29.19 | 3579.19 | 3459 | 120.19 | 3583 | 4.722 | 0.73956 | Today Cloudy weather. Today four module send to HI-PYSIX LAB (PUNE) by OM Mover and Packages courier pvt ltd. Sending REC Module Details (1.JMPD100903452, 2.JMPD100904140,3.JMPD100903872,4.JMPD100902565)for module degradation testing purpose. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
165 | 2019-06-15 | 475 | 548 | 549 | 605 | 16.58 | 2193.58 | 2098.5 | 95.08 | 2197 | 2.89 | 0.74094 | Module clean by Rain & cloudy day & Grid Failure From-12:19 to 12:43 and 16:35 to 16:39. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
166 | 2019-06-16 | 745 | 899 | 897 | 973 | 25.13 | 3539.13 | 3415.5 | 123.63 | 3543 | 4.799 | 0.71957 | Module clean by Rain & cloudy day.Grid Failure From-7:51 to 8:00 and 14:26 to 14:35. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
167 | 2019-06-17 | 741 | 893 | 882 | 1043 | 27.93 | 3586.93 | 3429.75 | 157.18 | 3590 | 5.134 | 0.68154 | Module clean by Rain & cloudy day.Grid Failure From-12:56 to 13:15 and 15:22 to 16:00 & 17:21 to 17:30. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
168 | 2019-06-18 | 317 | 362 | 373 | 383 | 10.95 | 1445.95 | 1374.75 | 71.2 | 1449 | 1.985 | 0.71148 | Module clean by Rain & full cloudy day.Grid Failure From-10:56 to 11:42 and 12:18 to 12:23 & 13:32 to 13:40. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
169 | 2019-06-19 | 735 | 871 | 862 | 1008 | 27.99 | 3503.99 | 3360 | 143.99 | 3505 | 4.647 | 0.73514 | cloudy day.Grid Failure From-16:07 to 16:12. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
170 | 2019-06-20 | 690 | 808 | 802 | 928 | 26.16 | 3254.16 | 3147 | 107.16 | 3258 | 4.262 | 0.74506 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
171 | 2019-06-21 | 830 | 1006 | 998 | 1179 | 34.57 | 4047.57 | 3927 | 120.57 | 4051 | 5.486 | 0.71971 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
172 | 2019-06-22 | 854 | 1029 | 1023 | 1210 | 33.75 | 4149.75 | 4012.5 | 137.25 | 4150 | 5.697 | 0.70999 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
173 | 2019-06-23 | 888 | 1075 | 1068 | 1250 | 35.03 | 4316.03 | 4181.25 | 134.78 | 4320 | 5.837 | 0.72135 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 2019-06-24 | 475 | 542 | 545 | 604 | 18.28 | 2184.28 | 2118 | 66.28 | 2188 | 2.876 | 0.7415 | cloudy day.Grid Failure From-10:59 to 11:03 and 13:25 to 13:46 & 17:54 to 17:57. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
175 | 2019-06-25 | 695 | 826 | 821 | 963 | 28.75 | 3333.75 | 3217.5 | 116.25 | 3337 | 4.383 | 0.74206 | cloudy day.Grid Failure From-08:06 to 08:15 and 08:58 to 9:03. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
176 | 2019-06-26 | 780 | 927 | 923 | 1069 | 31.07 | 3730.07 | 3595.5 | 134.57 | 3734 | 4.914 | 0.74061 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
177 | 2019-06-27 | 848 | 1029 | 1013 | 1194 | 34.75 | 4118.75 | 3986.25 | 132.5 | 4122 | 5.557 | 0.72297 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
178 | 2019-06-28 | 600 | 701 | 700 | 791 | 24.32 | 2816.32 | 2714.25 | 102.07 | 2820 | 3.542 | 0.77598 | Today Replaced The D.C.12 Amp Fuse Link of The String-08 --tive in AJB-111 of The Inverter-2 during The Period of 18:35 To 18:40.Cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
179 | 2019-06-29 | 763 | 916 | 918 | 1074 | 31.89 | 3702.89 | 3575.25 | 127.64 | 3706 | 4.886 | 0.73927 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2019-06-30 | 865 | 1040 | 1023 | 1205 | 35.11 | 4168.11 | 4026.75 | 141.36 | 4172 | 5.612 | 0.72457 | cloudy day.Grid Failure From-7:02 to 7:10. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
181 | 2019-07-01 | 786 | 944 | 937 | 1083 | 32.19 | 3782.19 | 3672 | 110.19 | 3786 | 5.113 | 0.7217 | Today has been replaced silica gel in Transformer No-4.(300KVA), & cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
182 | 2019-07-02 | 842 | 1018 | 1013 | 1180 | 32.3 | 4085.3 | 3949.5 | 135.8 | 4089 | 5.486 | 0.72646 | Today has been done all Air filter cleaned of all inverter (Cabinet door),cloudy day. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
183 | 2019-07-03 | 859 | 1040 | 1034 | 1199 | 33.93 | 4165.93 | 4026 | 139.93 | 4169 | 5.602 | 0.72534 | Today visual Inspection all Array and checked connection of MC4 connectors and rebuild all cables throught Tie cable.cloudy day.Grid Failure From-17:25 to 18:25 and 18:29 to 18:32.cloudy day. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
184 | 2019-07-04 | 311 | 351 | 353 | 283 | 10.04 | 1308.04 | 1214.25 | 93.79 | 1312 | 1.654 | 0.77313 | Today we are found one module crack in visual inspection,Inveter no -3(Delsolar) module no-122,String line-B,ROW-M,serial no-PB10B048480207.full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
185 | 2019-07-05 | 469 | 553 | 554 | 620 | 19.39 | 2215.39 | 2102.25 | 113.14 | 2219 | 2.839 | 0.76181 | full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
186 | 2019-07-06 | 549 | 628 | 630 | 710 | 20.96 | 2537.96 | 2454.75 | 83.21 | 2540 | 3.201 | 0.77339 | full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
187 | 2019-07-07 | 627 | 724 | 726 | 822 | 23.44 | 2922.44 | 2817.75 | 104.69 | 2925 | 3.673 | 0.77617 | full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
188 | 2019-07-08 | 690 | 819 | 811 | 927 | 27.04 | 3274.04 | 3146.25 | 127.79 | 3278 | 4.326 | 0.73854 | cloudy day.Grid Failure From-08:44 to 08:52 and 09:06 to 09:11 & 13:16 to 13:20. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
189 | 2019-07-09 | 701 | 826 | 827 | 943 | 27.37 | 3324.37 | 3204.75 | 119.62 | 3328 | 4.451 | 0.72875 | Today has been done of Preventive Maintenance in Main Transformer (1250KVA) & Transformer-4 (315 KVA).(Oil Leakege of LV side,bushing gasket and tightness of cables connection and bus-bar supporter).full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
190 | 2019-07-10 | 763 | 916 | 912 | 1043 | 29.6 | 3663.6 | 3546 | 117.6 | 3667 | 4.913 | 0.72747 | Today we are found oil leakage in visual inspection on Transformer No-4 in LV side so after again (315 KVA) Preventive Maintenance has been done. |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2019-07-11 | 656 | 769 | 766 | 867 | 26.6 | 3084.6 | 2959 | 125.6 | 3085 | 4.112 | 0.73123 | full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
192 | 2019-07-12 | 797 | 955 | 953 | 1109 | 32.86 | 3846.86 | 3721.5 | 125.36 | 3850 | 5.257 | 0.7138 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
193 | 2019-07-13 | 781 | 939 | 932 | 1078 | 31.58 | 3761.58 | 3628.5 | 133.08 | 3765 | 5.128 | 0.7156 | cloudy day.Grid Failure From-7:41 to 7:52. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
194 | 2019-07-14 | 717 | 847 | 847 | 978 | 29.11 | 3418.11 | 3297.75 | 120.36 | 3422 | 4.658 | 0.71603 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
195 | 2019-07-15 | 667 | 798 | 791 | 897 | 28.17 | 3181.17 | 3068.25 | 112.92 | 3185 | 4.369 | 0.71053 | Today Replaced The D.C.12 Amp Fuse Link of The String-07--tive in AJB-117 of The Inverter-3 during The Period of 9:30 to 9:35.cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
196 | 2019-07-16 | 696 | 831 | 832 | 958 | 28.5 | 3345.5 | 3222.75 | 122.75 | 3349 | 4.719 | 0.6917 | cloudy day.Grid Failure From-07:40 to 07:47 and 14:25 to 14:32 & 16:07 to 16:22. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
197 | 2019-07-17 | 119 | 146 | 146 | 146 | 4.39 | 561.39 | 499.5 | 61.89 | 565 | 2.234 | 0.2465 | Today P.M of A.C.D.B. Panel.(change the all neutral cables in neutral busbar to MCB becuase the cables are light sparks and corrosion in lugs.) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2019-07-18 | 802 | 973 | 968 | 1104 | 31.98 | 3878.98 | 3742.5 | 136.48 | 3882 | 5.264 | 0.71877 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
199 | 2019-07-19 | 815 | 990 | 988 | 1119 | 33.38 | 3945.38 | 3812.25 | 133.13 | 3949 | 5.357 | 0.71849 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
200 | 2019-07-20 | 757 | 921 | 912 | 1028 | 27.9 | 3645.9 | 3522.75 | 123.15 | 3649 | 5.156 | 0.68978 | cloudy day.Grid Failure From-06:42 to 06:51 and 08:39 to 08:50 & 11:40 to 11:43 &15:06 to 15:08.Today we are replaced the del-solar module, Module No- 122 (ROW NO-M) and B Line , replace old Module no: PB10B048480207 to New Module no: PB10B068470359 in inverter No-3. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
201 | 2019-07-21 | 718 | 853 | 852 | 983 | 28.4 | 3434.4 | 3315 | 119.4 | 3438 | 4.544 | 0.73743 | Full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
202 | 2019-07-22 | 876 | 1097 | 1078 | 1295 | 35.84 | 4381.84 | 4224.75 | 157.09 | 4385 | 6.001 | 0.71219 | Full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
203 | 2019-07-23 | 820 | 1001 | 993 | 1180 | 32.33 | 4026.33 | 3891.75 | 134.58 | 4030 | 5.564 | 0.70594 | Today the courier company (DHL) has taken four module and send to REC GROUP Singapore.REC Module serial number Details : 1.JMPD100901615,2.JMPD100903322,3.JMPD100903188,4.JMPD100904208. Full cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
204 | 2019-07-24 | 684 | 831 | 822 | 922 | 25.48 | 3284.48 | 3170.25 | 114.23 | 3288 | 4.406 | 0.72734 | Today Replaced The D.C.12 Amp Fuse Link of The String-07 ++tive in AJB-116 of The Inverter-3 during The Period of 16:05 to16:15.full cloudy day.Grid Failure From-17:04 to 17:11. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
205 | 2019-07-25 | 582 | 690 | 680 | 756 | 22.25 | 2730.25 | 2617.5 | 112.75 | 2734 | 3.54 | 0.75275 | Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 34 (Row No-A) and A Line , old Module no:NPC10BY1130364 to replace the New Module no: NPC10BY1113790. 2)Module No-5 (Row No-D) and A Line , old Module no:NPC10BY1109685 to replace the New Module no: NPC10BY1113791.3)Module No-63 (Row No-D) and B Line , old Module no:NPC10BY108902 to replace the New Module no: NPC10BY1113792.Full cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
206 | 2019-07-26 | 486 | 565 | 570 | 640 | 18.6 | 2279.6 | 2185.5 | 94.1 | 2283 | 2.897 | 0.76809 | Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 80 (Row No-E) and A Line , old Module no:NPC10BY112719 to replace the New Module no: NPC10BY1113797. 2)Module No-20 (Row No-E) and B Line , old Module no:NPC10BY1114038 to replace the New Module no: NPC10BY1113789.3)Module No-84 (Row No-F) and B Line , old Module no:NPC10BY1111596 to replace the New Module no: NPC10BY1113793.full cloudy day.Grid Failure From16:34 to 16:40. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
207 | 2019-07-27 | 504 | 582 | 580 | 661 | 18.85 | 2345.85 | 2235 | 110.85 | 2349 | 2.912 | 0.78622 | Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 28 (Row No-G) and B Line , old Module no:NPC10BY1116216 to replace the New Module no: NPC10BY1113798. 2)Module No-16 (Row No-H) and B Line , old Module no:NPC10BY1107955 to replace the New Module no: NPC10BY1113794.3)Module No-57 (Row No-J) and B Line , old Module no:NPC10BY1130398 to replace the New Module no: NPC10BY1113795.4)Module No-14 (Row No-K) and A Line , old Module no:NPC10BY1108020 to replace the New Module no: NPC10BY1113796.Full cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
208 | 2019-07-28 | 390 | 452 | 453 | 504 | 13.56 | 1812.56 | 1729.5 | 83.06 | 1837 | 2.167 | 0.82623 | Full cloudy day.Grid Failure From-7:21 to 7:23. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
209 | 2019-07-29 | 379 | 430 | 434 | 483 | 13.45 | 1739.45 | 1629.75 | 109.7 | 1733 | 2.213 | 0.76326 | Today we are replaced the NexPower Module in Inverter No-4. 1)Module No- 27 (Row No-I) and B Line , old Module no:NPC10BY1130264 to replace the New Module no: NPC10BY1113801. 2)Module No-82 (Row No-I) and B Line , old Module no:NPC10BY1112987 to replace the New Module no: NPC10BY1113799.3)Module No-92 (Row No-I) and B Line , old Module no:NPC10BY1112888 to replace the New Module no: NPC10BY1113800.Full cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
210 | 2019-07-30 | 299 | 345 | 347 | 379 | 10.36 | 1380.36 | 1290 | 90.36 | 1389 | 1.655 | 0.81801 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
211 | 2019-07-31 | 300 | 339 | 343 | 377 | 10.57 | 1369.57 | 1275 | 94.57 | 1435 | 1.699 | 0.82321 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
212 | 2019-08-01 | 198 | 227 | 232 | 253 | 6.48 | 916.48 | 808 | 108.48 | 920 | 1.127 | 0.79564 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
213 | 2019-08-02 | 508 | 605 | 600 | 690 | 19.2 | 2422.2 | 2305 | 117.2 | 2426 | 3.147 | 0.75136 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
214 | 2019-08-03 | 289 | 333 | 338 | 388 | 10.11 | 1358.11 | 1276 | 82.11 | 1362 | 1.667 | 0.79633 | Today Replaced The D.C.12 Amp Fuse Link of The String-09 --tive in AJB-101 of The Inverter-4 during The Period of 10:10 To 10:20 (E-Line).cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
215 | 2019-08-04 | 373 | 447 | 448 | 509 | 13.82 | 1790.82 | 1695 | 95.82 | 1794 | 2.2249 | 0.7859 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
216 | 2019-08-05 | 588 | 689 | 696 | 807 | 23.81 | 2803.81 | 2692.5 | 111.31 | 2807 | 3.581 | 0.764 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
217 | 2019-08-06 | 656 | 780 | 796 | 932 | 26.83 | 3190.83 | 3077.25 | 113.58 | 3194 | 4.228 | 0.7363 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
218 | 2019-08-07 | 345 | 312 | 413 | 469 | 12.94 | 1551.94 | 1462 | 89.94 | 1555 | 2.108 | 0.71897 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
219 | 2019-08-08 | 310 | 299 | 419 | 479 | 14.15 | 1521.15 | 1437 | 84.15 | 1525 | 2.139 | 0.69488 | Today we are found the cable fault (Under ground) in AJB No. 8,9 and 10 of the Inverter No.2. So we are bypass MCB and AJB No 8 and 10 in Inverter,Because the MCB No 8 and 10 are Auto trip.cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
220 | 2019-08-09 | 176 | 158 | 201 | 226 | 5.89 | 766.89 | 675 | 91.89 | 770 | 1.018 | 0.73722 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
221 | 2019-08-10 | 130 | 125 | 162 | 177 | 4.77 | 598.77 | 519 | 79.77 | 603 | 1.128 | 0.52103 | cloudy day.Grid Failure From-10:30 to 10:36 and 12:12 to 12:51 &13:52 to 13:58 and 14:38 to 16:20. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
222 | 2019-08-11 | 509 | 497 | 589 | 721 | 21.57 | 2337.57 | 2226 | 111.57 | 2341 | 3.158 | 0.72251 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
223 | 2019-08-12 | 667 | 667 | 797 | 957 | 28.01 | 3116.01 | 2986.5 | 129.51 | 3120 | 4.475 | 0.67954 | Today has been done all air filter paper clean in all inverter. cloudy day.Grid Failure From-15:22 to 15:27 and 16:32 to 16:34. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
224 | 2019-08-13 | 757 | 769 | 902 | 1089 | 32.46 | 3549.46 | 3412.5 | 136.96 | 3553 | 5.05 | 0.68574 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
225 | 2019-08-14 | 537 | 531 | 635 | 761 | 23.06 | 2487.06 | 2400 | 87.06 | 2492 | 3.395 | 0.71542 | Full Cloudy day,Today evening time Mr.Alpha Engineers team came to cable fault finding ,found the 5 cable fault. 3 cable fault in cable peet & 2 cable fault found near 5meter cable peet. cable fault in AJB No108 ++tive and --tive, AJB No:109 --tive and AJB No:110 ++tive and --tive are faulty cable. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
226 | 2019-08-15 | 243 | 136 | 287 | 323 | 8.05 | 997.05 | 892.5 | 104.55 | 1001 | 1.413 | 0.69047 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
227 | 2019-08-16 | 419 | 237 | 474 | 569 | 15.92 | 1714.92 | 1601.25 | 113.67 | 1718 | 2.416 | 0.69307 | Today Replaced The D.C.12 Amp Fuse Link of The String-02 --tive in AJB-100 of The Inverter-4 during The Period of 9:35 to 09:40. (B-Line).full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
228 | 2019-08-17 | 497 | 227 | 575 | 686 | 19.59 | 2004.59 | 1926.75 | 77.84 | 2008 | 3.061 | 0.63937 | full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
229 | 2019-08-18 | 769 | 305 | 927 | 1149 | 34.95 | 3184.95 | 3066 | 118.95 | 3188 | 5.172 | 0.60078 | Today we are change the Contactor in AJB No.9 (MJB No-2) Positive Cable of the Inverter No-2.Cloudy Day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
230 | 2019-08-19 | 673 | 272 | 887 | 1063 | 30.8 | 2925.8 | 2791.5 | 134.3 | 2929 | 4.874 | 0.58572 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 2019-08-20 | 769 | 627 | 907 | 1104 | 32.57 | 3439.57 | 3321 | 118.57 | 3443 | 5.079 | 0.66071 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 2019-08-21 | 853 | 707 | 1023 | 1260 | 37.1 | 3880.1 | 3750 | 130.1 | 3884 | 5.799 | 0.6528 | Today we are found the cable fault in string no 3 (--tive cable) and 1( --tive cable) of the AJB No : 116 and 117. those cable are Crack and burn in cable duct. We are link the joint MC4 connector between cable. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 2019-08-22 | 837 | 695 | 1044 | 1255 | 37.34 | 3868.34 | 3723 | 145.34 | 3872 | 5.743 | 0.65713 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 2019-08-23 | 859 | 718 | 1073 | 1265 | 38.03 | 3953.03 | 3822 | 131.03 | 3957 | 5.95 | 0.64819 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 2019-08-24 | 865 | 718 | 1079 | 1270 | 37.6 | 3969.6 | 3843 | 126.6 | 3973 | 5.968 | 0.64885 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 2019-08-25 | 628 | 509 | 761 | 872 | 26.61 | 2796.61 | 2684.25 | 112.36 | 2800 | 4.216 | 0.64731 | cloudy day.Grid Failure From-15:29 to 15:40 to 16:29 and 16:31 to 16:59 &17:06. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
237 | 2019-08-26 | 107 | 102 | 181 | 192 | 5.84 | 587.84 | 524.25 | 63.59 | 636 | 0.959 | 0.64638 | Full cloudy day.Grid Failure From-13:38 to 13:40 to 14:27 and 14:35 to 16:55 &16:58.Today P.M of Inverter No-1 has been done during 14:10 to 16:20. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
238 | 2019-08-27 | 379 | 294 | 444 | 509 | 14.14 | 1640.14 | 1513 | 127.14 | 1644 | 2.294 | 0.69849 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 2019-08-28 | 424 | 333 | 514 | 585 | 16.94 | 1872.94 | 1795.5 | 77.44 | 1876 | 2.823 | 0.6477 | cloudy day.Grid Failure From-12:12 to 12:55 and 14:04 to 14:06... |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
240 | 2019-08-29 | 644 | 536 | 791 | 932 | 25.05 | 2928.05 | 2814 | 114.05 | 2932 | 4.073 | 0.70162 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 2019-08-30 | 775 | 639 | 958 | 1124 | 31.85 | 3527.85 | 3408.7 | 119.15 | 3531 | 5.247 | 0.6559 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 2019-08-31 | 447 | 351 | 530 | 604 | 21.35 | 1953.35 | 2049 | -95.65 | 1957 | 2.752 | 0.6931 | Scada net connection failure .cloudy day.Grid Failure From-14:07 to 14:19. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
243 | 2019-09-01 | 837 | 695 | 1043 | 1200 | 43.48 | 3818.48 | 3702.75 | 115.73 | 3823 | 5.809 | 0.64144 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 2019-09-02 | 604 | 497 | 746 | 877 | 30.56 | 2754.56 | 2636.25 | 118.31 | 2758 | 4.057 | 0.66259 | cloudy day.Grid Failure From-08:27 to 08:35. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
245 | 2019-09-03 | 617 | 498 | 756 | 872 | 30.091 | 2773.091 | 2670.75 | 102.341 | 2774 | 4.077 | 0.66316 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
246 | 2019-09-04 | 517 | 458 | 690 | 806 | 27.445 | 2498.445 | 2459.25 | 39.195 | 2502 | 3.776 | 0.64581 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
247 | 2019-09-05 | 322 | 260 | 404 | 469 | 16.06 | 1471.06 | 1434 | 37.06 | 1475 | 3.689 |  | Today morning time we are found VCB and Master relay are operated due to night time heavy rain and more time grid failure , we are cleared the fault and manually plant started on 12:30. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 2019-09-06 | 639 | 526 | 786 | 927 | 32.48 | 2910.48 | 2798.25 | 112.23 | 2914 | 4.408 | 0.64432 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
249 | 2019-09-07 | 605 | 502 | 766 | 827 | 32.95 | 2732.95 | 2641.5 | 91.45 | 2736 | 4.277 | 0.62349 | cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
250 | 2019-09-08 | 599 | 499 | 751 | 751 | 32.4 | 2632.4 | 2524.5 | 107.9 | 2604 | 4.798 | 0.52897 | cloudy day.Grid Failure From-09:47 to 10:58. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
251 | 2019-09-09 | 385 | 310 | 469 | 529 | 16.22 | 1709.22 | 1616.25 | 92.97 | 1713 | 2.463 | 0.67787 | Today we are changed the SPD (--tive) in AJB-104 of The Inverter-4 during the period of 18:15 to 18:30.full cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
252 | 2019-09-10 | 130 | 91 | 151 | 167 | 4.22 | 543.22 | 454.5 | 88.72 | 547 | 0.853 | 0.62502 | Full cloudy day.Grid Failure From-09:21 to 10:31 and 11:51 to 11:56 & 12:08 to 12:13 and 13:01 to 13:05. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
253 | 2019-09-11 | 373 | 288 | 449 | 493 | 15.18 | 1618.18 | 1530.75 | 87.43 | 1622 | 2.418 | 0.6538 | Full cloudy day.Grid Failure From-07:18 to 7:25 and 09:15 to 09:23 & 09:44 to 09:56. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
254 | 2019-09-12 | 299 | 226 | 352 | 389 | 11.42 | 1277.42 | 1225.5 | 51.92 | 1281 | 1.812 | 0.68904 | Full Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
255 | 2019-09-13 | 147 | 102 | 172 | 186 | 4.97 | 611.97 | 523.5 | 88.47 | 615 | 0.881 | 0.68038 | Full Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
256 | 2019-09-14 | 141 | 107 | 176 | 187 | 4.94 | 615.94 | 523.5 | 92.44 | 619 | 0.882 | 0.68403 | Full cloudy day.Grid Failure From-11:06 to 11:08 and 13:17 to 13:19. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
257 | 2019-09-15 | 362 | 283 | 439 | 504 | 15.96 | 1603.96 | 1506.75 | 97.21 | 1607 | 2.331 | 0.67193 | Full Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
258 | 2019-09-16 | 684 | 565 | 851 | 993 | 37.16 | 3130.16 | 3011.25 | 118.91 | 3134 | 4.664 | 0.65493 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2019-09-17 | 752 | 622 | 993 | 1103 | 39.94 | 3509.94 | 3343.5 | 166.44 | 3513 | 5.319 | 0.64373 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 2019-09-18 | 685 | 565 | 852 | 993 | 20.72 | 3115.72 | 3016.5 | 99.22 | 3119 | 4.148 | 0.73287 | cloudy day.Grid Failure From-09:42 to 09:43 and 16:13 to 16:17. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
261 | 2019-09-19 | 734 | 611 | 912 | 1074 | 41.14 | 3372.14 | 3258 | 114.14 | 3376 | 5.138 | 0.64041 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
262 | 2019-09-20 | 651 | 543 | 817 | 968 | 34.78 | 3013.78 | 2900.25 | 113.53 | 3017 | 4.581 | 0.6419 | cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
263 | 2019-09-21 | 582 | 475 | 720 | 836 | 29.13 | 2642.13 | 2535.75 | 106.38 | 2646 | 3.945 | 0.65373 | cloudy day.Grid Failure From-15:17 to 15:19. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
264 | 2019-09-22 | 452 | 367 | 555 | 656 | 22.57 | 2052.57 | 1962 | 90.57 | 2056 | 3.097 | 0.64705 | cloudy day.Grid Failure From-11:36 to 11:41. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
265 | 2019-09-23 | 594 | 487 | 741 | 836 | 30.08 | 2688.08 | 2572.5 | 115.58 | 2753 | 4.001 | 0.67064 | cloudy day.Grid Failure From-11:36 to 11:41. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
266 | 2019-09-24 | 825 | 706 | 1053 | 1275 | 49.02 | 3908.02 | 3790.5 | 117.52 | 3912 | 6.117 | 0.62332 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | 2019-09-25 | 684 | 594 | 882 | 1059 | 39.26 | 3258.26 | 3132.75 | 125.51 | 3262 | 4.988 | 0.6374 | Grid Failure From-12:47 to 12:49. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | 2019-09-26 | 486 | 390 | 595 | 695 | 21.58 | 2187.58 | 2087.25 | 100.33 | 2191 | 3.158 | 0.67621 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
269 | 2019-09-27 | 305 | 232 | 363 | 409 | 11.83 | 1320.83 | 1230.75 | 90.08 | 1324 | 1.826 | 0.70671 | Full cloudy day.Grid Failure From-08:02 to 08:11. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
270 | 2019-09-28 | 526 | 435 | 655 | 761 | 26.22 | 2403.22 | 2300.25 | 102.97 | 2407 | 3.539 | 0.6629 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
271 | 2019-09-29 | 436 | 345 | 529 | 600 | 18.01 | 1928.01 | 1827 | 101.01 | 1926 | 2.538 | 0.73963 | Full cloudy day.Grid Failure From-13:38 to 13:45. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
272 | 2019-09-30 | 192 | 147 | 232 | 272 | 8 | 851 | 759 | 92 | 854 | 1.232 | 0.67562 | Full cloudy day.Grid Failure From-14:30 to 14:42. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
273 | 2019-10-01 | 633 | 531 | 801 | 942 | 33.88 | 2940.88 | 2828.25 | 112.63 | 2944 | 4.547 | 0.63105 | Today Replaced The D.C.12 Amp Fuse Link of The String-09 --tive in AJB-105 of The Inverter-1 during The Period of 8:40 to 08:47. (H-Line).Grid Failure From-14:54 to 15:05.full cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
274 | 2019-10-02 | 774 | 656 | 983 | 1149 | 44.6 | 3606.6 | 3483.75 | 122.85 | 3610 | 5.482 | 0.64183 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
275 | 2019-10-03 | 255 | 582 | 872 | 1008 | 33.88 | 2750.88 | 2685.75 | 65.13 | 2755 | 4.922 | 0.54555 | Today Inverter No 1 under breakdown during 11:00 (3-10-19) to 19:00 (4-10-19) due to Install MIRU-01 in Inverter by ABB. Cloudy day.Grid Failure From-16:45 to 16:54 and 17:16 to 17:18. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
276 | 2019-10-04 | 329 | 520 | 1064 | 1230 | 47.41 | 3190.41 | 3090.25 | 100.16 | 3196 | 6.071 | 0.5131 | Today Inverter No 2 under breakdown during 14:02 (4-10-19) to 19:00(4-10-19) due to Install MIRU-01 in Inverter by ABB. Grid Failure From-9:44 to 9:49. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2019-10-05 | 766 | 661 | 993 | 1180 | 45.88 | 3645.88 | 3515.25 | 130.63 | 3651 | 5.655 | 0.62926 | Today we are Install new Cooling fan in inverter no-1. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 2019-10-06 | 751 | 670 | 1003 | 1149 | 46.17 | 3619.17 | 3491.25 | 127.92 | 3625 | 5.737 | 0.61585 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2019-10-07 | 766 | 671 | 993 | 1134 | 42.97 | 3606.97 | 3471 | 135.97 | 3610 | 5.794 | 0.60727 | Grid Failure From-12:33 to 12:45 and 13:48 to 13:53. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 2019-10-08 | 811 | 730 | 1093 | 1255 | 50.7 | 3939.7 | 3814.5 | 125.2 | 3944 | 6.107 | 0.62945 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 2019-10-09 | 736 | 655 | 968 | 1114 | 43.87 | 3516.87 | 3388.5 | 128.37 | 3520 | 5.566 | 0.61639 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 2019-10-10 | 792 | 661 | 1048 | 1209 | 48.81 | 3758.81 | 3629.25 | 129.56 | 3762 | 5.946 | 0.61666 | Today morning time inverter No-1 ABB 250KW are not wakeup due to Err DC Bracker Trip(8188), Reset the Err manually than inverter started-8:49. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2019-10-11 | 856 | 781 | 1150 | 1336 | 55.04 | 4178.04 | 4042.5 | 135.54 | 4182 | 6.627 | 0.61506 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
284 | 2019-10-12 | 867 | 776 | 1154 | 1326 | 54.87 | 4177.87 | 4043.25 | 134.62 | 4181 | 6.505 | 0.62645 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
285 | 2019-10-13 | 827 | 741 | 1094 | 1255 | 53.66 | 3970.66 | 3837.75 | 132.91 | 3975 | 6.238 | 0.62108 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2019-10-14 | 796 | 711 | 1033 | 1214 | 48.24 | 3802.24 | 3670.5 | 131.74 | 3806 | 6.112 | 0.60693 | Today we are found the cable fault in string no 1(--tive cable) of the AJB No:117 of inverter no-3. those cable are crack and burn in cable duct. We are link and joint new MC4 connector. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2019-10-15 | 782 | 700 | 1038 | 1205 | 47.97 | 3772.97 | 3651.75 | 121.22 | 3776 | 6.013 | 0.61206 | Today has been done all Air filter paper cleaned of all inverter and inverter no-2 only one change sqaure filter paper.(Cabinet door Filter).Grid Failure From-16:07 to 16:13. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2019-10-16 | 776 | 686 | 1008 | 1154 | 47.82 | 3671.82 | 3467.25 | 204.57 | 3675 | 5.848 | 0.6125 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 2019-10-17 | 751 | 650 | 978 | 1129 | 46.17 | 3554.17 | 3504.75 | 49.42 | 3560 | 5.701 | 0.60863 | Today we are found oil leakage in visual inspection on Transformer No-4 in LV side, (315 KVA) Preventive Maintenance is not done oil leakge continue in B-Phase...,Module Cleaning has been done in Row- A,B,C. Inverter No-4 , total module cleaning-288. |  | 288 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
290 | 2019-10-18 | 736 | 645 | 953 | 1104 | 44.06 | 3482.06 | 3360 | 122.06 | 3486 | 5.585 | 0.60835 | Today we are found oil leakage in visual inspection on Transformer No-4 in LV side, (315 KVA) Preventive Maintenance is not done oil leakge continue in B-Phase..,Module Cleaning has been done in Row- A,D,E. Inverter No-4 , total module cleaning-275. |  | 275 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2019-10-19 | 741 | 640 | 942 | 1074 | 43.33 | 3440.33 | 3310.5 | 129.83 | 3444 | 5.507 | 0.60954 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
292 | 2019-10-20 | 690 | 590 | 872 | 993 | 40.21 | 3185.21 | 3066 | 119.21 | 3189 | 5.113 | 0.6079 | Module Cleaning has been done in Row-F,G, nverter No-4 , total module cleaning-410. |  | 410 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 2019-10-21 | 595 | 489 | 726 | 836 | 31.35 | 2677.35 | 2571 | 106.35 | 2681 | 4.134 | 0.63209 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
294 | 2019-10-22 | 549 | 549 | 685 | 802 | 31.05 | 2616.05 | 2418 | 198.05 | 2620 | 4.651 | 0.54904 | Today Replaced The D.C.12 Amp Fuse Link of The String-05 ++tive in AJB-104 of The Inverter-4 during The Period of 8:30 to 08:35.Grid Failure From 10:49 to 11:47 and 16:14 to 16:22. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
295 | 2019-10-23 | 101 | 80 | 121 | 136 | 13.19 | 451.19 | 372.75 | 78.44 | 455 | 5.765 | 0.076925 | Grid Failure From-09:27 to 14:00. Grid failure after All Inverter not start because Inverter NO -1 and 2 error is " GRID MON FLT" and Inverter NO-3 and 4 error is " Under Votage and Over Current during 14:00 (23.10.19) to 18:00 (24.10.19) and after called ABB and came Arifbhai and resolve problem on 25.10.2019. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2019-10-24 | [5 empty] | 0 |  | 0 |  | 5.247 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2019-10-25 | 257 | 227 | 504 | 645 | 48.07 | 1681.07 | 1559.25 | 121.82 | 1685 | 5.126 | 0.32039 | Yesterday night Government side 11KV line fuse failure after plant started on 12:30. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2019-10-26 | 560 | 414 | 686 | 786 | 24.21 | 2470.21 | 2356.5 | 113.71 | 2475 | 3.844 | 0.62754 | Today we are changed and replaced MCB (ABB ,3-Pole and 125Amp) in AJB No: 8 of Inverter No-2 in Main Junction Box because the negative terminal by pass in MCB.Today we are Install the new DC RR Cable 70Sqmm in AJB No-8 (++tive and --tive)and 10(++tive and --tive) of Inverter No-2 due to those cable are underground fault (puncture and cut) on 8 Aug 2019 |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2019-10-27 | 332 | 397 | 393 | 469 | 14.03 | 1605.03 | 1509.75 | 95.28 | 1610 | 2.179 | 0.72015 | full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
300 | 2019-10-28 | 469 | 590 | 585 | 700 | 20.87 | 2364.87 | 2241 | 123.87 | 2368 | 3.339 | 0.69122 | full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
301 | 2019-10-29 | 494 | 620 | 604 | 741 | 21.84 | 2480.84 | 2366.25 | 114.59 | 2484 | 3.459 | 0.69993 | Today Replaced the D.C.12 Amp fuse link of the string-08 --tive in AJB-110 of The Inverter-2 during the period of 7:35 to 07:40. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
302 | 2019-10-30 | 796 | 1084 | 1059 | 1260 | 29.76 | 4228.76 | 4077.25 | 151.51 | 4232 | 5.638 | 0.7316 | Module clean by rain |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2019-10-31 | 731 | 943 | 932 | 1084 | 29.35 | 3719.35 | 3583.5 | 135.85 | 3723 | 5.281 | 0.68712 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2019-11-01 | 751 | 977 | 978 | 1124 | 30.54 | 3860.54 | 3720 | 140.54 | 3864 | 5.589 | 0.67384 | Grid Failure From-17:06 to 17:08. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 2019-11-02 | 343 | 403 | 408 | 469 | 13.61 | 1636.61 | 1548 | 88.61 | 1640 | 2.204 | 0.72525 | Today Replaced the D.C.12 Amp fuse link of the string-07 ++tive in AJB-105 of The Inverter-4 during the period of 9:30 to 09:35.Fully cloudy day.Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
306 | 2019-11-03 | 403 | 484 | 489 | 569 | 15.99 | 1960.99 | 1849.5 | 111.49 | 1964 | 2.559 | 0.74804 | Full cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
307 | 2019-11-04 | 640 | 701 | 847 | 998 | 26.64 | 3212.64 | 3099.75 | 112.89 | 3216 | 4.97 | 0.63068 | Today we are Install the new DC RR Cable 70Sqmm in AJB No-106 ( --tive)and AJB No: 109(++tive and --tive) of Inverter No-2 due to those cable are underground fault (puncture and cutting) on 8 Aug 2019.Grid Failure From-10:04 to 10:21. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2019-11-05 | 666 | 852 | 857 | 988 | 28.19 | 3391.19 | 3262.5 | 128.69 | 3395 | 4.953 | 0.66807 | Grid Failure From-06:40 to 08:00. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2019-11-06 | 654 | 836 | 842 | 958 | 27.35 | 3317.35 | 3189 | 128.35 | 3321 | 4.794 | 0.67519 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2019-11-07 | 459 | 565 | 569 | 645 | 17.42 | 2255.42 | 2147.25 | 108.17 | 2259 | 3.143 | 0.70053 | Today breakdown of Inverter No-4 during 17:08 18:51 due to Oil leakege in B Phase has been completed by Alpha Engineers Company Pvt.ltd and Change O-ring in B-phase.Grid Failure From-15:42 to 15:46. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2019-11-08 | 600 | 756 | 751 | 887 | 24.94 | 3018.94 | 2879.25 | 139.69 | 3022 | 4.294 | 0.68594 | Grid Failure From-08:03 to 08:32 and 08:53 to 08:58 and 17:05 to 17:40.. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2019-11-09 | 716 | 922 | 923 | 1053 | 29.98 | 3643.98 | 3525 | 118.98 | 3647 | 5.262 | 0.67552 | Grid Failure From-13:15 to 13:20. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 2019-11-10 | 665 | 852 | 851 | 963 | 28.28 | 3359.28 | 3242.25 | 117.03 | 3363 | 4.889 | 0.67044 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 2019-11-11 | 595 | 756 | 761 | 832 | 25.84 | 2969.84 | 2856 | 113.84 | 2973 | 4.415 | 0.65632 | Grid Failure From-07:07 to 07:57 and 16:51 to 16:58. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2019-11-12 | 645 | 852 | 847 | 968 | 28.38 | 3340.38 | 3206.25 | 134.13 | 3344 | 4.961 | 0.65698 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2019-11-13 | 661 | 846 | 847 | 972 | 27.84 | 3353.84 | 3222.75 | 131.09 | 3357 | 4.949 | 0.66113 | Grid Failure From-08:15 to 08:26 and 16:40 to 16:47. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2019-11-14 | 670 | 857 | 852 | 958 | 28.07 | 3365.07 | 3228 | 137.07 | 3369 | 4.938 | 0.66497 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2019-11-15 | 131 | 147 | 147 | 156 | 5.61 | 586.61 | 518.25 | 68.36 | 590 | 3.915 | 0.14688 | Today Replaced the D.C.12 Amp fuse link of the string-06 --tive in AJB-102 of The Inverter-4 during the period of 8:40 to 08:45.Grid Failure From-09:23 to 015:42.Today we are send submersible pump to service and repaire at Umiya Electrical,Gandhinagar.MOdule cleaning not done 5-11-19 to 17-11-19 due to motor not start. |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
319 | 2019-11-16 | 534 | 710 | 695 | 817 | 27.89 | 2783.89 | 2653.5 | 130.39 | 2787 | 4.861 | 0.55881 | Grid Failure From-07:07 to 09:58 and 16:49 to 16:54. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2019-11-17 | 645 | 827 | 837 | 892 | 27.5 | 3228.5 | 3073.5 | 155 | 3232 | 4.746 | 0.66374 | Module Cleaning has been done in Row-A,B,C, Inverter No-4 , total module cleaning-288. |  | 288 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2019-11-18 | 615 | 776 | 796 | 867 | 26.65 | 3080.65 | 2937 | 143.65 | 3084 | 4.486 | 0.67005 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2019-11-19 | 676 | 888 | 903 | 993 | 29.55 | 3489.55 | 3334.5 | 155.05 | 3493 | 5.17 | 0.65851 | Today Replaced the D.C.12 Amp fuse link of the string-05 ++tive in AJB-105 of The Inverter-4 during the period of 9:00 to 09:05. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
323 | 2019-11-20 | 614 | 795 | 811 | 897 | 25.45 | 3142.45 | 2991 | 151.45 | 3146 | 5.203 | 0.58933 | Module Cleaning has been done in Row-D,E,F, Inverter No-4 , total module cleaning-504.Grid Failure From-10:37 to 10:58 and 12:50 to 13:12. |  | 504 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2019-11-21 | 681 | 882 | 897 | 1033 | 28.8 | 3521.8 | 3369.75 | 152.05 | 3525 | 5.272 | 0.65168 | Module Cleaning has been done in Row-G,H,I, Inverter No-4 , total module cleaning-496.Grid Failure From-08:52 to 08:58. |  | 496 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2019-11-22 | 635 | 832 | 837 | 988 | 27.04 | 3319.04 | 3162 | 157.04 | 3323 | 5.134 | 0.63085 | Module Cleaning has been done in Row-I,J, Inverter No-4 , total module cleaning-280.Grid Failure From-08:30 to 08:52 and 09:43 to 09:51. |  | 280 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2019-11-23 | 595 | 751 | 771 | 907 | 25.88 | 3049.88 | 2910.75 | 139.13 | 3053 | 4.421 | 0.67307 | Grid Failure From-08:54 to 08:57. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2019-11-24 | 615 | 792 | 802 | 953 | 27.44 | 3189.44 | 3048 | 141.44 | 3193 | 4.7 | 0.66215 | Module Cleaning has been done in Row K,L & S,T and Tracker ,Inverter No-4 and 3 , total module cleaning-432. |  | 432 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2019-11-25 | 589 | 750 | 776 | 887 | 26.31 | 3028.31 | 2892.75 | 135.56 | 3032 | 4.449 | 0.66423 | Module Cleaning has been done in Row Q,R,S,T ,Inverter No-3 ,total module cleaning-294 |  | 294 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2019-11-26 | 580 | 741 | 796 | 872 | 29.29 | 3018.29 | 2867.25 | 151.04 | 3022 | 4.343 | 0.6782 | Module Cleaning has been done in Row N.O.P ,Inverter No-3, total module cleaning-546. |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2019-11-27 | 529 | 666 | 751 | 771 | 24.17 | 2741.17 | 2612.25 | 128.92 | 2745 | 3.985 | 0.67138 | Module Cleaning has been done in Row-L, M, Inverter No-2 and 3, total module cleaning-504. |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2019-11-28 | 544 | 731 | 776 | 817 | 24.98 | 2892.98 | 2755.5 | 137.48 | 2896 | 4.106 | 0.68744 | Module Cleaning has been done in Row-J,K , Inverter No-2 , total module cleaning-567. |  | 567 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2019-11-29 | 550 | 761 | 787 | 806 | 25.25 | 2929.25 | 2794.5 | 134.75 | 2933 | 4.15 | 0.68884 | Module Cleaning has been done in Row-I , Inverter No-2 , total module cleaning-273. |  | 273 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2019-11-30 | 590 | 826 | 846 | 887 | 13.19 | 3162.19 | 3036.75 | 125.44 | 3164 | 4.498 | 0.6856 | Today we are install new Tracker controller with display unit in Tracker no-6.Now Tracker no-5 and 6 working condition.Grid Failure From-16:17 to 16:24. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2019-12-01 | 625 | 857 | 867 | 928 | 43.61 | 3320.61 | 3170.25 | 150.36 | 3324 | 4.668 | 0.69404 | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-1 , total module cleaning-903. |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2019-12-02 | 650 | 827 | 837 | 871 | 41.17 | 3226.17 | 3070.5 | 155.67 | 3230 | 4.594 | 0.68527 | Module Cleaning has been done in Row-A,B,C and A,B,C, Inverter No-1 & 4 , total module cleaning-498. |  | 498 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2019-12-03 | 655 | 836 | 852 | 903 | 42.77 | 3288.77 | 3141 | 147.77 | 3292 | 4.668 | 0.68736 | Module Cleaning has been done in Row-D,E,F,G,H, Inverter No-4 , total module cleaning-900. |  | 900 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2019-12-04 | 600 | 757 | 766 | 841 | 36.93 | 3000.93 | 2858.25 | 142.68 | 3004 | 4.156 | 0.70449 | Module Cleaning has been done in Row-I,J,K, Inverter No-4 , total module cleaning-540. |  | 540 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2019-12-05 | 534 | 670 | 690 | 777 | 32.06 | 2703.06 | 2568 | 135.06 | 2707 | 3.639 | 0.72503 | Module Cleaning has been done in Row L & O,P,Q,R,S,T and Tracker ,Inverter No-4 and 3 , total module cleaning-816.Grid Failure From-15:36 to 15:41. |  | 816 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2019-12-06 | 393 | 469 | 514 | 549 | 20.24 | 1945.24 | 1824 | 121.24 | 1949 | 2.485 | 0.76443 | Module Cleaning has been done in Row-K,L,M,N Inverter No-2 and 3 , total module cleaning-987.Today we are change safe master relay "BD5935" in Inverter No:2 and Installed new relay by Salimbhai ABB. |  | 987 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2019-12-07 | 610 | 786 | 787 | 867 | 40.48 | 3090.48 | 2964.75 | 125.73 | 3094 | 4.289 | 0.7031 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2019-12-08 | 661 | 866 | 857 | 912 | 45.01 | 3341.01 | 3217.5 | 123.51 | 3350 | 4.701 | 0.69456 | Module Cleaning has been done in Row-H,I,J ,Inverter No-1 and 2 , total module cleaning-798. |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2019-12-09 | 690 | 903 | 887 | 953 | 46.48 | 3479.48 | 3344.25 | 135.23 | 3483 | 4.87 | 0.69707 | Module Cleaning has been done in Row-A,B,C,D,E,F,G & A,B,C,D ,Inverter No-1 and 4 , total module cleaning-1314. |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2019-12-10 | 705 | 918 | 902 | 998 | 48.65 | 3571.65 | 3439.5 | 132.15 | 3575 | 5.064 | 0.68807 | Module Cleaning has been done in Row-E,F,G ,Inverter No-4 , total module cleaning-558. |  | 558 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 2019-12-11 | 706 | 927 | 907 | 1018 | 48.99 | 3606.99 | 3475.5 | 131.49 | 3610 | 5.164 | 0.68136 | Module Cleaning has been done in Row-H,I,J,K,L and Tracker ,Inverter No-4 , total module cleaning-924. |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 2019-12-12 | 670 | 861 | 857 | 973 | 46.26 | 3407.26 | 3274.5 | 132.76 | 3412 | 4.746 | 0.7007 | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T ,Inverter No-3 , total module cleaning-1092. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2019-12-13 | 661 | 873 | 872 | 983 | 46.86 | 3435.86 | 3297.75 | 138.11 | 3439 | 4.751 | 0.7055 | Module Cleaning has been done in Row-I,J,K,L ,Inverter No-2 , total module cleaning-969. |  | 969 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 2019-12-14 | 731 | 973 | 952 | 1068 | 53.99 | 3777.99 | 3642 | 135.99 | 3781 | 5.26 | 0.70061 | Today we are change string cable of AJB No-07 and 10,String Number 7 in AJB No-7 and String number-1 in AJB No-10 due to Under ground fault. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2019-12-15 | 741 | 1043 | 978 | 1094 | 55.61 | 3911.61 | 3767.25 | 144.36 | 3915 | 5.304 | 0.71942 | Module Cleaning has been done in Row-F,G,H ,Inverter No-1 , total module cleaning-630. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2019-12-16 | 766 | 1058 | 998 | 1114 | 57.35 | 3993.35 | 3840.75 | 152.6 | 3997 | 5.445 | 0.71547 | Module Cleaning has been done in Row-A,B,C,D,E & A ,Inverter No-1 and 4 , total module cleaning-636. |  | 636 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 2019-12-17 | 791 | 1099 | 1028 | 1149 | 59.52 | 4126.52 | 3972 | 154.52 | 4131 | 5.632 | 0.7149 | Module Cleaning has been done in Row-B,C,D,E,F ,Inverter No-4 , total module cleaning-720.Today we are replaced the Nex Power Module in Inverter No-4. 1)Module No- 64 (Row No-E) and A Line , old Module no:NPC10BY1109824 to replace the New Module no: NPC10BY1113802. |  | 720 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2019-12-18 | 680 | 932 | 878 | 978 | 47.06 | 3515.06 | 3384.75 | 130.31 | 3536 | 4.765 | 0.72327 | Module Cleaning has been done in Row-,G,H,I, Inverter No-4 , total module cleaning-594. & Today we are replaced new phase failure relay (S2 VMR3) in inverter No-1 ABB 250KW. & Grid Failure from-16:48 to 16:54. |  | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2019-12-19 | 706 | 978 | 922 | 1058 | 51.02 | 3715.02 | 3570.75 | 144.27 | 3719 | 5.099 | 0.71088 | Module Cleaning has been done in Row-J,K,L & Q,R,S,T and Tracker ,Inverter No-4 and 3 , total module cleaning-822. and Grid Failure from-08:25 to 08:30. |  | 822 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2019-12-20 | 691 | 953 | 912 | 1033 | 51.01 | 3640.01 | 3500.25 | 139.76 | 3645 | 4.971 | 0.71467 | Module Cleaning has been done in row-L,M,N,O,P ,Inverter No-2 and 3 , total module cleaning-1050. and Grid Failure from-17:17 to 17:19. |  | 1050 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2019-12-21 | 670 | 922 | 892 | 988 | 49.03 | 3521.03 | 3386.25 | 134.78 | 3525 | 4.842 | 0.70956 | Today has been done all Air filter paper cleaned of all inverter (Cabinet door Filter).Grid Failure From-11:41 to 11:45 and 17:17 to 17:25. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2019-12-22 | 600 | 826 | 792 | 842 | 39.83 | 3099.83 | 2973 | 126.83 | 3104 | 3.988 | 0.75861 | Module Cleaning has been done in row-I,J,K ,Inverter No-2, total module cleaning-840. |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2019-12-23 | 569 | 772 | 730 | 761 | 35.55 | 2867.55 | 2751 | 116.55 | 2868 | 3.875 | 0.72137 | Module Cleaning has been done in row-H,G,F,Inverter No-1, total module cleaning-630. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2019-12-24 | 640 | 872 | 817 | 872 | 41.99 | 3242.99 | 3117 | 125.99 | 3245 | 4.511 | 0.70112 | Module Cleaning has been done in row-,A,B,C,D,E, Inverter No-1, total module cleaning-594 & Today we are replaced 2 led lamp in CRC Panel (DC110) & 1 in VCB Panel (230AC). |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2019-12-25 | 651 | 877 | 832 | 882 | 42.78 | 3284.78 | 3155 | 129.78 | 3287 | 4.56 | 0.70257 | Module Cleaning has been done in row-A,B,C,D,E,F,G,Inverter No-4, total module cleaning-990. |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2019-12-26 | 695 | 972 | 887 | 1013 | 51.22 | 3618.22 | 3480 | 138.22 | 3622 | 4.815 | 0.73317 | Module Cleaning has been done in row-H,I,J,K,Inverter No-4, total module cleaning-732. |  | 732 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2019-12-27 | 832 | 1175 | 1083 | 1260 | 65.57 | 4415.57 | 4254.75 | 160.82 | 4418 | 6.182 | 0.69655 | Module Cleaning has been done in row-L,& Q,R,S,T, & Tracker,Inverter No-4 & 3, total module cleaning-480. Today Replaced the D.C.12 Amp fuse link of the string-03 ++tive in AJB-111 of The Inverter-3 during the period of 14:30 to 14:35. |  | 480 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
361 | 2019-12-28 | 831 | 1164 | 1099 | 1250 | 67.57 | 4411.57 | 4245.75 | 165.82 | 4415 | 6.046 | 0.71173 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2019-12-29 | 610 | 827 | 796 | 852 | 40.48 | 3125.48 | 2993.25 | 132.23 | 3129 | 4.103 | 0.74329 | Module Cleaning has been done in Row-N,O,P ,Inverter No-3 , total module cleaning-546. cloudy day |  | 546 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
363 | 2019-12-30 | 751 | 1053 | 1013 | 1099 | 57.45 | 3973.45 | 3828 | 145.45 | 3974 | 5.503 | 0.70385 | Module Cleaning has been done in Row- J,K,L,M ,Inverter No-2 and 3 , total module cleaning-925.Today Replaced the D.C.12 Amp fuse link of the string-09 ++tive in AJB-101 of The Inverter-4 during the period of 8:35 to 08:40.and replaced the connector in string-02 in AJB-113 of The Inverter-3. |  | 925 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
364 | 2019-12-31 | 645 | 907 | 852 | 882 | 44.45 | 3330.45 | 3238 | 92.45 | 3332 | 4.605 | 0.70523 | Module Cleaning has been done in Row-G,H,I, Inverter No-1&2, total module cleaning-714. cloudy day and Grid Failure from-16:40 to 17:46. |  | 714 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0

## 2020
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2020-01-01 | 545 | 721 | 686 | 690 | 31.78 | 2673.78 | 2559 | 114.78 | 2679 | 3.556 | 0.73428 | Module Cleaning has been done in Row-B,C,D,E,F, Inverter No-1, total module cleaning-624. cloudy day and Grid Failure from-14:20 to 14:24 . |  | 624 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
1 | 2020-01-02 | 580 | 781 | 731 | 756 | 34.56 | 2882.56 | 2748.75 | 133.81 | 2888 | 3.974 | 0.70831 | Module Cleaning has been done in Row-A,& A,B,C,D,E,F,G Inverter No-1&4, total module cleaning-1032. cloudy day and Grid Failure from-15:13 to 15:15 and 15:20 to 15:25. |  | 1032 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
2 | 2020-01-03 | 604 | 807 | 766 | 817 | 37.06 | 3031.06 | 2903.25 | 127.81 | 3036 | 4.061 | 0.72865 | Module Cleaning has been done in Row-H,I,J,K, Inverter No-4, total module cleaning-738.Today Replaced the connector of the string-01 in AJB-112 of The Inverter-3. |  | 738 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2020-01-04 | 666 | 912 | 852 | 892 | 44 | 3366 | 3226.5 | 139.5 | 3371 | 4.634 | 0.70901 | crack |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2020-01-05 | 625 | 852 | 811 | 922 | 47.54 | 3257.54 | 3126.75 | 130.79 | 3263 | 5.407 | 0.58818 | Module Cleaning has been done in Row-O,R,S,T and L and Tracker, Inverter No-3 and 4, total module cleaning-480. cloudy day and Grid Failure from-11:30 to 12:38 .Today we are replaced the connector in string-08 in AJB-111 of The Inverter-3(L-line). |  | 480 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
5 | 2020-01-06 | 710 | 973 | 953 | 1054 | 53.16 | 3743.16 | 3609.75 | 133.41 | 3749 | 5.167 | 0.70718 | Module Cleaning has been done in Row-L,M,N,O,P, Inverter No-2 and 3, total module cleaning-924. |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2020-01-07 | 524 | 700 | 695 | 731 | 33.05 | 2683.05 | 2559.75 | 123.3 | 2688 | 3.688 | 0.71038 | Today came Mahindra Teqo company for On-site Testing of PV Module . Today only Flash Test Done on REC module(5+1 new module(6 Qty) and DEL Solar (5 Qty)module by REC Groups ,At- 1MW Solar Power Plant ,PDPU., Module Cleaning has been done in Row-K,L Inverter No-2 total module cleaning-399,cloudy day. |  | 399 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
7 | 2020-01-08 | 706 | 993 | 948 | 1028 | 51.23 | 3726.23 | 3586 | 140.23 | 3732 | 5.054 | 0.71971 | Module Cleaning has been done in Row-F,G,H,I, Inverter No-1&2, total module cleaning-903. cland Grid Failure from-11:06 to 11:11 |  | 903 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2020-01-09 | 837 | 1185 | 1124 | 1230 | 66.68 | 4442.68 | 4275 | 167.68 | 4448 | 5.652 | 0.76704 | Today came Mahindra Teqo company for On-site Testing of PV Module . Today only EL Test Done on REC module(5+1 new module(6 Qty) and DEL Solar (5 Qty)module by REC Groups ,At- 1MW Solar Power Plant ,PDPU., Module Cleaning has been done in Row-C,D,E,Inverter No-1 total module cleaning-438. |  | 438 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2020-01-10 | 685 | 973 | 897 | 972 | 54.02 | 3581.02 | 3461 | 120.02 | 3587 | 5.878 | 0.59478 | Module Cleaning has been done in Row-A,B.And,A,B,C, Inverter No-1&4, total module cleaning-393,Today we are replaced the 2(32A-2P) MCB in ACDB.Grid Failure from-12:14 to 13:23.Today we are reconnect testing module (10 Module) |  | 393 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2020-01-11 | 726 | 998 | 937 | 1019 | 51.28 | 3731.28 | 3582.75 | 148.53 | 3737 | 4.893 | 0.74439 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2020-01-12 | 625 | 861 | 807 | 866 | 42.46 | 3201.46 | 3093.75 | 107.71 | 3207 | 4.614 | 0.67744 | Module Cleaning has been done in Row-D,E,F, Inverter No-4, total module cleaning-504. Grid Failure from-11:55 to 12:07 and 12:43 to 12:46. |  | 504 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2020-01-13 | 423 | 535 | 514 | 560 | 22.42 | 2054.42 | 1942.5 | 111.92 | 2059 | 2.673 | 0.75078 | Today we are change ++tive string DC 6 Sqmm cable (25m) in string no-7 of AJB No: 107 in due to underground fault(Cable Puncture) and fault observed in 14 Dec 2019.Module Cleaning has been done in Row-G,H, Inverter No-4, total module cleaning-396. Grid Failure from-09:30 to 09:33. |  | 396 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2020-01-14 | 762 | 1083 | 1008 | 1139 | 58.14 | 4050.14 | 3915 | 135.14 | 4056 | 5.702 | 0.6933 | Grid Failure from-11:02 to 11:11. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2020-01-15 | 786 | 1104 | 1028 | 1154 | 59.49 | 4131.49 | 3975 | 156.49 | 4137 | 5.679 | 0.71001 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2020-01-16 | 721 | 993 | 943 | 1023 | 50.88 | 3730.88 | 3582 | 148.88 | 3736 | 5.216 | 0.69811 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4,and Tracker, total module cleaning-852. Grid Failure from-10:30 to 10:49. |  | 852 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2020-01-17 | 625 | 847 | 816 | 852 | 40.91 | 3180.91 | 3058 | 122.91 | 3187 | 4.29 | 0.72406 | Module Cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No-3, total module cleaning-840. |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2020-01-18 | 720 | 1013 | 988 | 1039 | 52.12 | 3812.12 | 3672 | 140.12 | 3818 | 5.165 | 0.72047 | Module Cleaning has been done in Row-J,K,L,M, Inverter No-2 and 3, total module cleaning-1071. |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2020-01-19 | 766 | 1098 | 1038 | 1113 | 57.5 | 4072.5 | 3927 | 145.5 | 4078 | 5.389 | 0.73755 | Module Cleaning has been done in Row-E,F,G,H,I Inverter No-1 & 2, total module cleaning-1050. |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2020-01-20 | 847 | 1210 | 1145 | 1245 | 64.89 | 4511.89 | 4345 | 166.89 | 4517 | 5.962 | 0.73843 | Module Cleaning has been done in Row-A,B,C,D and A,B, Inverter No-1 & 4, total module cleaning-498. Today we are Remove 500ml Oil in all Transformer for Oil Testing Purpose. |  | 498 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2020-01-21 | 812 | 1149 | 1078 | 1185 | 61.44 | 4285.44 | 4132 | 153.44 | 4291 | 5.784 | 0.72307 | Module Cleaning has been done in Row-C,D,E,F. Inverter No-4 , total module cleaning-630+M228 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2020-01-22 | 806 | 1130 | 1069 | 1179 | 59.77 | 4243.77 | 4080 | 163.77 | 4849 | 5.665 | 0.83427 | Module Cleaning has been done in Row-G,H. Inverter No-4 , total module cleaning-396.today we are again remove 200 ml oil in all trasformer for oil testing peropse. |  | 396 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2020-01-23 | 791 | 1109 | 1048 | 1154 | 57.96 | 4159.96 | 4017 | 142.96 | 4165 | 5.498 | 0.73835 | Module Cleaning has been done in Row-S,T and I,J,K,L . Inverter No-3 and 4,and Tracker, total module cleaning-810. Grid Failure from-16:11 to 16:13. |  | 810 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2020-01-24 | 832 | 1184 | 1134 | 1266 | 65.07 | 4481.07 | 4322 | 159.07 | 4487 | 5.931 | 0.73736 | Module Cleaning has been done in Row-N,O,P,Q,R, Inverter No-3 total module cleaning-756 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2020-01-25 | 594 | 811 | 781 | 861 | 39.89 | 3086.89 | 2964.75 | 122.14 | 3092 | 4.041 | 0.74577 | Cloudy Day,Today we are install 24watt solar street light (2 Nos)in Campus Boundary of Solar plant.Grid Failure from 17:08 to 17:15. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
25 | 2020-01-26 | 797 | 1114 | 1084 | 1195 | 61.03 | 4251.03 | 4087 | 164.03 | 4257 | 5.662 | 0.7328 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2020-01-27 | 670 | 918 | 887 | 958 | 47.25 | 3480.25 | 3341.25 | 139 | 3486 | 4.717 | 0.7203 | Module Cleaning has been done in Row-L,M, Inverter No-2,and 3 total module cleaning-504, Cloudy Day |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
27 | 2020-01-28 | 685 | 947 | 907 | 998 | 49.11 | 3586.11 | 3456 | 130.11 | 3592 | 4.775 | 0.73319 | Today early mornig 2:45am UGVCL staff Came and Disconnect Power Supply of 1MW Solar Power Plant and remove UGVCL energy meter and after we are taken temporary Power Suppy by Maruti Excellance and connect with ACDB.(3-Phase A.C).Module Cleaning has been done in Row-I,J,K, Inverter No-2 total module cleaning-840, Cloudy Day |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
28 | 2020-01-29 | 817 | 1169 | 1094 | 1159 | 60.76 | 4299.76 | 4144 | 155.76 | 4305 | 5.789 | 0.72481 | Module Cleaning has been done in Row-H,G,F,E,D,C inverter no 1 total module cleaning-1008, Cloudy Day |  | 1008 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
29 | 2020-01-30 | 857 | 1190 | 1114 | 1204 | 63.31 | 4428.31 | 4267 | 161.31 | 4444 | 6 | 0.7219 | Module Cleaning has been done in Row-A,B & A,B,C,D,E,F,Inverter no 1&4 total module cleaning-897 |  | 897 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2020-01-31 | 826 | 1154 | 1079 | 1195 | 60.51 | 4314.51 | 4191 | 123.51 | 4319 | 5.864 | 0.71786 | Module Cleaning has been done in Row-G,H,I,J,K, Inverter No-4, total module cleaning-936. Grid Failure from-01:00am to 08:10am. |  | 936 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2020-02-01 | 888 | 1235 | 1159 | 1316 | 65.75 | 4663.75 | 4483.5 | 180.25 | 4669 | 6.207 | 0.73315 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2020-02-02 | 857 | 1189 | 1124 | 1259 | 64.43 | 4493.43 | 4341 | 152.43 | 4499 | 5.924 | 0.74021 | Module Cleaning has been done in Row-O,P,Q,R,S,T & L, and Tracker, Inverter No-3&4, total module cleaning-627. |  | 627 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2020-02-03 | 791 | 1099 | 1068 | 1150 | 57.44 | 4165.44 | 4016 | 149.44 | 4171 | 5.51 | 0.7378 | Module Cleaning has been done in Row-K,L,M,N,O,Inverter No-2&3, total module cleaning-1103 |  | 1103 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2020-02-04 | 842 | 1195 | 1149 | 1219 | 64.06 | 4469.06 | 4307.25 | 161.81 | 4475 | 5.954 | 0.73255 | Module Cleaning has been done in Row-J,K,Inverter No-2, total module cleaning-367 |  | 367 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2020-02-05 | 806 | 1144 | 1069 | 1145 | 60.11 | 4224.11 | 4068 | 156.11 | 4230 | 5.751 | 0.71689 | Module Cleaning has been done in Row-D,E,F,G,H,I, Inverter No-1 & 2, total module cleaning-1176.Grid failure from 11:00 to 11:13. |  | 1176 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2020-02-06 | 857 | 1194 | 1134 | 1209 | 61.79 | 4455.79 | 4299 | 156.79 | 4461 | 6.011 | 0.72333 | Module Cleaning has been done in Row-A,B,C and A,B,C,D Inverter No-1 & 4, total module cleaning-642 |  | 642 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2020-02-07 | 837 | 1155 | 1099 | 1175 | 58.68 | 4324.68 | 4173.75 | 150.93 | 4330 | 5.746 | 0.73447 | Module Cleaning has been done in Row-E,F,G,H,I Inverter No-4, total module cleaning-954.Today Preventive maintenance of Inverter No-1 has been done. |  | 954 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2020-02-08 | 881 | 1240 | 1169 | 1270 | 64.29 | 4624.29 | 4461 | 163.29 | 4630 | 6.171 | 0.73127 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2020-02-09 | 882 | 1229 | 1165 | 1270 | 64.23 | 4610.23 | 4452 | 158.23 | 4616 | 6.155 | 0.73095 | Module Cleaning has been done in Row-J,K,L, and Tracker, Inverter No-4, total module cleaning-528. |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2020-02-10 | 857 | 1195 | 1139 | 1250 | 63.19 | 4504.19 | 4343 | 161.19 | 4510 | 6.016 | 0.73067 | Module Cleaning has been done in Row-O,P,Q,R,S,T, Inverter No-3, total module cleaning-630 |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2020-02-11 | 812 | 1119 | 1093 | 1174 | 57.69 | 4255.69 | 4103 | 152.69 | 4261 | 5.728 | 0.72504 | Module Cleaning has been done in Row-J,K,L,M,N, Inverter No-2 & 3, total module cleaning-1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2020-02-12 | 827 | 1159 | 1104 | 1190 | 58.48 | 4338.48 | 4074.75 | 263.73 | 4344 | 5.872 | 0.72104 | Module Cleaning has been done in Row-D,E,F,G,H,I, Inverter No-1 & 2, total module cleaning-1176. Grid Failure from-17:22 to 17:30. |  | 1176 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2020-02-13 | 846 | 1160 | 1099 | 1184 | 57.92 | 4346.92 | 4201.5 | 145.42 | 4352 | 5.895 | 0.71954 | Module Cleaning has been done in Row-A,B,C and A,B,C,D,E, Inverter No-1 & 4, total module cleaning-804.Grid Failure IACE from -08:38 to 09:00. |  | 804 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2020-02-14 | 852 | 1168 | 1114 | 1210 | 58.97 | 4402.97 | 4251.75 | 151.22 | 4408 | 5.976 | 0.71893 | Module Cleaning has been done in Row-F,G, Inverter No 4, total module cleaning-396.Grid Failure from-16:26 to 16:31. Today we are install new communication card in string inveter no-07(2100570073) for tracker. |  | 396 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2020-02-15 | 842 | 1150 | 1099 | 1210 | 55.62 | 4356.62 | 4192.5 | 164.12 | 4362 | 5.991 | 0.70964 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2020-02-16 | 816 | 1109 | 1053 | 1154 | 56.08 | 4188.08 | 4050 | 138.08 | 4194 | 5.723 | 0.71426 | Module Cleaning has been done in Row-G,H,I, Inverter No 4, total module cleaning- 594. |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2020-02-17 | 852 | 1154 | 1114 | 1219 | 60.46 | 4399.46 | 4238.25 | 161.21 | 4405 | 6.105 | 0.70326 | Module Cleaning has been done in Row-J,K,L, and Tracker Inverter No 4, total module cleaning- 528.Grid Failure from-17:01 to 17:20. |  | 528 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2020-02-18 | 857 | 1179 | 1129 | 1261 | 64.03 | 4490.03 | 4338 | 152.03 | 4496 | 6.236 | 0.7027 | Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No 03, total module cleaning- 441 |  | 441 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2020-02-19 | 640 | 847 | 837 | 861 | 42.45 | 3227.45 | 3108 | 119.45 | 3233 | 4.81 | 0.65511 | Module Cleaning has been done in Row-O,N,M,Inverter No 03, total module cleaning- 651.Grid Failure from-16:27 to 18:17. Today we are repleced the d.c 12 amp fuselink of the string no 09++tive line ajb no 103 of the inverter no 04 during the time of (16:50 to 16:55) .Today Came Arifbhai from Abb.Ltd for Checked all Parameter of Inverter. |  | 651 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2020-02-20 | 882 | 1225 | 1194 | 1291 | 66.4 | 4658.4 | 4487 | 171.4 | 4664 | 6.386 | 0.71184 | Module Cleaning has been done in Row-M,N,Inverter No 03, total module cleaning- 462 |  | 462 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2020-02-21 | 822 | 1164 | 1104 | 1184 | 58.27 | 4332.27 | 4185 | 147.27 | 4338 | 5.802 | 0.72873 | Module Cleaning has been done in Row-J,K,L,Inverter No 02, total module cleaning- 819. |  | 819 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2020-02-22 | 902 | 1255 | 1174 | 1260 | 64.31 | 4655.31 | 4476.75 | 178.56 | 4661 | 6.084 | 0.74669 | Module Cleaning has been done in Row-H,I,Inverter No 01 and 02, total module cleaning-504. |  | 504 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2020-02-23 | 832 | 1109 | 1044 | 1104 | 54.73 | 4143.73 | 4005 | 138.73 | 4149 | 5.54 | 0.72994 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,Inverter No 01, total module cleaning-882.Cloudy day |  | 882 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
54 | 2020-02-24 | 877 | 1174 | 1098 | 1205 | 57.67 | 4411.67 | 4247.25 | 164.42 | 4417 | 5.898 | 0.72992 | Module Cleaning has been done in Row-A,B,C,D,E,F,Inverter No 04, total module cleaning-792.Cloudy day |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
55 | 2020-02-25 | 846 | 1145 | 1079 | 1199 | 57.18 | 4326.18 | 4187.25 | 138.93 | 4332 | 5.843 | 0.72261 | Module Cleaning has been done in Row-G,H,I,Inverter No 04, total module cleaning-594.Cloudy day |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
56 | 2020-02-26 | 786 | 1058 | 988 | 1114 | 51.62 | 3997.62 | 3854 | 143.62 | 4004 | 5.536 | 0.70494 | Module Cleaning has been done in Row-J,K,L, and tracker , Inverter No 04, total module cleaning-528.Cloudy day,Grid Failure from 14:44 to 14:47. |  | 528 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
57 | 2020-02-27 | 812 | 1099 | 1053 | 1190 | 54.51 | 4208.51 | 4053.75 | 154.76 | 4214 | 5.757 | 0.71343 | Module Cleaning has been done in Row-P,Q,R,S,T, Inverter No -03, total module cleaning-441. Today we are install new tracker controller with display unit in tracker no-3. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2020-02-28 | 706 | 927 | 933 | 993 | 48.62 | 3607.62 | 3477.75 | 129.87 | 3613 | 4.737 | 0.74339 | Module Cleaning has been done in Row-L,M,N,Inverter No 02&03, total module cleaning-714.Cloudy day |  | 714 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
59 | 2020-02-29 | 811 | 1104 | 1088 | 1154 | 61.16 | 4218.16 | 4065 | 153.16 | 4244 | 5.645 | 0.73276 | Today has been done Air filter paper clean of all inverter.(Cabinet door Filter) |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2020-03-01 | 827 | 1159 | 1119 | 1199 | 65.09 | 4369.09 | 4219.5 | 149.59 | 4374 | 5.923 | 0.71976 | Module Cleaning has been done in Row-J,K,Inverter No 02, total module cleaning-567 |  | 567 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 2020-03-02 | 806 | 1119 | 1049 | 1104 | 60.54 | 4138.54 | 3992.25 | 146.29 | 4144 | 5.626 | 0.71791 | Module Cleaning has been done in Row-E,F,G,H,I, Inverter No 1& 02, total module cleaning- 1050.Grid Failure from-14:49 to 14:54. |  | 1050 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2020-03-03 | 786 | 1039 | 967 | 1023 | 54.08 | 3869.08 | 3736.05 | 133.03 | 3875 | 5.377 | 0.7024 | Module Cleaning has been done in Row-A,B,C,D,&A,B,C,D,E,,Inverter No 01&04, total module cleaning-930 |  | 930 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2020-03-04 | 893 | 1209 | 1129 | 1265 | 65.34 | 4561.34 | 4406.25 | 155.09 | 4567 | 6.251 | 0.71209 | Grid Failure from-18:04 to 18:10. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2020-03-05 | 816 | 1023 | 1024 | 1160 | 56.97 | 4079.97 | 3933 | 146.97 | 4085 | 5.694 | 0.69924 | Today we are change and install new ++tive and --tive string DC 6 Sqmm cable (234meter) in string no- 1,2,3 of AJB No: 110 in Inverter No-2 due to underground fault(Cable Puncture).Cloudy Day. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
65 | 2020-03-06 | 822 | 1099 | 1058 | 1199 | 62.62 | 4240.62 | 4069.5 | 171.12 | 4246 | 5.894 | 0.70214 | Grid Failure IACE side due to VCB trip from-08:30 to 09:05 and 13:01 to 13:14.Cloudy Day. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
66 | 2020-03-07 | 953 | 1331 | 1270 | 1432 | 79.74 | 5065.74 | 4895.25 | 170.49 | 5071 | 6.868 | 0.71964 | Today came Powertech Engineers pvt.ltd for Oil filteration and testing of all 5 transformer, BDV test has been done of oil in all transformer. |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2020-03-08 | 509 | 685 | 655 | 720 | 39.51 | 2608.51 | 2532 | 76.51 | 2614 | 3.518 | 0.72421 | Grid failure from 9:38 to 13:38 because IACE side Grid failure due to VCB Trip.Module Cleaning has been done in Row-F,G,H, Inverter No 04, total module cleaning- 594. |  | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2020-03-09 | 927 | 1265 | 1210 | 1381 | 71.53 | 4854.53 | 4692.75 | 161.78 | 4855 | 6.508 | 0.7271 | Module Cleaning has been done in Row-I,J,K,L, and tracker , Inverter No 04, total module cleaning-726. |  | 726 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2020-03-10 | 897 | 1215 | 1169 | 1316 | 66.36 | 4663.36 | 4496.25 | 167.11 | 4669 | 6.319 | 0.72016 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2020-03-11 | 792 | 1058 | 1034 | 1164 | 62.4 | 4110.4 | 3957.75 | 152.65 | 4111 | 5.44 | 0.73655 | Module Cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No -03, total module cleaning-840.Cloudy Day |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
71 | 2020-03-12 | 967 | 1336 | 1325 | 1457 | 88.69 | 5173.69 | 4993.5 | 180.19 | 5174 | 7.004 | 0.72 | Module Cleaning has been done in Row-J,K,L,M, Inverter No -02 and 03, total module cleaning-1071.IACE side Grid failure from 15:40 to 15:48. |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2020-03-13 | 867 | 1200 | 1149 | 1250 | 72.49 | 4538.49 | 4381.5 | 156.99 | 4539 | 6.02 | 0.73488 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I ,Inverter No- 1&2, total module cleaning-1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2020-03-14 | 968 | 1345 | 1291 | 1411 | 86 | 5101 | 4926 | 175 | 5101 | 6.989 | 0.71137 | Grid Failure IACE side due to VCB trip from-11:41 to 12:07. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2020-03-15 | 705 | 973 | 912 | 978 | 59.34 | 3627.34 | 3489 | 138.34 | 3628 | 6.28 | 0.56307 | Today Replaced the D.C.12 Amp fuse link of the string-03 --tive line in AJB-104 of The Inverter-4 during the period of 8:25 to 08:30, & Grid Failure IACE side due to VCB trip from-09:07 to 09:44 and 13:02 to 14:25(11KV Side). Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-4, total module cleaning-594, & Cloudy Day. |  | 594 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
75 | 2020-03-16 | 575 | 766 | 726 | 801 | 50.56 | 2918.56 | 2790 | 128.56 | 2919 | 6.776 | 0.41987 | Module Cleaning has been done in Row-F,G,H,I, Inverter No -4 total module cleaning-792.Grid failure from 11:19 to 14:25(11KV Side). |  | 792 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2020-03-17 | 922 | 1291 | 1230 | 1407 | 80.91 | 4930.91 | 4753.5 | 177.41 | 4931 | 6.709 | 0.71636 | Module Cleaning has been done in Row-J,K,L, and trackers, Inverter No 4, total module cleaning-528. |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2020-03-18 | 887 | 1229 | 1184 | 1350 | 69.45 | 4719.45 | 4568.25 | 151.2 | 4725 | 6.488 | 0.70981 | Today we are installed New LBS (650A) & 63KVA distribution transformer (11/.433KV) and get new supply in Plant(60 meter installed new 70Sq mm cable cable in 415V (LT) side).We are install new Analog Volt meter 415/110V (make: Rishab) in LT panel and Module Cleaning has been done in Row-P,Q,R,S,T , Inverter No 3, total module cleaning-441. |  | 441 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2020-03-19 | 792 | 1089 | 1059 | 1170 | 66.92 | 4176.92 | 4008.75 | 168.17 | 4177 | 6.205 | 0.65611 | Module Cleaning has been done in Row-N,O , Inverter No 3, total module cleaning-399.Today Came UGVCL Line man in evening time due to "B" Phase AB Switch are Sparking, So G.O.D Switch are disconnected for UGVCL Pole and add new link and joint the cable in during 16:14 to 16:55 |  | 399 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2020-03-20 | 937 | 1296 | 1270 | 1431 | 84.33 | 5018.33 | 4773 | 245.33 | 5019 | 6.746 | 0.72514 | Module Cleaning has been done in Row-K,L,M, Inverter No 2&3, total module cleaning-777 |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2020-03-21 | 872 | 1219 | 1184 | 1331 | 65.41 | 4671.41 | 4464 | 207.41 | 4677 | 6.434 | 0.7085 | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2020-03-22 | 822 | 1149 | 1114 | 1245 | 58.41 | 4388.41 | 4199.25 | 189.16 | 4394 | 6.097 | 0.70242 | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2020-03-23 | 801 | 1089 | 1054 | 1179 | 56.89 | 4179.89 | 3993 | 186.89 | 4185 | 5.777 | 0.70607 | Cloudy Day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
83 | 2020-03-24 | 852 | 1170 | 1134 | 1275 | 60.94 | 4491.94 | 4295.25 | 196.69 | 4500 | 6.152 | 0.71293 | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2020-03-25 | 469 | 584 | 569 | 615 | 23.8 | 2260.8 | 2085 | 175.8 | 2266 | 2.928 | 0.7543 | Fully Cloudy Day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
85 | 2020-03-26 | 594 | 771 | 741 | 822 | 31.68 | 2959.68 | 2805 | 154.68 | 2965 |  |  | Fully Cloudy Day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
86 | 2020-03-27 | 741 | 978 | 937 | 1104 | 0 | 3760 | 3557.25 | 202.75 | 3765 |  |  | Today we are found Trackers 'ACDB' fire due to yesterday night time heavy rain with air flow so whole mcb burn in 'ACDB' box because water spread in Box ,So we are disconnect All string Inverter, and Grid failure from 12:55 to 13:05.Fully Cloudy Day and No Module cleaning (No Man power) |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
87 | 2020-03-28 | 963 | 1340 | 1286 | 1466 | 0 | 5055 | 4830.75 | 224.25 | 5060 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2020-03-29 | 957 | 1346 | 1290 | 1477 | 0 | 5070 | 4860.75 | 209.25 | 5075 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2020-03-30 | 918 | 1301 | 1255 | 1411 | 0 | 4885 | 4686.75 | 198.25 | 4890 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2020-03-31 | 912 | 1280 | 1230 | 1391 | 0 | 4813 | 4599.75 | 213.25 | 4818 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2020-04-01 | 913 | 1275 | 1225 | 1392 | 34.37 | 4839.37 | 4628.25 | 211.12 | 4845 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2020-04-02 | 922 | 1305 | 1260 | 1421 | 82.77 | 4990.77 | 4767 | 223.77 | 4991 |  |  | Today we are changed burn MCB and install new MCB connection of "ACDB" in trackers.today we are give water in all Earth Pit.No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2020-04-03 | 933 | 1301 | 1245 | 1426 | 83.18 | 4988.18 | 4774.5 | 213.68 | 4989 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2020-04-04 | 907 | 1275 | 1224 | 1381 | 82.28 | 4869.28 | 4664.25 | 205.03 | 4870 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2020-04-05 | 872 | 1240 | 1200 | 1336 | 79.41 | 4727.41 | 4521 | 206.41 | 4728 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2020-04-06 | 866 | 1220 | 1169 | 1310 | 77.34 | 4642.34 | 4443.75 | 198.59 | 4643 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2020-04-07 | 882 | 1225 | 1180 | 1341 | 77.69 | 4705.69 | 4493.25 | 212.44 | 4706 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2020-04-08 | 877 | 1209 | 1164 | 1316 | 74.43 | 4640.43 | 4432 | 208.43 | 4641 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2020-04-09 | 862 | 1190 | 1149 | 1295 | 73.41 | 4569.41 | 4371 | 198.41 | 4570 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2020-04-10 | 868 | 1199 | 1154 | 1285 | 75.58 | 4581.58 | 4374 | 207.58 | 4582 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2020-04-11 | 861 | 1190 | 1150 | 1280 | 74.06 | 4555.06 | 4333.5 | 221.56 | 4556 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2020-04-12 | 847 | 1194 | 1144 | 1260 | 75.6 | 4520.6 | 4317.75 | 202.85 | 4521 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2020-04-13 | 867 | 1190 | 1149 | 1271 | 74.96 | 4551.96 | 4347 | 204.96 | 4552 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2020-04-14 | 852 | 1179 | 1134 | 1260 | 74.68 | 4499.68 | 4292.25 | 207.43 | 4500 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2020-04-15 | 831 | 1114 | 1079 | 1199 | 69.17 | 4292.17 | 4075.5 | 216.67 | 4293 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2020-04-16 | 840 | 1127 | 1101 | 1221 | 70.17 | 4359.17 | 4139.25 | 219.92 | 4360 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2020-04-17 | 784 | 1040 | 985 | 1093 | 58.66 | 3960.66 | 3776.25 | 184.41 | 3961 |  |  | Cloudy day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
108 | 2020-04-18 | 841 | 1125 | 1084 | 1189 | 68.18 | 4307.18 | 4102.5 | 204.68 | 4308 |  |  | Cloudy day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
109 | 2020-04-19 | 852 | 1164 | 1124 | 1270 | 70.64 | 4480.64 | 4265.25 | 215.39 | 4481 |  |  | Cloudy day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
110 | 2020-04-20 | 877 | 1200 | 1154 | 1306 | 78.13 | 4615.13 | 4404 | 211.13 | 4616 |  |  | Cloudy day and No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0
111 | 2020-04-21 | 837 | 1134 | 1094 | 1255 | 72.48 | 4392.48 | 4178.25 | 214.23 | 4393 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2020-04-22 | 841 | 1134 | 1094 | 1250 | 70.25 | 4389.25 | 4177.5 | 211.75 | 4390 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2020-04-23 | 877 | 1184 | 1144 | 1320 | 77.12 | 4602.12 | 4378.5 | 223.62 | 4603 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2020-04-24 | 872 | 1200 | 1159 | 1346 | 78.54 | 4655.54 | 4430.25 | 225.29 | 4656 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2020-04-25 | 872 | 1179 | 1129 | 1305 | 74.42 | 4559.42 | 4344.75 | 214.67 | 4560 |  |  | Grid failure from 17:17 to 17:37.Today Replaced the D.C.12 Amp fuse link of the string-03 --tive in AJB-102 of The Inverter-4 during the period of 18:30 to 18:35.No Module cleaning (No Man power) |  |  | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
116 | 2020-04-26 | 852 | 1159 | 1119 | 1306 | 74.14 | 4510.14 | 4287 | 223.14 | 4511 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2020-04-27 | 837 | 1149 | 1104 | 1295 | 74.07 | 4459.07 | 4237.5 | 221.57 | 4460 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2020-04-28 | 842 | 1165 | 1124 | 1306 | 75.39 | 4512.39 | 4299.75 | 212.64 | 4513 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2020-04-29 | 831 | 1144 | 1108 | 1290 | 73.81 | 4446.81 | 4227.75 | 219.06 | 4447 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2020-04-30 | 801 | 1104 | 1064 | 1225 | 71.02 | 4265.02 | 4056 | 209.02 | 4266 |  |  | Today has been done Air filter paper clean of all inverter.(Cabinet door Filter).No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2020-05-01 | 827 | 1123 | 1089 | 1260 | 70.01 | 4369.01 | 4153.5 | 215.51 | 4670 |  |  | Today we are change Brether of all Transformer(5 Nos).No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2020-05-02 | 862 | 1180 | 1139 | 1335 | 78.05 | 4594.05 | 4376.25 | 217.8 | 4595 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 2020-05-03 | 836 | 1139 | 1093 | 1291 | 71.63 | 4430.63 | 4210.5 | 220.13 | 4431 |  |  | No Module cleaning (No Man power) |  |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2020-05-04 | 847 | 1149 | 1109 | 1325 | 74.17 | 4504.17 | 4287 | 217.17 | 4505 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F Inverter No 4, total module cleaning-792. |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2020-05-05 | 792 | 1079 | 1039 | 1291 | 66.76 | 4267.76 | 4059.75 | 208.01 | 4268 |  |  | Module Cleaning has been done in Row- G,H,I,J,K,L and Trackers Inverter No 4, total module cleaning-1122. |  | 1122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2020-05-06 | 796 | 1099 | 1109 | 1335 | 70.92 | 4409.92 | 4185.75 | 224.17 | 4410 |  |  | Module Cleaning has been done in Row- N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-840. |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2020-05-07 | 801 | 1194 | 1164 | 1346 | 74.83 | 4579.83 | 4359.75 | 220.08 | 4580 |  |  | Module Cleaning has been done in Row- K,L,M, Inverter No 2 and 3, total module cleaning-777. |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2020-05-08 | 822 | 1215 | 1174 | 1348 | 76.24 | 4635.24 | 4408.5 | 226.74 | 4636 |  |  | Module Cleaning has been done in Row- ,I,J, Inverter No 1&2, total module cleaning-567. |  | 567 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2020-05-09 | 851 | 1222 | 1159 | 1340 | 76.19 | 4648.19 | 4428 | 220.19 | 4649 |  |  | Module Cleaning has been done in Row- ,F,G,H, Inverter No 1 , total module cleaning-630. |  | 630 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2020-05-10 | 882 | 1224 | 1160 | 1346 | 77.61 | 4689.61 | 4469.25 | 220.36 | 4690 |  |  | Module Cleaning has been done in Row- ,A,B,C,D,E,& A,B,C,D,E, Inverter No 1&2 , total module cleaning-1464. |  | 1464 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2020-05-11 | 873 | 1185 | 1134 | 1356 | 75.29 | 4623.29 | 4405.5 | 217.79 | 4624 |  |  | Module Cleaning has been done in Row- F,G,H,I,J,K,L, and Trackers Inverter No 4, total module cleaning-1320. |  | 1320 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2020-05-12 | 846 | 1174 | 1134 | 1316 | 76.26 | 4546.26 | 4334.25 | 212.01 | 4547 |  |  | Module Cleaning has been done in Row- N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-840. |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2020-05-13 | 868 | 1211 | 1159 | 1340 | 78.06 | 4656.06 | 4419 | 237.06 | 4657 |  |  | Module Cleaning has been done in Row-I,J,K,L,M, Inverter No- 2&3, total module cleaning-1344. |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2020-05-14 | 882 | 1213 | 1159 | 1341 | 78.6 | 4673.6 | 4455.75 | 217.85 | 4674 |  |  | Grid failure from-16:55 to 17:04 and 18:00 to 18:06, & Module Cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No- 1, total module cleaning-1113. |  | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2020-05-15 | 877 | 1195 | 1149 | 1351 | 78.47 | 4650.47 | 4414.5 | 235.97 | 4651 |  |  | Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2020-05-16 | 857 | 1174 | 1135 | 1320 | 74.69 | 4560.69 | 4347.75 | 212.94 | 4561 |  |  | Module Cleaning has been done in Row- H,I,J,K,L & Inverter No- 4 and Tracker , total module cleaning-924 |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2020-05-17 | 892 | 1230 | 1169 | 1356 | 79.1 | 4726.1 | 4480.5 | 245.6 | 4727 |  |  | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T & Inverter No-3 and Tracker , total module cleaning-1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2020-05-18 | 888 | 1205 | 1159 | 1341 | 75.37 | 4668.37 | 4424.25 | 244.12 | 4669 |  |  | Module Cleaning has been done in Row-I,J,K,L ,Inverter No-2 total module cleaning-1092.Today we are repleced the d.c 12 amp fuse link of the string no 03 --tive line AJB No-102 of the inverter No-04 during the time of 17:40 to 17:45. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
139 | 2020-05-19 | 884 | 1228 | 1174 | 1406 | 80.59 | 4772.59 | 4539.75 | 232.84 | 4773 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113. |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2020-05-20 | 880 | 1207 | 1175 | 1391 | 79.46 | 4732.46 | 4511.25 | 221.21 | 4733 |  |  |  |  | 990 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2020-05-21 | 872 | 1219 | 1179 | 1341 | 79.5 | 4690.5 | 4458.75 | 231.75 | 4691 |  |  | Today we are repleced the d.c 12 amp fuse link of the string no 08 ++tive line AJB No-102 of the inverter No-04 during the time of 17:45 to 17:50.Module Cleaning has been done in Row- H,I,J,K,L & Trackers Inverter No- 4 and, total module cleaning-924 |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
142 | 2020-05-22 | 882 | 1215 | 1170 | 1366 | 79.38 | 4712.38 | 4497 | 215.38 | 4713 |  |  | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2020-05-23 | 887 | 1214 | 1169 | 1391 | 79.14 | 4740.14 | 4499.25 | 240.89 | 4741 |  |  | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2020-05-24 | 881 | 1220 | 1179 | 1406 | 81.76 | 4767.76 | 4533.75 | 234.01 | 4767 |  |  | Today has been done Air filter paper clean of all inverter.(Cabinet door Filter).Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113. |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2020-05-25 | 641 | 892 | 862 | 1023 | 82.48 | 3500.48 | 3308.25 | 192.23 | 4767 |  |  | Today we are replaced 125A Change over switch of Incoming line 415V during 10:34 to 13:00..Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2020-05-26 | 766 | 1053 | 1018 | 1205 | 71.18 | 4113.18 | 3897.75 | 215.43 | 4114 |  |  | Grid failure from 7:32 to 7:54 and 12:52 to 13:51.Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924 |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2020-05-27 | 358 | 46 | 449 | 534 | 34.81 | 1421.81 | 1307.25 | 114.56 | 1308 |  |  | Grid failure from 7:38 to 13:30. Today grid failure after Inverter No-2 ABB 250kw failure due to Err. D.C Bracker trip (8188) replaced the bracker switch handle after started inverter-18:00. (During the Brack down time 13:50 to 18:00) and today we are changed AB switch of B-phase in Solar H-pole side due to grid failure. Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092. |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2020-05-28 | 862 | 1154 | 1114 | 1326 | 74.42 | 4530.42 | 4290.75 | 239.67 | 4531 |  |  | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2020-05-29 | 826 | 1094 | 1053 | 1275 | 65.53 | 4313.53 | 4095 | 218.53 | 4314 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113. |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2020-05-30 | 827 | 1094 | 1054 | 1285 | 67.36 | 4327.36 | 4121.25 | 206.11 | 4328 |  |  | Module Cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990, and Cloudy day |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
151 | 2020-05-31 | 821 | 1108 | 1093 | 1275 | 69.63 | 4366.63 | 4139.25 | 227.38 | 4367 |  |  | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
152 | 2020-06-01 | 792 | 1084 | 1039 | 1216 | 67.06 | 4198.06 | 3976.5 | 221.56 | 4199 |  |  | Grid failure from 7:38 to 13:30. Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
153 | 2020-06-02 | 841 | 1119 | 1078 | 1255 | 9.77 | 4302.77 | 4130.25 | 172.52 | 4294 |  |  | Today evening time tracker postion automatically change so we are change and replace MCB(2 Nos - C32A TP & 3 Nos 2DP C16A ) in ACDB Tracker Box after manually strated 17:45, Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092 and Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
154 | 2020-06-03 | 666 | 862 | 822 | 963 | 3.5 | 3316.5 | 3167.25 | 149.25 | 3317 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G,H, Inverter No- 1, total module cleaning-1113.Grid failure from 7:30 to 7:45 and 12:06 to 12:15 & 13.44 to 13:47.Cloudy day |  | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
155 | 2020-06-04 | 776 | 1023 | 993 | 1174 | 54.64 | 4020.64 | 3816.75 | 203.89 | 4021 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990.Grid failure from 07:27 to 07:38, Cloudy day. |  | 990 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
156 | 2020-06-05 | 811 | 1079 | 1043 | 1240 | 65.07 | 4238.07 | 4033.5 | 204.57 | 4239 |  |  | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
157 | 2020-06-06 | 782 | 1048 | 1003 | 1205 | 63.23 | 4101.23 | 3839.25 | 261.98 | 4102 |  |  | Grid failure from 8:37 to 8:45 and 12:42 to 12:50. Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
158 | 2020-06-07 | 690 | 887 | 867 | 1013 | 48.52 | 3505.52 | 3375 | 130.52 | 3506 |  |  | Cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
159 | 2020-06-08 | 660 | 893 | 862 | 1008 | 51.39 | 3474.39 | 3258.75 | 215.64 | 3475 |  |  | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092.Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
160 | 2020-06-09 | 721 | 962 | 917 | 1093 | 65.33 | 3758.33 | 3578.25 | 180.08 | 3759 |  |  | Module cleaning by rain,Grid failure from 10:52 to 11:03,11:04 to 11:15, 11:30 to 11:45 , 11:48 to 11:59 and 12:03 to 12:26. |  |  | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2020-06-10 | 736 | 963 | 938 | 1110 | 48.19 | 3795.19 | 3553.5 | 241.69 | 3796 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2020-01-06 | 695 | 877 | 846 | 1002 | 45.25 | 3465.25 | 3291.75 | 173.5 | 3466 |  |  | Module cleaning by rain. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2020-01-12 | 787 | 1048 | 1014 | 1215 | 57.51 | 4121.51 | 3909.75 | 211.76 | 4122 |  |  | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day,Grid failure from 17:10 to 17:40. |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
164 | 2020-06-13 | 665 | 857 | 831 | 973 | 42.35 | 3368.35 | 3184.5 | 183.85 | 3369 |  |  | Module cleaning by rain. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2020-06-14 | 630 | 812 | 787 | 927 | 32.2 | 3188.2 | 3036 | 152.2 | 3189 |  |  | Module clean by rain.Grid failure from 7:30 to 8:36. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2020-06-15 | 662 | 977 | 942 | 1124 | 39.19 | 3744.19 | 3609 | 135.19 | 3745 |  |  | Module clean by rain.Grid failure from 9:17 to 9:25. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2020-06-16 | 664 | 968 | 938 | 1109 | 37.32 | 3716.32 | 3609 | 107.32 | 3717 |  |  | Module cleaning by rain. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2020-06-17 | 746 | 978 | 947 | 1109 | 37.53 | 3817.53 | 3597 | 220.53 | 3818 |  |  | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
169 | 2020-06-18 | 771 | 1013 | 978 | 1164 | 42.07 | 3968.07 | 3765.75 | 202.32 | 3969 |  |  | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092.Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
170 | 2020-06-19 | 882 | 1079 | 1033 | 1270 | 46.16 | 4310.16 | 4035.75 | 274.41 | 4311 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113.Cloudy day. |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
171 | 2020-06-20 | 827 | 1094 | 1069 | 1286 | 48.99 | 4324.99 | 4112.25 | 212.74 | 4325 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990.Today we are replaced silica gel in Transformer No-2.(300KVA)Cloudy day. |  | 990 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0
172 | 2020-06-21 | 735 | 957 | 927 | 1093 | 38.43 | 3750.43 | 3549.75 | 200.68 | 3751 |  |  | Module Cleaning has been done in Row- H,I,J,K,L & Tracker, Inverter No- 4, total module cleaning-924, and Cloudy day |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
173 | 2020-06-22 | 832 | 1119 | 1084 | 1281 | 48.77 | 4364.77 | 4117.5 | 247.27 | 4365 |  |  | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
174 | 2020-06-23 | 776 | 998 | 952 | 1179 | 43.52 | 3948.52 | 3774 | 174.52 | 3949 |  |  | Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092.Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
175 | 2020-06-24 | 580 | 726 | 696 | 816 | 30.34 | 2848.34 | 2658 | 190.34 | 2849 |  |  | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113.Grid failure from 10:35 to 10:38.Cloudy day. |  | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
176 | 2020-06-25 | 695 | 907 | 877 | 1069 | 43.27 | 3591.27 | 3403.5 | 187.77 | 3592 |  |  | Module cleaning by rain. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2020-06-26 | 676 | 887 | 862 | 1013 | 40.41 | 3478.41 | 3313.5 | 164.91 | 3479 |  |  | Module clean by rain.Grid failure from 16:34 to 16:47 & 17:46 to 17:57 and 18:06 to 18:22. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 2020-06-27 | 761 | 1008 | 973 | 1164 | 58.06 | 3964.06 | 3738.75 | 225.31 | 3965 |  |  | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T, Inverter No 3, total module cleaning-1092, and Cloudy day. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
179 | 2020-06-28 | 832 | 1124 | 1088 | 1296 | 73.89 | 4413.89 | 4168.5 | 245.39 | 4414 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2020-06-29 | 574 | 1053 | 1018 | 1220 | 62.73 | 3927.73 | 3681 | 246.73 | 3928 |  |  | Today Inverter No:1(11:45 to 13:50) Breakdown due to Preventive Maintenance by AMC (ABB).Module Cleaning has been done in Row-I,J,K,L, Inverter No- 2, total module cleaning-1092. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2020-06-30 | 499 | 641 | 625 | 720 | 30.72 | 2515.72 | 2388.75 | 126.97 | 2516 | 3.32 | 0.73863 | Module clean by rain.Grid failure from 09:58 to 10:09 . |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2020-07-01 | 529 | 685 | 655 | 776 | 39.09 | 2684.09 | 2470.5 | 213.59 | 2685 | 5.294 | 0.49433 | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113.Grid failure from 10:39 to 13:25.Cloudy day. |  | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
183 | 2020-07-02 | 822 | 1109 | 1074 | 1296 | 72.83 | 4373.83 | 4167 | 206.83 | 4375 | 5.838 | 0.73041 | Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4, total module cleaning-990. |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2020-07-03 | 635 | 842 | 812 | 983 | 47.98 | 3319.98 | 3165.75 | 154.23 | 3320 |  |  | Module clean by rain.Grid failure from 15:26 to 15:30 and 16:18 to 16.27 . |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 2020-07-04 | 781 | 1053 | 1013 | 1224 | 60.35 | 4131.35 | 3914.25 | 217.1 | 4132 | 5.722 | 0.70383 | Module clean by rain.Grid failure from 16:08 to 16:10. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 2020-07-05 | 651 | 842 | 811 | 958 | 36.52 | 3298.52 | 3126 | 172.52 | 3299 | 4.316 | 0.745 | Fully cloudy day. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
187 | 2020-07-06 | 367 | 438 | 429 | 484 | 13.4 | 1731.4 | 1610.25 | 121.15 | 1732 | 2.071 | 0.81512 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2020-07-07 | 590 | 771 | 740 | 877 | 35.09 | 3013.09 | 2767.5 | 245.59 | 3014 | 4.057 | 0.72409 | Module clean by rain.Grid failure from 11:14 to 11:21. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2020-07-08 | 434 | 550 | 535 | 625 | 23.18 | 2167.18 | 2076.75 | 90.43 | 2168 | 2.63 | 0.80345 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2020-07-09 | 594 | 776 | 751 | 887 | 36.01 | 3044.01 | 2816.25 | 227.76 | 3045 | 4.082 | 0.72705 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2020-07-10 | 736 | 973 | 942 | 1139 | 48.98 | 3838.98 | 3662.5 | 176.48 | 3839 | 5.091 | 0.73497 | Module clean by rain.Grid failure from 11:12 to 11:16. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2020-07-11 | 686 | 912 | 887 | 1054 | 41.53 | 3580.53 | 3438.75 | 141.78 | 3581 | 4.512 | 0.77355 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 2020-07-12 | 534 | 690 | 671 | 786 | 32.65 | 2713.65 | 2565 | 148.65 | 2714 | 3.543 | 0.74661 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2020-07-13 | 680 | 913 | 882 | 1033 | 44.45 | 3552.45 | 3315 | 237.45 | 3553 | 4.727 | 0.73259 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 2020-07-14 | 650 | 887 | 867 | 1013 | 46.01 | 3463.01 | 3327 | 136.01 | 3464 | 4.748 | 0.71108 | Fully cloudy day.Grid failure from 18:01 to 18:25. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
196 | 2020-07-15 | 631 | 821 | 781 | 902 | 39.47 | 3174.47 | 2970.75 | 203.72 | 3175 | 4.269 | 0.72489 | Today we are replaced cooling fan(Cabinet door)D.C. side in Inverter No-4 and remove 2 Nos fan (Not working)A.C side(Canbinet door) in Inverter No-3.(total 3 fan not working)Module clean by rain.Grid failure from 17:07 to 17:11. |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 2020-07-16 | 619 | 817 | 791 | 918 | 33.18 | 3178.18 | 3002.25 | 175.93 | 3179 | 3.992 | 0.77616 | Module clean by rain. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2020-07-17 | 636 | 837 | 600 | 957 | 34.07 | 3064.07 | 2847.75 | 216.32 | 3065 | 4.338 | 0.68864 | Yesterday night (16-07-2020) Inverter No-3 not working due ACDC Rectifier switch(SMPS) are not work so Inverter are stop after 17-07-2020 manually started 10:45am. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 2020-07-18 | 745 | 1048 | 1013 | 1230 | 61.71 | 4097.71 | 3906 | 191.71 | 4098 | 5.951 | 0.67117 | Cloudy day.Grid failure from 12:01 to 12:09 and 16:33 to 17:23. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
200 | 2020-07-19 | 751 | 1028 | 988 | 1200 | 60.87 | 4027.87 | 3845.25 | 182.62 | 4028 | 5.374 | 0.73054 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
201 | 2020-07-20 | 706 | 948 | 917 | 1098 | 52.76 | 3721.76 | 3487.5 | 234.26 | 3722 | 4.992 | 0.7267 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
202 | 2020-07-21 | 751 | 1033 | 1003 | 1195 | 51.23 | 4033.23 | 3848.25 | 184.98 | 4034 | 5.5 | 0.71487 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
203 | 2020-07-22 | 812 | 1144 | 1104 | 1346 | 60.95 | 4466.95 | 4266 | 200.95 | 4467 | 6.277 | 0.69361 | Module clean by rain.Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
204 | 2020-07-23 | 720 | 988 | 953 | 1139 | 57.19 | 3857.19 | 3641.25 | 215.94 | 3858 | 5.241 | 0.71746 | Module clean by rain.Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
205 | 2020-07-24 | 620 | 867 | 837 | 983 | 41.74 | 3348.74 | 3163.5 | 185.24 | 3349 | 4.398 | 0.74219 | Module clean by rain.Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
206 | 2020-07-25 | 534 | 736 | 710 | 836 | 35.45 | 2851.45 | 2730 | 121.45 | 2852 | 4.556 | 0.61012 | Grid failure from 08:56 to 10:17. Module clean by rain.Cloudy day |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
207 | 2020-07-26 | 666 | 902 | 872 | 1024 | 49.98 | 3513.98 | 3300.75 | 213.23 | 3514 | 4.778 | 0.71682 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
208 | 2020-06-27 | 720 | 1018 | 983 | 1159 | 63.76 | 3943.76 | 3738.5 | 205.26 | 3944 | 5.15 | 0.74642 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
209 | 2020-07-28 | 656 | 907 | 887 | 1028 | 50.53 | 3528.53 | 3335.25 | 193.28 | 3529 | 4.819 | 0.71375 | Today has been done Air filter paper clean of all inverter (Cabinet door Filter).Cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
210 | 2020-07-29 | 665 | 922 | 887 | 1043 | 45.96 | 3562.96 | 3347.25 | 215.71 | 3563 | 4.988 | 0.69621 | Cloudy day.Grid failure from 11:34 to 11:46 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
211 | 2020-07-30 | 519 | 701 | 670 | 781 | 30.88 | 2701.88 | 2580 | 121.88 | 2702 | 3.466 | 0.75982 | Module clean by rain.Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
212 | 2020-07-31 | 686 | 953 | 918 | 1094 | 53.63 | 3704.63 | 3461.25 | 243.38 | 3705 | 5.109 | 0.70681 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
213 | 2020-08-01 | 705 | 983 | 947 | 1149 | 58.14 | 3842.14 | 3654 | 188.14 | 3843 | 4.828 | 0.77581 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
214 | 2020-08-02 | 696 | 993 | 958 | 1129 | 57.52 | 3833.52 | 3629.25 | 204.27 | 3834 | 5.476 | 0.6824 | Cloudy day.Grid failure from 15:39 to 15:46 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
215 | 2020-08-03 | 670 | 942 | 907 | 1059 | 46.93 | 3624.93 | 3417.75 | 207.18 | 3625 | 4.808 | 0.73485 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
216 | 2020-08-04 | 640 | 902 | 877 | 1053 | 54.3 | 3526.3 | 3337.5 | 188.8 | 3519 | 4.946 | 0.69345 | Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
217 | 2020-08-05 | 499 | 671 | 645 | 756 | 35.1 | 2606.1 | 2476.5 | 129.6 | 2604 | 3.453 | 0.73502 | Cloudy day.Grid failure from 16:43 to 17:02 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
218 | 2020-08-06 | 202 | 282 | 288 | 318 | 8.73 | 1098.73 | 936.75 | 161.98 | 1099 | 1.413 | 0.75807 | Today we are change and replace new phase failure relay in Inverter no-1 during 9:45 to 10:30 and change and replace new SPD in AJB No-109 in Inverter No-2 during 10:40 to 11:45. .Module clean by rain.fully cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
219 | 2020-08-07 | 363 | 529 | 504 | 575 | 18.15 | 1989.15 | 1798.5 | 190.65 | 1989 | 2.506 | 0.77358 | Today we are change and replace new SPD in AJB No-104 in Inverter No-1 and AJB No-117 in Inverter No-3 during 9:10 to 09:45.Module clean by rain.fully cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
220 | 2020-08-08 | 469 | 746 | 726 | 861 | 33.89 | 2835.89 | 2711.25 | 124.64 | 2836 | 3.68 | 0.75112 | Module clean by rain.Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
221 | 2020-08-09 | 282 | 428 | 413 | 474 | 13.41 | 1610.41 | 1434.75 | 175.66 | 1611 | 1.958 | 0.80193 | Module clean by rain.fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
222 | 2020-08-10 | 398 | 626 | 600 | 691 | 20.79 | 2335.79 | 2186.25 | 149.54 | 2336 | 3.104 | 0.73351 | Module clean by rain.cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
223 | 2020-08-11 | 529 | 848 | 826 | 972 | 35.86 | 3210.86 | 3042.75 | 168.11 | 3211 | 3.397 | 0.92129 | Today we are replaced connector in string no-03(++tive) of AJB No-104 inverter no-1 during 10:00 to 10:25..Module clean by rain.cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
224 | 2020-08-12 | 338 | 523 | 499 | 580 | 18.37 | 1958.37 | 1814.25 | 144.12 | 1959 | 2.576 | 0.74121 | Cloudy day.Grid failure from 15:37 to 15:25 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
225 | 2020-08-13 | 242 | 363 | 353 | 398 | 10.78 | 1366.78 | 1222.5 | 144.28 | 1223 | 1.71 | 0.69708 | Module clean by rain. cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
226 | 2020-08-14 | 378 | 585 | 569 | 666 | 20.28 | 2218.28 | 2049 | 169.28 | 2219 | 2.588 | 0.83569 | Cloudy day.Grid failure from 08:30 to 08:37 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
227 | 2020-08-15 | 267 | 413 | 399 | 453 | 13.19 | 1545.19 | 1408.5 | 136.69 | 1546 | 2.022 | 0.74521 | Module clean by rain. Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
228 | 2020-08-16 | 373 | 479 | 469 | 534 | 11.32 | 1866.32 | 1710 | 156.32 | 1867 | 2.315 | 0.78604 | Today we are found (morning time) the error of Isolation resistance in string-3 of string inverter no-6 after remove the string in inverter.Module clean by rain. Fully cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
229 | 2020-08-17 | 393 | 499 | 478 | 565 | 15.45 | 1950.45 | 1767.75 | 182.7 | 1951 | 2.33 | 0.81612 | Module clean by rain, Cloudy day.Grid failure from 15:30 to 15:36 and 15:42 to 15:51 & 18:15 to 18:18. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
230 | 2020-08-18 | 403 | 529 | 509 | 600 | 18.72 | 2059.72 | 1953 | 106.72 | 2058 |  |  | today we are not found value of insolation in scada..Module clean by rain, Cloudy day.Grid failure from 13:23 to 13:29. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
231 | 2020-08-19 | 585 | 787 | 772 | 897 | 30.73 | 3071.73 | 2882.25 | 189.48 | 3072 |  |  | Module clean by rain, Cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
232 | 2020-08-20 | 414 | 514 | 509 | 595 | 15.58 | 2047.58 | 1882.05 | 165.53 | 2048 |  |  | Module clean by rain, Cloudy , today we are replace the dc 12 amp fuse link of the string no 06 -- line,Ajb no 103 inverter no 04 during 08:20 to 08:25. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0
233 | 2020-08-21 | 327 | 433 | 418 | 493 | 19.97 | 1690.97 | 1534.5 | 156.47 | 1691 |  |  | Today installed new copper transformer 63KVA and removed aluminium transformer 63KVA during 14:20 to 15:35.we are change and replaced adam-4015-CE in tracker side(WS-2) |  |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
234 | 2020-08-22 | 227 | 277 | 267 | 318 | 8.51 | 1097.51 | 987 | 110.51 | 1098 |  |  | Today we are change and replaced adam-4118-AE in Inverter-1 side (WS-1).Module clean by rain. Fully cloudy day |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
235 | 2020-08-23 | 151 | 187 | 176 | 212 | 4.91 | 730.91 | 588.75 | 142.16 | 776 |  |  | Module clean by rain. Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
236 | 2020-08-24 | 232 | 282 | 268 | 317 | 7.63 | 1106.63 | 966 | 140.63 | 1107 |  |  | Module clean by rain. Fully cloudy day |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
237 | 2020-08-25 | 559 | 741 | 690 | 872 | 34.19 | 2896.19 | 2718 | 178.19 | 2897 |  |  | Today we are Install the new Communication cable CAT 6(128m)in SEED Box-1 inverter -1 side total 3 cable install 1.Anomometer ,2.humidity weather and 3, Signal cable. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 2020-08-26 | 529 | 691 | 640 | 822 | 34.07 | 2716.07 | 2514.75 | 201.32 | 2717 |  |  | Today Replaced the D.C.12 Amp fuse link of the string-03 --tive line in AJB-102 of The Inverter-4 during the period of 8:15 to 08:20. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
239 | 2020-08-27 | 661 | 902 | 832 | 1089 | 50.89 | 3534.89 | 3380.25 | 154.64 | 3535 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 2020-08-28 | 484 | 625 | 574 | 735 | 24.5 | 2442.5 | 2289.75 | 152.75 | 2443 | 2.953 | 0.80633 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 2020-08-29 | 494 | 670 | 620 | 837 | 32.75 | 2653.75 | 2473.5 | 180.25 | 2654 | 3.715 | 0.6963 | Today afternoon time breakdown due to install new Energy meter of Incoming line (415V) during 15:51 to 16:21. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 2020-08-30 | 111 | 136 | 126 | 156 | 3.65 | 532.65 | 422.25 | 110.4 | 533 | 0.647 | 0.80293 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 2020-08-31 | 257 | 318 | 303 | 378 | 11.48 | 1267.48 | 1130.25 | 137.23 | 1268 | 1.408 | 0.87775 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 2020-09-01 | 650 | 907 | 826 | 1054 | 44.35 | 3481.35 | 3285 | 196.35 | 3482 | 4.282 | 0.79256 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 2020-09-02 | 595 | 811 | 746 | 947 | 37.23 | 3136.23 | 2988.75 | 147.48 | 3137 | 3.845 | 0.79519 | Today P.M of VCB and install new single core cable(230v AC) in VCB to LBS for Auxiliary Suppy to LBS during 17:40 to 18:50. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 2020-09-03 | 625 | 882 | 807 | 1008 | 41.22 | 3363.22 | 3150.75 | 212.47 | 3364 | 4.317 | 0.7595 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 2020-09-04 | 731 | 1033 | 947 | 1185 | 53.42 | 3949.42 | 3751.5 | 197.92 | 3950 | 5.169 | 0.74481 | Grid failure from 09:26 to 09:30 and 14:09 to 14:11. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 2020-09-05 | 661 | 927 | 847 | 1074 | 45.63 | 3554.63 | 3360 | 194.63 | 3555 | 4.446 | 0.77933 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 2020-09-06 | 705 | 1008 | 928 | 1174 | 52.63 | 3867.63 | 3691.5 | 176.13 | 3868 | 4.862 | 0.7754 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 2020-09-07 | 71 | 96 | 75 | 91 | 3.64 | 336.64 | 229.5 | 107.14 | 337 | 4.572 | 0.071842 | Grid failure from 09:33 to 16:48 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | 2020-09-08 | 690 | 998 | 912 | 1169 | 50.01 | 3819.01 | 3615.75 | 203.26 | 3820 | 4.929 | 0.75537 | Today we are install new REC module (3 Nos) in Inverter No-1. 1)Module No- 15 (Row No-E) and B Line, Module no:JMPD100902548 ,2)Module No- 12 (Row No-G) and B Line, Module no:JMPD100903063,3)Module No- 12 (Row No-H) and B Line , Module no:JMPD100902866 due to old module gone to testing purpose on singapore. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 2020-09-09 | 530 | 746 | 681 | 842 | 34.8 | 2833.8 | 2662.5 | 171.3 | 2834 | 3.575 | 0.77264 | Today we are install new 15KW ACDB Box in Tracker's Inverter. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 2020-09-10 | 695 | 993 | 902 | 1169 | 45.39 | 3804.39 | 3594 | 210.39 | 3805 | 5.027 | 0.73773 | Grid Failure From-16:44 to 16:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 2020-09-11 | 585 | 847 | 771 | 958 | 42.42 | 3203.42 | 3031.5 | 171.92 | 3204 | 4.182 | 0.74673 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 2020-09-12 | 675 | 993 | 897 | 1139 | 49.16 | 3753.16 | 3540 | 213.16 | 3754 | 4.845 | 0.75518 | Grid failure from -13:07 to 13:12 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 2020-09-13 | 610 | 862 | 787 | 993 | 43.04 | 3295.04 | 3132.75 | 162.29 | 3296 | 2.356 | 1.3635 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 2020-09-14 | 494 | 680 | 625 | 781 | 33.59 | 2613.59 | 2445 | 168.59 | 2614 | 3.313 | 0.76902 | Grid failure from -12:29 to12:38 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 2020-09-15 | 559 | 786 | 715 | 897 | 38.3 | 2995.3 | 2806.5 | 188.8 | 2996 | 3.762 | 0.7762 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 2020-09-16 | 560 | 796 | 726 | 897 | 35.95 | 3014.95 | 2853.75 | 161.2 | 3015 | 3.852 | 0.76288 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 2020-09-17 | 463 | 640 | 590 | 731 | 27.85 | 2451.85 | 2250 | 201.85 | 2452 | 3.082 | 0.77543 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 2020-09-18 | 570 | 792 | 726 | 917 | 37.08 | 3042.08 | 2851.5 | 190.58 | 3043 | 3.767 | 0.78733 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | 2020-09-19 | 655 | 942 | 856 | 1014 | 49.71 | 3516.71 | 3355.5 | 161.21 | 3517 | 4.413 | 0.77677 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | 2020-09-20 | 630 | 943 | 862 | 1128 | 45.49 | 3608.49 | 3361.5 | 246.99 | 3609 | 4.516 | 0.77891 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 2020-09-21 | 676 | 1003 | 913 | 1150 | 46.45 | 3788.45 | 3568.5 | 219.95 | 3793 | 4.715 | 0.78407 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 2020-09-22 | 741 | 1119 | 1018 | 1275 | 61.33 | 4214.33 | 4010.25 | 204.08 | 4215 | 5.426 | 0.75713 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 2020-09-23 | 519 | 715 | 650 | 806 | 30.84 | 2720.84 | 2555.25 | 165.59 | 2721 | 3.045 | 0.87095 | Today we are cleaning all inverter Door filters. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | 2020-09-24 | 720 | 1069 | 973 | 1225 | 58.76 | 4045.76 | 3833.25 | 212.51 | 4046 | 5.261 | 0.74957 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | 2020-09-25 | 651 | 942 | 851 | 1084 | 52.59 | 3580.59 | 3390.75 | 189.84 | 3581 | 4.634 | 0.75318 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 2020-09-26 | 590 | 857 | 787 | 973 | 44.67 | 3251.67 | 3058.5 | 193.17 | 3252 | 4.066 | 0.77954 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 2020-09-27 | 529 | 761 | 690 | 856 | 39.46 | 2875.46 | 2702.25 | 173.21 | 2876 | 3.652 | 0.76756 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 2020-09-28 | 660 | 969 | 907 | 1104 | 56.35 | 3696.35 | 3500.25 | 196.1 | 3697 | 4.82 | 0.74758 | Today we are found 3 MC4 connector Burn in Invertor No-3 AJB No-2 string No-8 ++tive site & AJB 4 string No-1 ++tive site & AJB-6 string No-2 ++tive site. we replaced all 3 MC4 connector and started the strings. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 2020-09-29 | 640 | 952 | 918 | 1104 | 55.75 | 3669.75 | 3468.75 | 201 | 3670 | 4.767 | 0.75037 | Module Cleaning has been done in Row- A,B,C,D,E,F, Inverter No- 4, total module cleaning-792, and Cloudy day. |  | 792 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
273 | 2020-09-30 | 696 | 1053 | 1028 | 1210 | 59.5 | 4046.5 | 3834.75 | 211.75 | 4047 | 4.655 | 0.84736 | Module Cleaning has been done in Row- G,H,I Inverter No- 4, total module cleaning-594, and Cloudy day. |  | 594 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
274 | 2020-10-01 | 660 | 983 | 937 | 1179 | 58.19 | 3817.19 | 3616.5 | 200.69 | 3818 | 4.89 | 0.76099 | Module Cleaning has been done in Row- J,K,L,A,B,C, and Trackers Inverter No- 4, total module cleaning-816, and Today we are found 2 MC4 connector Burn in Invertor No-3 AJB No-2 string No-2 ++tive site & AJB 3 string No-1 ++tive site. we replaced all 2 MC4 connector and started the strings. |  | 816 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | 2020-10-02 | 680 | 1033 | 1004 | 1235 | 63.3 | 4015.3 | 3804.75 | 210.55 | 4016 | 5.162 | 0.75828 | Module Cleaning has been done in Row-,D,E,F,G,H, Inverter No- 4, total module cleaning-702,Grid failure from -12:58 to 13:01 & 17:01 to 17:04 |  | 702 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 2020-10-03 | 716 | 1120 | 1083 | 1351 | 70.77 | 4340.77 | 4122.75 | 218.02 | 4341 | 5.624 | 0.75231 | Module Cleaning has been done in Row- I,J,K,L, Tracker 5,6,7 and Row-Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1020 |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 2020-10-04 | 670 | 1002 | 983 | 1229 | 64.97 | 3948.97 | 3744.75 | 204.22 | 3949 | 5.089 | 0.75632 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 2020-10-05 | 706 | 1084 | 1079 | 1306 | 70.4 | 4245.4 | 4021.5 | 223.9 | 4246 | 5.312 | 0.77907 | Module Cleaning has been done in Row- L Inverter No- 2 & M,N,O,P Inverter No- 3 total module cleaning-1050 |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 2020-10-06 | 650 | 1073 | 1038 | 1204 | 66.33 | 4031.33 | 3825.75 | 205.58 | 4032 | 5.541 | 0.70923 | Module Cleaning has been done in Row- H Inverter No- 1 & I,J,K Inverter No- 2 total module cleaning-1071 & Grid failure from -11:35 to12:07 |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 2020-10-07 | 700 | 1150 | 1079 | 1235 | 64.52 | 4228.52 | 4018.5 | 210.02 | 4229 | 5.531 | 0.74522 | Module Cleaning has been done in Row- A,B,C,D,E,F,G Inverter No- 1 & R,S,T Inverter No- 3 total module cleaning-1050 & Grid failure from -07:15 to 07:30 & 08:09 to 08:14 & 10:28 to 10:35 & In the cantrol room 1 exhaust fan failure, removed the fan and send to reparing. |  | 1050 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 2020-10-08 | 707 | 1144 | 1103 | 1225 | 70.81 | 4249.81 | 4045.5 | 204.31 | 4250 | 5.491 | 0.75438 | Module Cleaning has been done in Row- L,Inverter No- 2 & M,N,O,P,Q, Inverter No- 3 & total module cleaning-1176 & Grid failure from -05:25 to 06:08. |  | 1176 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 2020-10-09 | 690 | 1099 | 1049 | 1164 | 61.3 | 4063.3 | 3853.5 | 209.8 | 4064 | 5.011 | 0.79046 | Module Cleaning has been done in Row- H,Inverter No- 1 & I,J,K, Inverter No- 2 & total module cleaning-1071 |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 2020-10-10 | 690 | 1093 | 1033 | 1140 | 63.86 | 4019.86 | 3808.5 | 211.36 | 4020 | 5.144 | 0.76169 | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 |  | 1044 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 2020-10-11 | 666 | 1034 | 983 | 1093 | 59.99 | 3835.99 | 3651.75 | 184.24 | 3836 | 4.893 | 0.76411 | Grid failure from -16:23 to16:26 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 2020-10-12 | 615 | 962 | 907 | 1049 | 53.47 | 3586.47 | 3382.5 | 203.97 | 3587 | 5.029 | 0.69519 | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 & Grid failure from -10:03 to10:44 |  | 1026 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 2020-10-13 | 660 | 998 | 953 | 1144 | 58.9 | 3813.9 | 3622.5 | 191.4 | 3814 | 4.765 | 0.78014 | Module Cleaning has been done in Row- I,J,K,L, Inverter No- 4 & Q,R,S,T, Inverter No - 3, total module cleaning-1020 |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 2020-10-14 | 650 | 983 | 967 | 1119 | 58.9 | 3777.9 | 3587.25 | 190.65 | 3778 | 4.569 | 0.80592 | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 & Grid failure from -17:10 to 17:14 |  | 1050 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 2020-10-15 | 661 | 1053 | 1019 | 1199 | 63.01 | 3995.01 | 3774 | 221.01 | 3996 | 4.865 | 0.80056 | Module Cleaning has been done in Row- H, Inverter No- 1 & I,J,K Inverter No - 2, total module cleaning-1071 |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 2020-10-16 | 619 | 963 | 912 | 1089 | 53.13 | 3636.13 | 3435 | 201.13 | 3637 | 4.464 | 0.79409 | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 & Grid failure from -15:00 to15:05 |  | 1044 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 2020-10-17 | 479 | 706 | 675 | 801 | 32.11 | 2693.11 | 2502 | 191.11 | 2694 | 3.311 | 0.79303 | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 2020-10-18 | 525 | 761 | 726 | 872 | 40.42 | 2924.42 | 2757 | 167.42 | 2925 | 3.541 | 0.80511 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 2020-10-19 | 594 | 887 | 852 | 1003 | 45.75 | 3381.75 | 3185.25 | 196.5 | 3382 | 3.922 | 0.84046 | Module Cleaning has been done in Row- I,J,K,L, Inverter No- 4 & Q,R,S,T, Inverter No - 3, total module cleaning-1020 |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 2020-10-20 | 625 | 953 | 922 | 1064 | 52.96 | 3616.96 | 3410.25 | 206.71 | 3617 | 4.68 | 0.75328 | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 2020-10-21 | 635 | 993 | 948 | 1099 | 55.09 | 3730.09 | 3543 | 187.09 | 3731 | 4.802 | 0.75728 | Module Cleaning has been done in Row- H, Inverter No- 1 & I,J,K Inverter No - 2, total module cleaning-1071 |  | 1071 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 2020-10-22 | 716 | 1144 | 1083 | 1257 | 71.13 | 4271.13 | 4062.75 | 208.38 | 4272 | 5.474 | 0.76064 | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 & Today 1 Module Damage By Monkey, Inverter No-4 Thin Film Side Row No-C Module No-50 'B' Side S.No-NPC 10BY1116233 |  | 1044 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 2020-10-23 | 731 | 1169 | 1109 | 1275 | 73.98 | 4357.98 | 4151.25 | 206.73 | 4358 | 5.555 | 0.76464 | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 2020-10-24 | 705 | 1144 | 1079 | 1270 | 72.99 | 4270.99 | 4078.5 | 192.49 | 4271 | 9.63 | 0.43227 | Module Cleaning has been done in Row- I,J,K, Inverter No- 4 & total module cleaning - 540 |  | 540 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 2020-10-25 | 615 | 1039 | 988 | 1154 | 61.68 | 3857.68 | 3661.5 | 196.18 | 3858 | 5.066 | 0.74225 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 2020-10-26 | 650 | 1129 | 1078 | 1270 | 71.27 | 4198.27 | 3997.5 | 200.77 | 4199 | 5.42 | 0.75509 | Module Cleaning has been done in Row- L, Inverter No- 4 & Tracker 5,6,7, & N,O,P,Q,R,S,T, & total module cleaning - 1026 Today Failure D2D Blower Fan Inverter No - 1, & We Replaced New D2D Blower Fan. |  | 1026 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 2020-10-27 | 640 | 952 | 1054 | 1205 | 70.66 | 3921.66 | 3736.5 | 185.16 | 3922 | 5.406 | 0.70711 | Grid failure from 10:07 to 10:11 & 11:00 to 11:11 & Today we are cleaning all inverter Door filters. & Today Come to ABB Engineer For Inverter No-2, for PM Activity, Breakdown During 13:14 to 14:06 & Module Cleaning has been done in Row- J,K,L, Inverter No-2 & Row No- M, Inverter NO-3 & total module cleaning - 1071 |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 2020-10-28 | 671 | 1094 | 1033 | 1149 | 66.5 | 4013.5 | 3816.75 | 196.75 | 4014 | 5.027 | 0.77825 | Module Cleaning has been done in Row- E,F,G,H, Inverter No-1 & Row No- I, Inverter NO-2 & total module cleaning - 1050 |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 2020-10-29 | 660 | 1038 | 978 | 1074 | 61.97 | 3811.97 | 3612 | 199.97 | 3812 | 4.883 | 0.76088 | Grid failure from -11:33 to11:38 & Module Cleaning has been done in Row- A,B,C,D, Inverter No-1 & Row No- A,B,C,D,E,F, Inverter NO-4 & total module cleaning - 1128 |  | 1128 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 2020-10-30 | 671 | 1048 | 998 | 1093 | 64.13 | 3874.13 | 3683.25 | 190.88 | 3875 | 5.034 | 0.75026 | Module Cleaning has been done in Row- G,H,I,J,K,L Tracker 5,6,7 and Row-Inverter No- 4 & total module cleaning-1122& Grid failure from-1:34 to 1:37 |  | 1122 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 2020-10-31 | 655 | 998 | 942 | 1074 | 58.85 | 3727.85 | 3535.5 | 192.35 | 3728 | 4.658 | 0.78006 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 2020-11-01 | 630 | 973 | 923 | 1038 | 57.27 | 3621.27 | 3453 | 168.27 | 3622 | 4.603 | 0.76694 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 2020-11-02 | 625 | 948 | 922 | 1008 | 56.12 | 3559.12 | 3370.5 | 188.62 | 3560 | 4.554 | 0.76192 | Module Cleaning has been done in Row- M,N,O,P,Q,R,S,T Inverter No- 3 & total module cleaning-1085 |  | 1085 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 2020-11-03 | 645 | 1028 | 993 | 1089 | 61.72 | 3816.72 | 3624.75 | 191.97 | 3817 | 4.73 | 0.78653 | Grid failure from -08:12 to 08:17 & Module Cleaning has been done in Row- I,J,K,L, Inverter No- 2 total module cleaning-1092 |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 2020-11-04 | 700 | 1124 | 1059 | 1174 | 67.37 | 4124.37 | 3927.75 | 196.62 | 4125 | 5.058 | 0.79487 | Module Cleaning has been done in Row- A,B,C,D,E,F,G, H, Inverter No- 1, total module cleaning-1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 2020-11-05 | 651 | 1018 | 962 | 1059 | 59.77 | 3749.77 | 3562.5 | 187.27 | 3750 | 4.766 | 0.76688 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No- 4, total module cleaning-1188 |  | 1188 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 2020-11-06 | 675 | 1048 | 988 | 1129 | 62.63 | 3902.63 | 3705 | 197.63 | 3903 | 4.943 | 0.76959 | Module Cleaning has been done in Row- I,J,K,L, Tracker 5,6,7 and Row-Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1020 |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 2020-11-07 | 656 | 1013 | 978 | 1084 | 61.89 | 3792.89 | 3602.25 | 190.64 | 3793 | 4.759 | 0.77682 | Today we are found 3 MC4 connector Burn in Inverter No-4 AJB No-105 string No-2 ++tive line & string No-4 --tive line 5--tive&7++tive line. we replaced all 3 MC4 connector and started the strings & Module clening has been done in Row l, inverter No-2 M,N,O,P Inverter no-3 total Module Clening-1050 |  | 1050 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 2020-11-08 | 645 | 983 | 952 | 1023 | 58.71 | 3661.71 | 3472.5 | 189.21 | 3662 | 4.461 | 0.80009 | Today we are found 2 MC4 connector Burn in Inverter No-4 AJB No-106 string No-2 ++tive line & string No-4 --tive line & . we replaced all 2 MC4 connector and started the strings |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 2020-11-09 | 605 | 933 | 888 | 942 | 53.72 | 3421.72 | 3240 | 181.72 | 3422 | 4.344 | 0.76779 | Today we are found 4 MC4 connector Burn in Inverter No-2 AJB No-01 string No-1 ++tive line & string No-4 --tive line & AJB-7 string No-7++tive line. we replaced all 4 MC4 connector and started the strings & Grid failure from 9:19 to 9:24 & Moduule Cleaning has been Done in Row-H, inverter no-1 I,J,K, inverter No-2 total moduel clening 1071 |  | 1071 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 2020-11-10 | 509 | 781 | 705 | 827 | 43.83 | 2865.83 | 2685.75 | 180.08 | 2866 | 4.464 | 0.62576 | Yesterday nighat time Grid failure & UGVCL side phase sikvans chang so morning time inverter not wark up after all phase sikvans chang then inverter stated 10:40 & Module cleaning has been done in Row-A,B,C,D,E,F,G inverter no-1 & A,B inverter no-4&total module cleaning-1044 |  | 1044 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 2020-11-11 | 609 | 912 | 857 | 907 | 47.94 | 3332.94 | 3156.75 | 176.19 | 3333 | 4.208 | 0.77199 | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 2020-11-12 | 585 | 847 | 796 | 847 | 46.23 | 3121.23 | 2943.75 | 177.48 | 3121 | 3.836 | 0.79299 | Module Cleaning has been done in Row- I,J,K,L, Inverter no-4 & Tracker 1,2,3, and Row-Q,R,S,T, Inverter No- 3 & total module cleaning-1020 |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 2020-11-13 | 635 | 983 | 943 | 1058 | 59.24 | 3678.24 | 3487.5 | 190.74 | 3679 | 4.669 | 0.768 | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 & Grid failure from -9:44 to 9:52 |  | 1050 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 2020-11-14 | 620 | 943 | 907 | 1008 | 55.08 | 3533.08 | 3344.25 | 188.83 | 3534 | 4.453 | 0.77351 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 2020-11-15 | 574 | 861 | 832 | 923 | 47.99 | 3237.99 | 3069.75 | 168.24 | 3238 | 4.13 | 0.76415 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 2020-11-16 | 645 | 1034 | 993 | 1124 | 64.06 | 3860.06 | 3671.25 | 188.81 | 3861 | 4.831 | 0.77896 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 2020-11-17 | 646 | 1003 | 962 | 1088 | 61.18 | 3760.18 | 3568.5 | 191.68 | 3761 | 4.727 | 0.77548 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 2020-11-18 | 620 | 942 | 887 | 998 | 54.13 | 3501.13 | 3313.5 | 187.63 | 3499 | 4.296 | 0.79384 | Moduule Cleaning has been Done in Row-H, inverter no-1 I,J,K, inverter No-2 total moduel clening 1071 |  | 1071 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 2020-11-19 | 695 | 1084 | 1014 | 1134 | 63.44 | 3990.44 | 3794.25 | 196.19 | 3991 | 4.844 | 0.80303 | Module Cleaning has been done in Row- A,B,C,D,E,F,G,Inverter No- 1 & A,B, Inverter No- 4 & total module cleaning-1044 |  | 1044 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2020-11-20 | 671 | 1080 | 947 | 1079 | 59.85 | 3836.85 | 3585.75 | 251.1 | 3837 | 4.497 | 0.83161 | Module Cleaning has been done in Row- C,D,E,F,G,H, Inverter No- 4 & total module cleaning-1026 |  | 1026 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 2020-11-21 | 660 | 993 | 927 | 1028 | 57.49 | 3665.49 | 3474.75 | 190.74 | 3666 | 4.454 | 0.80222 | Module Cleaning has been done in Row- I,J,K,L, Inverter no-4 &Tracker 5,6,7 and Row-Q,R,S,T, Inverter No- 3 & total module cleaning-1020 |  | 1020 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 2020-11-22 | 681 | 1043 | 978 | 1099 | 63.87 | 3864.87 | 3685.5 | 179.37 | 3865 | 4.763 | 0.7909 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 2020-11-23 | 665 | 1034 | 988 | 1119 | 64.18 | 3870.18 | 3678 | 192.18 | 3871 | 4.862 | 0.776 | Module Cleaning has been done in Row- L, Inverter No- 2 & M,N,O,,P Inverter No - 3, total module cleaning-1050 |  | 1050 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 2020-11-24 | 680 | 1083 | 1018 | 1119 | 67.4 | 3967.4 | 3766.5 | 200.9 | 3968 | 4.903 | 0.78879 | Module Cleaning has been done in Row-I,J,K,L Inverter No-2, total module cleaning-1092 &Today Preventive maintenance of transformer No-3&4 has been done. |  | 1092 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
329 | 2020-11-25 | 509 | 726 | 686 | 741 | 36.94 | 2698.94 | 2537.25 | 161.69 | 2699 | 2.783 | 0.94524 | Module Cleaning has been done in Row- A,B,C,D,E,F,G,H, Inverter No- 1 total module cleaning-1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 2020-11-26 | 595 | 877 | 826 | 907 | 48.66 | 3253.66 | 3077.25 | 176.41 | 3254 | 3.808 | 0.83286 | Today we are installed new pyranometer SP-110 at wather Module Cleaning has been done in Row- A,B,C,D,E,F,G, Inverter No- 4 total module cleaning-882 |  | 882 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 2020-11-27 | 680 | 1028 | 958 | 1099 | 61.31 | 3826.31 | 3630 | 196.31 | 3827 | 4.56 | 0.81799 | Today we are cleaning all inverter Door filters. & Today preventive maintenance of transformer No-2 has been done.& Module Cleaning has been done in Row- H,I,J,K,L Inverter No-4 & Tracker 1,2,3, total module cleaning - 924 |  | 924 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
332 | 2020-11-28 | 716 | 1094 | 1033 | 1199 | 70.08 | 4112.08 | 3909.75 | 202.33 | 4113 | 4.904 | 0.81745 | Modul Cleaning has been done in Row-N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 2020-11-29 | 660 | 1023 | 968 | 1134 | 64.8 | 3849.8 | 3654.75 | 195.05 | 3850 | 4.598 | 0.8161 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 2020-11-30 | 630 | 978 | 932 | 1089 | 62.1 | 3691.1 | 3506.25 | 184.85 | 3692 | 4.667 | 0.77104 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 2020-12-01 | 41 | 45 | 46 | 56 | 4.889 | 192.889 | 102 | 90.889 | 193 | 4.903 | 0.038366 | Grid failure from 08:53 to 17:20. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 2020-12-02 | 660 | 1033 | 988 | 1139 | 58.64 | 3878.64 | 3675.75 | 202.89 | 3879 | 4.919 | 0.76859 | Modul Cleaning has been done in Row-M,N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 1092 & Grid failure from 8:59 to 9:03. |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 2020-12-03 | 660 | 1059 | 1003 | 1144 | 69.29 | 3935.29 | 3733.5 | 201.79 | 3936 | 4.961 | 0.77328 | Modul Cleaning has been done in Row-I,J,K,L Inverter No-3 total module cleaning - 1092 & Grid failure from 9:12 to 9:15. |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 2020-12-04 | 650 | 1033 | 962 | 1088 | 65.37 | 3798.37 | 3600.75 | 197.62 | 3829 | 4.774 | 0.78173 | Module Cleaning has been done in Row- A,B,C,D,E,F,G,H Inverter No- 1 & A,B,C Inverter No - 4, total module cleaning-1401 & Grid failure from 3:15 to 3:18 |  | 1401 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 2020-12-05 | 620 | 963 | 903 | 983 | 58.37 | 3527.37 | 3339.75 | 187.62 | 3528 | 4.592 | 0.74882 | Modul Cleaning has been done in Row-D,E,F,G,H Inverter No-4 total module cleaning - 900 |  | 900 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 2020-12-06 | 636 | 978 | 917 | 1008 | 60.37 | 3599.37 | 3417.75 | 181.62 | 3600 | 4.672 | 0.75102 | Modul Cleaning has been done in Row-I,J,K,L Inverter No-4 & S,t inverter no-3 total module cleaning - 750 & Today 1 module damage by inverter No-4 this film side Row No-L module No-37 & A side (S.No-NPC10BY1110756). |  | 750 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 2020-12-07 | 639 | 987 | 922 | 1064 | 61.62 | 3673.62 | 3485.25 | 188.37 | 3674 | 4.711 | 0.76011 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 2020-12-08 | 641 | 968 | 913 | 1048 | 61.44 | 3631.44 | 3429.75 | 201.69 | 3632 | 4.653 | 0.76079 | Modul Cleaning has been done in Row-M,N,O,P,Q,R,S Inverter No-3 total module cleaning - 1008 & Today the transformer no-3,4 atending oil leakage both L.V and H.V side.& Today we are chang the new-24 MC4 conecter In the inverter No-3 AJB No-16,18. |  | 1008 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
343 | 2020-12-09 | 635 | 978 | 917 | 1049 | 61.27 | 3640.27 | 3447 | 193.27 | 3641 | 4.553 | 0.77943 | Today we are chang the new-58 MC4 conecter In the inverter No-3 AJB No-13,14,17.& inverter No-2 AJB No-12.& Module cleaning has been done in Row-I,J,K,L inverter no-2 total module cleaning -1092. |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 2020-12-10 | 610 | 927 | 877 | 992 | 56.48 | 3462.48 | 3273.75 | 188.73 | 3463 | 4.292 | 0.7864 | Today we are chang the new-81 MC4 conecter In the inverter No-2 AJB No-9,10,11.& inverter No-1 AJB No-1,2,3,4,5,6,7,8.& Module cleaning has been done in Row-A,B,C,D,E,F,G,H inverter no-1 total module cleaning -1113. |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 2020-12-11 | 181 | 227 | 217 | 232 | 7.28 | 864.28 | 732 | 132.28 | 865 | 8.22 | 0.10256 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 2020-12-12 | 519 | 741 | 670 | 782 | 36.97 | 2748.97 | 2589 | 159.97 | 2749 | 3.255 | 0.82315 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 2020-12-13 | 555 | 797 | 756 | 816 | 43.1 | 2967.1 | 2794.5 | 172.6 | 2968 | 3.426 | 0.84436 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 2020-12-14 | 479 | 675 | 650 | 691 | 31.69 | 2526.69 | 2361.75 | 164.94 | 2527 | 2.722 | 0.90484 | Modul Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning - 1566 |  | 1566 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 2020-12-15 | 509 | 731 | 691 | 761 | 36.91 | 2728.91 | 2580 | 148.91 | 2729 | 3.264 | 0.8149 | Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 & Grid failure from 05:29 to 5:43 & today we are change the new ( 61 ) MC4 conecter in the inverter no-4 AJB NO-19,20,21,22,23,24 |  | 1440 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 2020-12-16 | 625 | 922 | 877 | 967 | 49.73 | 3440.73 | 3258 | 182.73 | 3441 | 4.092 | 0.8196 | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 2020-12-17 | 670 | 1008 | 947 | 1059 | 58.48 | 3742.48 | 3559.5 | 182.98 | 3743 | 4.404 | 0.82837 | Module Cleaning has been done in Row- A,B,C,D,E,F,Inverter No- 1 &,O,P,Q,R inverter No-3 total module cleaning-1218 |  | 1218 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 2020-12-18 | 690 | 1039 | 978 | 1109 | 65.48 | 3881.48 | 3680.25 | 201.23 | 3882 | 4.591 | 0.82414 | Modul Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning - 1566 |  | 1566 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 2020-12-19 | 686 | 1048 | 993 | 1147 | 67.24 | 3941.24 | 3741 | 200.24 | 3942 | 4.608 | 0.83379 | Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 |  | 1440 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 2020-12-20 | 675 | 1023 | 978 | 1111 | 64.61 | 3851.61 | 3667.5 | 184.11 | 3852 | 4.552 | 0.82478 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 2020-12-21 | 695 | 1109 | 1038 | 1194 | 72.82 | 4108.82 | 3906 | 202.82 | 4109 | 5.151 | 0.77749 | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 2020-12-22 | 676 | 1043 | 973 | 1109 | 66.91 | 3867.91 | 3668.25 | 199.66 | 3868 | 4.851 | 0.77716 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C,D,E,F Inverter No-4 total module cleaning - 1464 |  | 1464 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 2020-12-23 | 661 | 1008 | 932 | 1069 | 63.08 | 3733.08 | 3544.5 | 188.58 | 3733 | 4.637 | 0.78465 | Module Cleaning has been done in Row-G,H,I,J,K,L, Tracker 1,2,3, and Row-Q,R,S,T, Inverter No- 4 and 3 total module cleaning-1416 |  | 1416 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 2020-12-24 | 654 | 1003 | 948 | 1058 | 63.1 | 3726.1 | 3539.25 | 186.85 | 3727 | 4.561 | 0.79644 | Module Cleaning has been done in Row-M,N,O,P and Row-J,K,L Inverter No-3 and 2 total module cleaning-1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 2020-12-25 | 646 | 978 | 917 | 1013 | 60.17 | 3614.17 | 3425.25 | 188.92 | 3615 | 4.068 | 0.86612 | Module Cleaning has been done in Row-I and Row-A,B,C,D,E,F,G,H Inverter No-2 and 1 total module cleaning-1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 2020-12-26 | 620 | 932 | 872 | 963 | 56.02 | 3443.02 | 3261 | 182.02 | 3444 | 4.19 | 0.80113 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning-1566 |  | 1566 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 2020-12-27 | 645 | 988 | 923 | 1028 | 61.04 | 3645.04 | 3474 | 171.04 | 3646 | 4.536 | 0.78342 | Grid failure from 11:26 to 11:32. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 2020-12-28 | 716 | 1099 | 1038 | 1175 | 70.9 | 4098.9 | 3884.25 | 214.65 | 4099 | 4.913 | 0.81317 | Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 |  | 1440 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 2020-12-29 | 660 | 1044 | 978 | 1098 | 66.83 | 3846.83 | 3645.75 | 201.08 | 3847 | 3.054 | 1.2277 | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 2020-12-30 | 716 | 1108 | 1023 | 1155 | 69.52 | 4071.52 | 3873.75 | 197.77 | 4072 | 4.648 | 0.85387 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C,D,E,F Inverter No-4 total module cleaning - 1464 |  | 1464 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 2020-12-31 | 595 | 872 | 831 | 882 | 48.61 | 3228.61 | 3045.75 | 182.86 | 3229 | 3.719 | 0.84624 | Module Cleaning has been done in Row-G,H,I,J,K,L, Tracker 1,2,3, and Row-Q,R,S,T, Inverter No- 4 and 3 total module cleaning-1416 & Today 1 module damage by monky, Inverter No-4 thin film side, Row No-I module No-92 & B side (S.No-NPC10BY1112877). |  | 1416 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 2021
| Date | 1104500527 | 1104500529 | 1.104501e+09 | 7802195.0 | 2100570073/ 2100567820/ 2100567898 | Total Generation (KWH) | Aggregate Meter Reading (KWH) | Difference | SEEDs data (KWH) | Insolation | PR (%) | Any Issues/Problems Observed | WO# | NO-OFF-CLEAN MODULES | Grid Failure | Inverter | Module Cleaning | Rainy day | No Module Cleaning | Transformer replacement and maintenance | Cable and Fuse maintenance | Plant Shutdown | Internet | Battery | Cloudy | Module Cleaning by rains
0 | 2021-01-01 | 514 | 746 | 721 | 756 | 37.83 | 2774.83 | 2605.5 | 169.33 | 2775 | 3.299 | 0.81985 | Module Cleaning has been done in Row-M,N,O,P and Row-J,K,L Inverter No-3 and 2 total module cleaning-1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2021-01-02 | 498 | 721 | 681 | 730 | 36.27 | 2666.27 | 2504.25 | 162.02 | 2667 | 3.06 | 0.84948 | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 |  | 1458 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2021-01-03 | 590 | 882 | 831 | 918 | 51.27 | 3272.27 | 3099 | 173.27 | 3273 | 3.936 | 0.81048 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 2021-01-04 | 504 | 716 | 685 | 725 | 36.5 | 2666.5 | 2506.5 | 160 | 2667 | 3.228 | 0.80527 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I,J Inverter No-4 total module cleaning-1566 |  | 1566 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 2021-01-05 | 544 | 786 | 751 | 787 | 41.5 | 2909.5 | 2730 | 179.5 | 2910 | 3.487 | 0.81338 | Today we are cleaning all inverter Door filters. & Module Cleaning has been done in Row- K,L, Tracker 1,2,3, and Row-M,N,O,P,Q,R,S,T, Inverter No- 3 and 4, total module cleaning-1440 & Today we are chang the new 1 MC4 conecter in the inverter no-1 - AJB-No-1. |  | 1440 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2021-01-06 | 661 | 1023 | 967 | 1068 | 62.39 | 3781.39 | 3597 | 184.39 | 3782 | 4.555 | 0.80926 | Module Cleaning has been done in Row-I,J,k,l Inverter No-2 & G,H Inverter No-1 total module cleaning - 1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 2021-01-07 | 221 | 312 | 298 | 313 | 16.25 | 1160.25 | 1046.25 | 114 | 1161 | 3.304 | 0.34249 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & A,B,C Inverter No-4 total module cleaning - 960 |  | 960 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2021-01-08 | 384 | 520 | 494 | 524 | 21.7 | 1943.7 | 1787.25 | 156.45 | 1944 | 2.216 | 0.85503 | Module Cleaning has been done in Row-D,E,F,G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1626 & Today we are found 1 MC4 connector Burn in Invertor No-4 AJB No-6 string No-4 --tive site. we replaced 1 MC4 connector and started the strings. |  | 1626 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2021-01-09 | 493 | 710 | 690 | 746 | 33.29 | 2672.29 | 2510.25 | 162.04 | 2673 | 3.106 | 0.83878 | Module Cleaning has been done in Row-L Inverter No-2 & Row-M,N,O,P,Q,R,S,T Inverter No-3 total module cleaning - 1344 & Today we are found 1 MC4 connector Burn in Invertor No-3 AJB No- string No-2 ++tive site we replaced all 1 MC4 connector and started the strings. |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 2021-01-10 | 509 | 752 | 711 | 817 | 39.38 | 2828.38 | 2667 | 161.38 | 2829 | 3.089 | 0.89262 | Grid failure from -10:15 to 10:22 & 11:32 to 11:47 & 01:51 to 01:59. |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2021-01-11 | 656 | 1002 | 953 | 1088 | 58.74 | 3757.74 | 3567.75 | 189.99 | 3758 | 4.046 | 0.90528 | Module Cleaning has been done in Row-I,J,K Inverter No-2 & Row-F,G,H Inverter No-1 total module cleaning - 1470 & Today we are found 1 MC4 connector Burn in Invertor No-2 AJB No-5 string No-1 ++tive site we replaced all 1 MC4 connector and started the strings. |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 2021-01-12 | 695 | 1059 | 987 | 1134 | 63.22 | 3938.22 | 3739.5 | 198.72 | 3939 | 4.697 | 0.81737 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 & Row-A,B,C,D,E,F,G, Inverter No-4 total module cleaning - 1473 & Today we are Recaind ABB -Wavlaty door fan -nos-3 and change the new fan in inverter no-3,4 |  | 1473 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 2021-01-13 | 736 | 1144 | 1069 | 1230 | 72.15 | 4251.15 | 4053 | 198.15 | 4252 | 5.111 | 0.81085 | Module Cleaning has been done in Row-H,I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-P,Q,R,S,T inverter No-3 total module cleaning -1365 |  | 1365 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2021-01-14 | 696 | 1109 | 1038 | 1205 | 71.41 | 4119.41 | 3927 | 192.41 | 4120 | 5.3 | 0.75766 | Grid failure from -03:54 to 04:32 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2021-01-15 | 650 | 1013 | 958 | 1088 | 62.64 | 3771.64 | 3573 | 198.64 | 3772 | 4.552 | 0.80765 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2021-01-16 | 635 | 983 | 935 | 1029 | 61.95 | 3643.95 | 3465.75 | 178.2 | 3644 | 4.464 | 0.79562 | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Row-K,L, Inverter No-2 total module cleaning - 1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2021-01-17 | 590 | 902 | 884 | 917 | 53.06 | 3346.06 | 3161.25 | 184.81 | 3347 | 3.891 | 0.83839 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2021-01-18 | 599 | 918 | 867 | 912 | 53.99 | 3349.99 | 3166.5 | 183.49 | 3350 | 4.303 | 0.7588 | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-C,D,E,F,G,H Inverter No-1 total module cleaning - 1575 & Grid failure from -02:37 to 2:54 |  | 1575 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2021-01-19 | 611 | 922 | 862 | 907 | 52.15 | 3354.15 | 3174 | 180.15 | 3355 | 4.128 | 0.79215 | Module Cleaning has been done in Row-A,B & Row-A,B,C,D,E,F,G,H,I,Inverter No-1&4 total module cleaning-1491 |  | 1491 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 2021-01-20 | 619 | 922 | 882 | 963 | 52.93 | 3438.93 | 3258 | 180.93 | 3439 | 4.168 | 0.80419 | Module Cleaning has been done in Row-J,K,L Inverter No-4 & Trecker 1,2,3 & Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1620 |  | 1620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2021-01-21 | 711 | 1134 | 1074 | 1210 | 73.15 | 4202.15 | 3999 | 203.15 | 4203 | 5.056 | 0.81022 | Module Cleaning has been done in Row-I,J,K,L Inverter No-2 & Row-G,H inverter No-1 total module cleaning -1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 2021-01-22 | 670 | 1049 | 1003 | 1099 | 66.17 | 3887.17 | 3684.75 | 202.42 | 3888 | 4.835 | 0.78376 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E,F inverter No-4 total module cleaning -1464 & Grid failure from 8:29 to 8:42 |  | 1464 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 2021-01-23 | 635 | 977 | 917 | 1053 | 56.63 | 3638.63 | 3450 | 188.63 | 3639 | 4.399 | 0.80627 | Module Cleaning has been done in Row-G,H,I,J,K,L & Inverter No-4 & Trecker 1,2,3 & Row-Q,R,S,T inverter No-3 total module cleaning -1416 & Grid failure from 6:30 to 8:21 & Grid failure from 10:37 to 10:42 |  | 1416 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 2021-01-24 | 671 | 1003 | 968 | 1074 | 60.38 | 3776.38 | 3598.5 | 177.88 | 3777 | 4.524 | 0.81372 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 2021-01-25 | 675 | 1024 | 1003 | 1088 | 65.66 | 3855.66 | 3659.25 | 196.41 | 3856 | 4.87 | 0.77172 | Module Cleaning has been done in Row-M,N,O,PInverter No-3 & Row-J,K,L, Inverter No-2 total module cleaning - 1617 & Today we are change the new (2) mc4 conecter in the inverter no-1 AJB No-6 & Grid failure from 11:24 to 11:54 & Today Replaced the D.C.15 Amp fuse link of the string-03 --tive line in AJB-123 of The Inverter-4 during the period of 11:30 to 11:35. |  | 1617 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
25 | 2021-01-26 | 767 | 1194 | 1144 | 1230 | 73.16 | 4408.16 | 4194 | 214.16 | 4409 | 5.026 | 0.85501 | Module Cleaning has been done in Row-I,Inverter No-2 & Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning - 1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 2021-01-27 | 775 | 1215 | 1149 | 1265 | 77.09 | 4481.09 | 4263 | 218.09 | 4482 | 5.295 | 0.82501 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning - 1386 Today Replaced the D.C.12 Amp fuse link of the string-08 --tive line in AJB-110 of The Inverter-2during the period of 10:30 to 10:35. |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
27 | 2021-01-28 | 757 | 1174 | 1109 | 1235 | 73.07 | 4348.07 | 4136.25 | 211.82 | 4349 | 5.118 | 0.82821 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 2021-01-29 | 766 | 1210 | 1134 | 1260 | 76.39 | 4446.39 | 4231.5 | 214.89 | 4447 | 5.276 | 0.82151 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 2021-01-30 | 771 | 1210 | 1154 | 1295 | 80.31 | 4510.31 | 4295.25 | 215.06 | 4511 | 5.319 | 0.8266 | Module Cleaning has been done in Row- J,K,L Inverter No-4 & Tracker 1,2,3, & Row-N,O,P,Q,R,S,T, Inverter No- 3 total module cleaning-1368 & Grid failure from 01:57 to 02:01. |  | 1368 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 2021-01-31 | 751 | 1189 | 1140 | 1270 | 78.92 | 4428.92 | 4232.25 | 196.67 | 4429 | 5.418 | 0.79674 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 2021-02-01 | 716 | 1139 | 942 | 1215 | 74.09 | 4086.09 | 3884.25 | 201.84 | 4087 | 5.253 | 0.75832 | Module Cleaning has been done in Row-M,N, Inverter No-3 & Row-J,K,L, Inverter No-2 total module cleaning - 1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 2021-02-02 | 690 | 1089 | 1028 | 1104 | 66.74 | 3977.74 | 3786.75 | 190.99 | 3978 | 4.934 | 0.78581 | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 & Today we are found 7 MC4 conecter burn in inverter no-4 AJB NO-19 string no-2 ++ive site & AJB NO-19 string no-4 ++ive site & AJB NO-20 string no-2 --ive site we replaced all-7 MC4 connector and started the string. |  | 1458 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 2021-02-03 | 620 | 927 | 887 | 938 | 50.84 | 3422.84 | 3242.25 | 180.59 | 3423 | 4.118 | 0.81016 | Module cleaning has been done in Row-B,C,D,E,F,G,H,I Inverter no-4 total module cleaning -1314 |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 2021-02-04 | 650 | 988 | 943 | 1023 | 57.54 | 3661.54 | 3474.75 | 186.79 | 3662 | 4.391 | 0.81284 | Module Cleaning has been done in Row-J,K,L Inverter No-4 & Trecker 1,2,3 & Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1620 |  | 1620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 2021-02-05 | 731 | 1139 | 1088 | 1171 | 68.95 | 4197.95 | 4002 | 195.95 | 4221 | 4.977 | 0.82661 | Module Cleaning has been done in Row-I,J,K,L Inverter No-2 & Row-G,H inverter No-1 total module cleaning -1533 & Today we are found 3 MC4 connecter burn in inverter no-2 AJB NO-108 string no-8 ++ive site & inverter NO-1 AJB NO-103 string no-5,6 ++ive site we replaced all-3 MC4 connector and started the string. |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 2021-02-06 | 766 | 1205 | 1140 | 1253 | 75.37 | 4439.37 | 4230 | 209.37 | 4440 | 5.172 | 0.83671 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E,F inverter No-4 total module cleaning -1464 |  | 1464 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | 2021-02-07 | 796 | 1255 | 1184 | 1321 | 80.9 | 4636.9 | 4425 | 211.9 | 4637 | 5.277 | 0.85645 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 2021-02-08 | 782 | 1244 | 1174 | 1335 | 81.18 | 4616.18 | 4401.75 | 214.43 | 4617 | 5.465 | 0.82342 | Module Cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-Q,R,S,T inverter No-3 total module cleaning -1416 & Today we are found 1MC4 connecter burn in inverter no-1 AJB NO-102 string no-8 ++ive site we replaced 1MC4 connector and started the string. |  | 1416 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 2021-02-09 | 700 | 1079 | 1039 | 1144 | 67.25 | 4029.25 | 3841.5 | 187.75 | 4030 | 4.851 | 0.8097 | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 & Row-J,K,L, inverter No-2 total module cleaning -1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 2021-02-10 | 741 | 1144 | 1088 | 1190 | 69.6 | 4232.6 | 4026.75 | 205.85 | 4233 | 4.708 | 0.87632 | Module Cleaning has been done in Row-I, inverter-2 & Row-A,B,C,D,E,F,G,H inverter no-1 & Row-A Inverter No-4 and total module cleaning-1458 |  | 1458 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 2021-02-11 | 650 | 984 | 943 | 1023 | 55.01 | 3655.01 | 3480 | 175.01 | 3656 | 4.336 | 0.82181 | Module cleaning has been done in Row-B,C,D,E,F,G,H,I Inverter no-4 total module cleaning -1314 |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 2021-02-12 | 681 | 1048 | 993 | 1084 | 62.93 | 3868.93 | 3687.75 | 181.18 | 3869 | 4.64 | 0.81271 | Module Cleaning has been done in Row-j,k,l Inverter No-4 & Trecker 1,2,3 & total module cleaning -528 |  | 528 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 2021-02-13 | 655 | 997 | 963 | 1033 | 58.96 | 3706.96 | 3518.25 | 188.71 | 3707 | 4.528 | 0.79794 | Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1617 |  | 1617 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 2021-02-14 | 671 | 1054 | 1013 | 1073 | 62.59 | 3873.59 | 3691.5 | 182.09 | 3874 | 4.726 | 0.79895 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 2021-02-15 | 685 | 1033 | 978 | 1064 | 59.18 | 3819.18 | 3636 | 183.18 | 3820 | 4.429 | 0.84064 | Module Cleaning has been done in Row-I,j inverter-2 & Row-D,E,F,G,H inverter no-1 total module cleaning-1470 |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 2021-02-16 | 746 | 1165 | 1098 | 1225 | 71.35 | 4305.35 | 4105.5 | 199.85 | 4306 | 4.849 | 0.86551 | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F,G inverter No-4 total module cleaning -1200 |  | 1200 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 2021-02-17 | 731 | 1103 | 1039 | 1174 | 66.71 | 4113.71 | 3917.25 | 196.46 | 4114 | 4.846 | 0.82743 | Module Cleaning has been done in Row-I,J,K,L Inverter No-4 & Trecker 1,2,3 & Row-R,S,T inverter no-3 total module cleaning -1092 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 2021-02-18 | 726 | 1089 | 1048 | 1169 | 66.48 | 4098.48 | 3892.5 | 205.98 | 4099 | 4.693 | 0.85129 | Module Cleaning has been done in Row-M,N,O,P,Q Inverter No-3 & Row-K,L Inverter No-2 total module cleaning - 1449 |  | 1449 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 2021-02-19 | 761 | 1179 | 1104 | 1246 | 72.23 | 4362.23 | 4156.5 | 205.73 | 4363 | 4.92 | 0.86432 | Today we are change the new (5) mc4 conecter in the inverter no-3 AJB No-116. & today we are found (2)MC4 connector burn in inverter no-3 AJB NO-116 string NO-2 ++ive site &--ive site we replaced all-2 MC4 connector & started the string.& module cleaning has been done in Row-I,J inverter no-2 & Row-D,E,F,G,H, inverter no-1 total module cleaning -1470 |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 2021-02-20 | 796 | 1241 | 1164 | 1325 | 78.01 | 4604.01 | 4378.5 | 225.51 | 4605 | 5.467 | 0.82098 | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F Inverter No-4 total module cleaning - 1002 |  | 1002 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 2021-02-21 | 761 | 1204 | 1144 | 1270 | 74.83 | 4453.83 | 4269 | 184.83 | 4454 | 5.333 | 0.81401 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 2021-02-22 | 716 | 1109 | 1049 | 1180 | 66.63 | 4120.63 | 3909 | 211.63 | 4121 | 5.083 | 0.7902 | Module Cleaning has been done in Row-G,H,I,J Inverter No-4 total module cleaning - 774 |  | 774 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 2021-02-23 | 725 | 1129 | 1083 | 1209 | 68.16 | 4214.16 | 4005 | 209.16 | 4215 | 5.057 | 0.81238 | Module Cleaning has been done in Row-k,l Inverter No-4 & Trecker 1,2,3 & ROW-P,Q,R,S,T inverter no-3 total module cleaning -789 |  | 789 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 2021-02-24 | 716 | 1104 | 1084 | 1195 | 67.93 | 4166.93 | 3969.75 | 197.18 | 4167 | 4.791 | 0.84772 | Module Cleaning has been done in Row-M,N,O Inverter No-3 & Row-L inverter no-2 total module cleaning - 903 & Grid failure from -15:19 to 15:23 |  | 903 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 2021-02-25 | 766 | 1229 | 1184 | 1325 | 75.6 | 4579.6 | 4359 | 220.6 | 4580 | 5.299 | 0.84241 | Module Cleaning has been done in Row-I,J,K inverter no-2 total module cleaning - 840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 2021-02-26 | 752 | 1190 | 1129 | 1271 | 71.17 | 4413.17 | 4199.25 | 213.92 | 4414 | 5.11 | 0.84191 | Module Cleaning has been done in Row-D,E,F,G,H inverter no-1 total module cleaning - 903 |  | 903 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 2021-02-27 | 755 | 1154 | 1099 | 1244 | 67.79 | 4319.79 | 4131 | 188.79 | 4320 | 5.038 | 0.83575 | Module Cleaning has been done in Row-A,B,C inverter no-1 & A,B,C,D,E,F total module cleaning - 1002 |  | 1002 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 2021-02-28 | 736 | 1129 | 1064 | 1220 | 65.81 | 4214.81 | 4019.25 | 195.56 | 4215 | 5.142 | 0.79895 | Today we are faund one module damej in Inverter no-4,AJB No-4,String no-2,module no-3,B-site module serial no-NPC10BY1130277 & Grid failure from -10:04 to 10:15 |  |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 2021-03-01 | 787 | 1215 | 1144 | 1336 | 73.01 | 4555.01 | 4332.75 | 222.26 | 4556 | 5.541 | 0.8014 | Module Cleaning has been done in Row-I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1122 |  | 1122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 2021-03-02 | 791 | 1235 | 1189 | 1376 | 82.04 | 4673.04 | 4451.25 | 221.79 | 4674 | 5.567 | 0.81831 | Today replced the 12-Amp D.C Fuse link of the string-7 in AJB-117 of the inverter no-3 during the poried-09:50 to 10:10 Module Cleaning has been done in Row-N,O,P,Q,R,S,T Inverter no-3 total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
61 | 2021-03-03 | 741 | 1189 | 1175 | 1285 | 78.93 | 4468.93 | 4256.25 | 212.68 | 4469 | 5.046 | 0.86321 | Module Cleaning has been done in Row-M, inverter no-3 & Row- J,K,L inverter no-2 total module cleaning total module cleaning - 1071 & Grid failure from-11:05 to 10:09 & Grid failure from-11:34 to 11:37 & Grid failure from-03:04 to 03:33 & Today we are found 1MC4 connecter burn in inverter no-1 AJB NO-105 string no-8 --ive site we replaced 1MC4 connector and started the string. |  | 1071 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 2021-03-04 | 771 | 1225 | 1164 | 1296 | 76.37 | 4532.37 | 4322.25 | 210.12 | 4533 | 5.264 | 0.83931 | Module Cleaning has been done in Row-,I inverter no-3 & Row-D,E,F,G,H inverter no-1 total module cleaning - 1176 & Grid failure from-16:43 to 16:49 & Grid failure from-17:32 to 17:54 |  | 1176 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 2021-03-05 | 776 | 1200 | 1144 | 1295 | 74.29 | 4489.29 | 4276.5 | 212.79 | 4490 | 4.792 | 0.91323 | Module Cleaning has been done in Row-A,B,C inverter no-1 & Row-A,B,C,D,E,F inverter no-4 total module cleaning - 1002 |  | 1002 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 2021-03-06 | 751 | 1159 | 1104 | 1280 | 71.01 | 4365.01 | 4158.75 | 206.26 | 4366 | 5.126 | 0.83015 | Module Cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1122 |  | 1122 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 2021-03-07 | 777 | 1204 | 1149 | 1346 | 79.26 | 4555.26 | 4346.25 | 209.01 | 4556 | 5.395 | 0.82309 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 2021-03-08 | 756 | 1167 | 1149 | 1295 | 74.98 | 4441.98 | 4236 | 205.98 | 4442 | 4.951 | 0.87446 | Grid failure from-07:19 to 07:25 & Module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, inverter no-3 & Row-L,inverter no-2 total module cleaning - 1344. |  | 1344 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 2021-03-09 | 771 | 1233 | 1185 | 1331 | 77.65 | 4597.65 | 4365.75 | 231.9 | 4598 | 5.437 | 0.82426 | Module Cleaning has been done in Row-I,J,K inverter no-2 & Row-G,H inverter no-1 total module cleaning - 1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 2021-03-10 | 766 | 1199 | 1139 | 1280 | 73.83 | 4457.83 | 4249.5 | 208.33 | 4458 | 5.104 | 0.8513 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 2021-03-11 | 711 | 1064 | 1013 | 1089 | 61.21 | 3938.21 | 3750 | 188.21 | 3939 | 4.312 | 0.89035 | Module Cleaning has been done in Row-A,B,C,D,E,F inverter no-1 & Row-A,B,C,D,E inverter no-4 total module cleaning - 1266 |  | 1266 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 2021-03-12 | 725 | 1103 | 1048 | 1225 | 63.12 | 4164.12 | 3954 | 210.12 | 4165 | 4.884 | 0.83117 | Module Cleaning has been done in Row-F,G,H,I,J,L,L Inverter No-4 & Trecker 1,2,3 total module cleaning -1320 |  | 1320 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 2021-03-13 | 782 | 1205 | 1175 | 1350 | 78.42 | 4590.42 | 4374 | 216.42 | 4591 | 5.522 | 0.81033 | module Cleaning has been done in Row-M,N,O,P,Q,R,S,T, inverter no-3 & Row-L,inverter no-2 total module cleaning - 1344. |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 2021-03-14 | 770 | 1190 | 1174 | 1321 | 75.39 | 4530.39 | 4326.75 | 203.64 | 4531 | 5.186 | 0.85156 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 2021-03-15 | 766 | 1194 | 1149 | 1290 | 73.62 | 4472.62 | 4266.75 | 205.87 | 4473 | 5.294 | 0.82351 | Module cleaning has been done in Row-I,J,k inverter no-2 & Row-F,G,H, inverter no-1 total module cleaning -1470 & Grid failure from-09:42 to 09:46 & Grid failure from-11:01 to 11:17 |  | 1470 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 2021-03-16 | 727 | 1114 | 1064 | 1184 | 65.33 | 4154.33 | 3944.25 | 210.08 | 4155 | 5.038 | 0.80383 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 2021-03-17 | 746 | 1139 | 1083 | 1215 | 68 | 4251 | 4042.5 | 208.5 | 4252 | 5.015 | 0.82637 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 2021-03-18 | 695 | 998 | 958 | 1059 | 56.25 | 3766.25 | 3567.75 | 198.5 | 3767 | 4.488 | 0.81808 | Module cleaning has been done in Row- A,B,C,D,E Inverter no-1 & Row-A,B,C,D Inverter No-4 total module cleaning -915 |  | 915 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 2021-03-19 | 696 | 1024 | 973 | 1119 | 56.94 | 3868.94 | 3681.75 | 187.19 | 3979 | 4.591 | 0.84473 | Module cleaning has been done in Row- E,F,G,H,I,J,K Inverter No-4 total module cleaning -1296 |  | 1296 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 2021-03-20 | 685 | 1007 | 983 | 1124 | 59.78 | 3858.78 | 3657.75 | 201.03 | 3859 | 4.607 | 0.81641 | Module Cleaning has been done in Row-L, Inverter No-4 & Row-M,N,O,P,Q,R,S,T, Inverter No-3 & Trecker 1,2,3 total module cleaning -1278 |  | 1278 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 2021-03-21 | 701 | 1038 | 1053 | 1174 | 64.95 | 4030.95 | 3837 | 193.95 | 4031 | 4.883 | 0.8046 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 2021-03-22 | 705 | 1089 | 1053 | 1190 | 66.33 | 4103.33 | 3893.25 | 210.08 | 4104 | 4.894 | 0.81733 | Module cleaning has been done in Row- I,J,K,L, Inverter No-2 & Row-H, Inverter No-1 total module cleaning -1323 |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 2021-03-23 | 711 | 1114 | 1039 | 1169 | 66.06 | 4099.06 | 3894 | 205.06 | 4100 | 4.895 | 0.81636 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 2021-03-24 | 756 | 1149 | 1083 | 1230 | 67.48 | 4285.48 | 4066.5 | 218.98 | 4286 | 5.117 | 0.81637 | Module cleaning has been done in Row- A,B,C,D,E,F,G Inverter No-1 & Row-A,B,C,D Inverter No-4 total module cleaning -1314 |  | 1314 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 2021-03-25 | 837 | 1250 | 1185 | 1386 | 77.36 | 4735.36 | 4504.5 | 230.86 | 4736 | 5.53 | 0.83472 | Module cleaning has been done in Row- E,F,G,H,I Inverter No-4 total module cleaning -954 |  | 954 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 2021-03-26 | 816 | 1225 | 1169 | 1396 | 79.35 | 4685.35 | 4464.75 | 220.6 | 4686 | 4.95 | 0.92268 | Module Cleaning has been done in Row-J,K,L, Inverter No-4 & Trecker 1,2,3 Row-M,N,O,P,Q,R,S,T, Inverter No-3 & total module cleaning -1620 |  | 1620 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 2021-03-27 | 726 | 1124 | 1084 | 1225 | 72.38 | 4231.38 | 4026.75 | 204.63 | 4232 | 5.036 | 0.81905 | Module cleaning has been done in Row- I,J,K,L Inverter No-2 total module cleaning -1092 & Grid failure from-08:22 to 08:25 & Grid failure from-12:09 to 12:36 |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 2021-03-28 | 781 | 1230 | 1169 | 1325 | 77.45 | 4582.45 | 4362.75 | 219.7 | 4583 | 5.611 | 0.79609 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 2021-03-29 | 796 | 1250 | 1185 | 1356 | 79.23 | 4666.23 | 4448.25 | 217.98 | 4667 | 5.579 | 0.81533 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 2021-03-30 | 802 | 1245 | 1184 | 1376 | 79.93 | 4686.93 | 4464.75 | 222.18 | 4687 | 5.481 | 0.83347 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 2021-03-31 | 766 | 1129 | 1074 | 1245 | 65.2 | 4279.2 | 4060.5 | 218.7 | 4280 | 4.879 | 0.855 | Module cleaning has been done in Row- A,B,C,D,E,F,G,H Inverter No-1 & Row-A,B,C, Inverter No-4 total module cleaning -1401 |  | 1401 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 2021-04-01 | 827 | 1240 | 1179 | 1351 | 79.37 | 4676.37 | 4457.25 | 219.12 | 4677 | 5.505 | 0.82806 | Today we are cleaning all inverter Door filters. |  |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 2021-04-02 | 811 | 1219 | 1159 | 1350 | 78.46 | 4617.46 | 4403.25 | 214.21 | 4618 | 5.392 | 0.83475 | Module cleaning has been done in Row- D,E,F,G,H,I,JInverter No-4 total module cleaning -1278 |  | 1278 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 2021-04-03 | 787 | 1175 | 1124 | 1366 | 75.36 | 4527.36 | 4306.5 | 220.86 | 4528 | 5.42 | 0.81425 | Module Cleaning has been done in Row-K,L, Inverter No-4 & Trecker 1,2,3 Row-P,Q,R,S,T, Inverter No-3 & total module cleaning -789 |  | 789 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 2021-04-04 | 710 | 1053 | 1028 | 1225 | 65.59 | 4081.59 | 3900 | 181.59 | 4082 | 5.165 | 0.77029 | Grid failure from-16:35 to 17:27 & Grid failure from-17:30 to 17:33 & Grid failure from-17:42 to 17:47 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 2021-04-05 | 772 | 1149 | 1145 | 1341 | 76.2 | 4483.2 | 4257.75 | 225.45 | 4484 | 5.535 | 0.78959 | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 2021-04-06 | 781 | 1210 | 1179 | 1351 | 78.56 | 4599.56 | 4374 | 225.56 | 4600 | 5.588 | 0.80233 | Module cleaning has been done in Row-I,J,K, Inverter No-2 total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 2021-04-07 | 811 | 1265 | 1205 | 1391 | 79.58 | 4751.58 | 4535.25 | 216.33 | 4752 | 5.65 | 0.81975 | Module cleaning has been done in Row- L, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -693 |  | 693 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 2021-04-08 | 786 | 1190 | 1134 | 1295 | 74.43 | 4479.43 | 4257 | 222.43 | 4480 | 5.557 | 0.78576 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-1 & Row-A,B,C,D, Inverter No-4 & total module cleaning -1104 |  | 1104 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 2021-04-09 | 772 | 1144 | 1088 | 1280 | 69.87 | 4353.87 | 4158 | 195.87 | 4354 | 5.369 | 0.7904 | Module cleaning has been done in Row-E,F,G,H,I,J,K Inverter No-4 total module cleaning -1134 |  | 1134 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 2021-04-10 | 766 | 1134 | 1089 | 1296 | 72.02 | 4357.02 | 4141.5 | 215.52 | 4358 | 5.451 | 0.77923 | Module Cleaning has been done in Row-K,L, Inverter No-4 & Trecker 1,2,3 Row-O,P,Q,R,S,T, Inverter No-3 & total module cleaning -978 |  | 978 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 2021-04-11 | 766 | 1149 | 1129 | 1305 | 75.55 | 4424.55 | 4229.25 | 195.3 | 4425 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 2021-04-12 | 740 | 1114 | 1094 | 1245 | 69.58 | 4262.58 | 4052.25 | 210.33 | 4263 |  | % | Today we are chang the new (10) mc4 conecter in the inverter no-1,2,3 AJB no-105,106,107,113 &114 &Module Cleaning has been done in Row-M,N, Inverter No-1 & Row-J,K,L, Inverter No-4 & total module cleaning -1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 2021-04-13 | 762 | 1154 | 1098 | 1255 | 67.09 | 4336.09 | 4109.25 | 226.84 | 4337 |  |  | Module Cleaning has been done in Row-I, Inverter No-2 & Row-D,E,F,G,H, Inverter No-1 & total module cleaning -1176 |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 2021-04-14 | 750 | 1124 | 1084 | 1255 | 66.69 | 4279.69 | 4089 | 190.69 | 4280 |  |  | Module Cleaning has been done in Row-A,B,C Inverter No-1 & Row-A,B,C,D,E,F,G Inverter No-4 & total module cleaning -1200 |  | 1200 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 2021-04-15 | 767 | 1134 | 1084 | 1275 | 71.74 | 4331.74 | 4125.75 | 205.99 | 4332 |  |  | Module Cleaning has been done in Row-I, Inverter No-2 & Row-H,I,J,K,L Inverter No-4 & Tracker-1,2,3 total module cleaning -924 |  | 924 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 2021-04-16 | 791 | 1180 | 1144 | 1381 | 76.61 | 4572.61 | 4347.75 | 224.86 | 4573 |  |  | Module cleaning has been done in Row-N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -840 |  | 840 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 2021-04-17 | 776 | 1179 | 1149 | 1361 | 74.32 | 4539.32 | 4325.25 | 214.07 | 4540 |  |  | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 2021-04-18 | 761 | 1164 | 1129 | 1316 | 72.39 | 4442.39 | 4226.25 | 216.14 | 4443 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 2021-04-19 | 777 | 1185 | 1122 | 1351 | 75.1 | 4510.1 | 4317 | 193.1 | 4511 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 2021-04-20 | 751 | 1134 | 1101 | 1259 | 65.16 | 4310.16 | 4077.75 | 232.41 | 4311 | 5.209 | 0.80663 | Module Cleaning has been done in Row-I,J,K,L nverter No-2 & Row-H Inverter No-1 total module cleaning -1323 |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 2021-04-21 | 786 | 1199 | 1124 | 1306 | 72.37 | 4487.37 | 4261.5 | 225.87 | 4488 | 5.211 | 0.83943 | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 total module cleaning -1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 2021-04-22 | 771 | 1160 | 1099 | 1287 | 70.8 | 4387.8 | 4172.25 | 215.55 | 4388 | 5.134 | 0.83304 | Module cleaning has been done in Row-A,B,C,D Inverter No-4 total module cleaning -432 |  | 432 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 2021-04-23 | 776 | 1159 | 1093 | 1299 | 72.18 | 4399.18 | 4173.75 | 225.43 | 4400 | 5.682 | 0.75475 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 2021-04-24 | 615 | 847 | 802 | 927 | 42.13 | 3233.13 | 3072 | 161.13 | 3234 | 3.9 | 0.80822 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 2021-04-25 | 736 | 1109 | 1043 | 1215 | 68.35 | 4171.35 | 3944.25 | 227.1 | 4172 | 5.178 | 0.7853 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 2021-04-26 | 726 | 1068 | 1008 | 1169 | 65.97 | 4036.97 | 3836.25 | 200.72 | 4037 | 5.348 | 0.73573 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 2021-04-27 | 695 | 1033 | 973 | 1139 | 61.25 | 3901.25 | 3701.25 | 200 | 3902 | 5.057 | 0.75205 | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-4 total module cleaning -990 |  | 990 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 2021-04-28 | 651 | 968 | 922 | 1124 | 49.15 | 3714.15 | 3545.25 | 168.9 | 3715 | 4.798 | 0.75466 | Grid failure from-05:04 to 05:08 & Module Cleaning has been done in Row-H,I,J,K,L Inverter No-4 & Tracker-1,2,3 total module cleaning -924 |  | 924 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2021-04-29 | 695 | 991 | 1008 | 1205 | 63.76 | 3962.76 | 3787.5 | 175.26 | 3963 | 4.902 | 0.78796 | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T, Inverter No-3 total module cleaning -1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 2021-04-30 | 670 | 1061 | 1008 | 1179 | 61.84 | 3979.84 | 3752.25 | 227.59 | 3980 | 4.885 | 0.79409 | Module Cleaning has been done in Row-I,J,K,L, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -1533 |  | 1533 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 2021-05-01 | 585 | 886 | 847 | 993 | 43.52 | 3354.52 | 3141.75 | 212.77 | 3355 | 4.072 | 0.80304 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 total module cleaning -483 & Grid failure from-03:26 to 03:32 |  | 483 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 2021-05-02 | 741 | 1135 | 1089 | 1285 | 69.82 | 4319.82 | 4114.5 | 205.32 | 4320 | 5.408 | 0.77857 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 2021-05-03 | 766 | 1154 | 1109 | 1316 | 71.27 | 4416.27 | 4189.5 | 226.77 | 4417 | 5.306 | 0.81136 | Grid failure from-07:15 to 07:20 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 2021-05-04 | 731 | 1124 | 1078 | 1270 | 69.88 | 4272.88 | 4069.5 | 203.38 | 4273 | 5.238 | 0.7951 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 2021-05-05 | 766 | 1190 | 1139 | 1366 | 78.24 | 4539.24 | 4311 | 228.24 | 4540 | 5.684 | 0.77849 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 2021-05-06 | 751 | 1168 | 1124 | 1336 | 76.55 | 4455.55 | 4245 | 210.55 | 4456 | 5.618 | 0.77307 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 2021-05-07 | 736 | 1145 | 1099 | 1315 | 73.51 | 4368.51 | 4152 | 216.51 | 4369 | 5.454 | 0.78076 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 2021-05-08 | 670 | 1018 | 978 | 1139 | 57.92 | 3862.92 | 3677.25 | 185.67 | 3863 | 5.037 | 0.74749 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 2021-05-09 | 655 | 988 | 947 | 1197 | 58.69 | 3845.69 | 3562.5 | 283.19 | 3846 | 4.811 | 0.77916 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 2021-05-10 | 737 | 1134 | 1089 | 1320 | 77.29 | 4357.29 | 4146.75 | 210.54 | 4358 | 5.473 | 0.77609 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 2021-05-11 | 745 | 1144 | 1099 | 1336 | 77.3 | 4401.3 | 4197.75 | 203.55 | 4402 | 5.593 | 0.76711 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 2021-05-12 | 746 | 1134 | 1089 | 1346 | 75.28 | 4390.28 | 4164.75 | 225.53 | 4391 | 5.507 | 0.77714 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-4 total module cleaning -1188 |  | 1188 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 2021-05-13 | 731 | 1104 | 1063 | 1361 | 73.36 | 4332.36 | 4128 | 204.36 | 4333 | 5.354 | 0.78879 | Module cleaning has been done in Row-I,J,K,L Inverter No-4 tracker 1,2,3 & Row- R,S,T inverter No-3 total module cleaning -893 |  | 893 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 2021-05-14 | 706 | 1083 | 1094 | 1315 | 72.25 | 4270.25 | 4050 | 220.25 | 4271 | 5.337 | 0.77998 | Module cleaning has been done in Row-M,N,O,P,Q, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1449 |  | 1449 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2021-05-15 | 645 | 1009 | 978 | 1139 | 54.36 | 3825.36 | 3616.5 | 208.86 | 3826 | 4.631 | 0.80524 | Module cleaning has been done in Row-I,J, Inverter No-2 & Row-D,E,F,G,H, inverter No-1 total module cleaning -1470 |  | 1470 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 2021-05-16 | 524 | 786 | 751 | 867 | 37.29 | 2965.29 | 2807.25 | 158.04 | 2966 | 3.852 | 0.75048 | Grid failure from-04:42 to 04:46 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2021-05-17 | 303 | 418 | 393 | 449 | 14.46 | 1577.46 | 1423.5 | 153.96 | 1578 | 1.761 | 0.87337 | Grid failure from-09:19 to 09:26 & 09:33 to 09:37 & 09:38 to 10:02 & 11:18 to 11:24 & 11:24 to 12:27 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2021-05-18 | 120 | 141 | 141 | 146 | 3.3 | 551.3 | 408.75 | 142.55 | 552 | 5.51 | 0.097643 | Grid failure from-03:48 to 07:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 2021-05-19 | 373 | 524 | 504 | 595 | 23.49 | 2019.49 | 1884 | 135.49 | 2020 | 2.266 | 0.86885 | Grid failure from-09:25 to 09:38 &09:48 to 10:02 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 2021-05-20 | 752 | 1155 | 1124 | 1330 | 76.67 | 4437.67 | 4233 | 204.67 | 4338 | 5.447 | 0.77622 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 2021-05-21 | 740 | 1149 | 1114 | 1351 | 73.05 | 4427.05 | 4217.25 | 209.8 | 4428 | 5.485 | 0.78683 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 2021-05-22 | 686 | 1038 | 1023 | 1205 | 64.44 | 4016.44 | 3819.75 | 196.69 | 4017 | 5.017 | 0.78039 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-O,P,Q,R,S,T inverter No-3 total module cleaning -1302 |  | 1302 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 2021-05-23 | 675 | 1064 | 1043 | 1240 | 65.29 | 4087.29 | 3897 | 190.29 | 4088 | 5.102 | 0.78095 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 2021-05-24 | 696 | 1109 | 1069 | 1290 | 69.43 | 4233.43 | 4019.25 | 214.18 | 4234 | 5.458 | 0.75608 | Module Cleaning has been done in Row-J,K,L Inverter No-2 & Row-M,N Inverter No-3 total module cleaning -1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 2021-05-25 | 731 | 1164 | 1114 | 1331 | 75.86 | 4415.86 | 4201.5 | 214.36 | 4416 | 5.692 | 0.75617 | Module Cleaning has been done in Row-I, Inverter No-2 & Row-A,B,C,D,E,F,G,H, Inverter No-1 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 2021-05-26 | 650 | 998 | 957 | 1149 | 55.92 | 3809.92 | 3619.5 | 190.42 | 3810 | 4.763 | 0.77965 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 & Grid failure from-11:03 to 11:06 |  | 1386 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 2021-05-27 | 685 | 1008 | 973 | 1220 | 61.1 | 3947.1 | 3741 | 206.1 | 3948 | 4.957 | 0.77627 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 & Grid failure from-01:28 to 01:32 |  | 1368 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 2021-05-28 | 696 | 1048 | 1023 | 1219 | 60.31 | 4046.31 | 3845.25 | 201.06 | 4047 | 5.171 | 0.7628 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 & Grid failure from-04:53 to 05:22 |  | 1344 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 2021-05-29 | 721 | 1059 | 1013 | 1215 | 63.41 | 4071.41 | 3865.5 | 205.91 | 4172 | 5.086 | 0.7995 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-1 total module cleaning -1113 & Today we are found 1 MC4 connecter born Inverter No-1 AJB-103 string no-3 +tive site we replaced 1-MC4 connecter and started the string |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 2021-05-30 | 750 | 1103 | 1064 | 1260 | 69.94 | 4246.94 | 4044 | 202.94 | 4247 | 5.331 | 0.77647 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 2021-05-31 | 747 | 1094 | 1048 | 1265 | 68.05 | 4222.05 | 4017 | 205.05 | 4223 | 5.244 | 0.78489 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,I Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2021-06-01 | 746 | 1094 | 1064 | 1305 | 70.37 | 4279.37 | 4068.75 | 210.62 | 4280 | 5.183 | 0.80485 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1368 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 2021-06-02 | 746 | 1134 | 1114 | 1311 | 75.89 | 4380.89 | 4166.25 | 214.64 | 4381 | 5.014 | 0.85161 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 2021-06-03 | 725 | 1089 | 1043 | 1235 | 68.58 | 4160.58 | 3965.25 | 195.33 | 4161 | 5.106 | 0.79427 | Module cleaning has been done in Row-A,B,C,D,E,F,G, Inverter No-1 total module cleaning -1113 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 2021-06-04 | 691 | 998 | 958 | 1149 | 60.88 | 3856.88 | 3660.75 | 196.13 | 3857 | 4.965 | 0.75715 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 & Grid failure from-04:14 to 04:38 |  | 1386 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 2021-06-05 | 766 | 1154 | 1119 | 1351 | 47.18 | 4437.18 | 3660.75 | 776.43 | 4438 | 5.098 | 0.84848 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 2021-06-06 | 726 | 1073 | 1038 | 1260 | 67.93 | 4164.93 | 3960 | 204.93 | 4165 | 4.656 | 0.87188 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 2021-06-07 | 690 | 1029 | 998 | 1189 | 63.17 | 3969.17 | 3790.5 | 178.67 | 3970 | 4.836 | 0.80012 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 2021-06-08 | 681 | 1003 | 968 | 1140 | 61.84 | 3853.84 | 3643.5 | 210.34 | 3854 | 4.488 | 0.83697 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning -1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 2021-06-09 | 670 | 973 | 927 | 1119 | 60.28 | 3749.28 | 3550.5 | 198.78 | 3750 | 4.403 | 0.83011 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 2021-06-10 | 650 | 937 | 905 | 1113 | 58.34 | 3663.34 | 3455.25 | 208.09 | 3663 | 4.435 | 0.805 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 2021-06-11 | 676 | 1008 | 975 | 1210 | 64.03 | 3933.03 | 3729 | 204.03 | 3934 | 5.021 | 0.76365 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1368 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 2021-06-12 | 675 | 1003 | 956 | 1164 | 61.53 | 3859.53 | 3677.25 | 182.28 | 3860 | 4.939 | 0.76173 | Module Cleaning has been done in Row-M, Inverter No-3 & Row-I,J,K,L, Inverter No-2 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 2021-06-13 | 650 | 952 | 944 | 1084 | 53.01 | 3683.01 | 3469.5 | 213.51 | 3684 | 4.606 | 0.77956 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H Inverter No-1 total module cleaning -1113 |  | 1113 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 2021-06-14 | 686 | 1004 | 968 | 1164 | 60.61 | 3882.61 | 3682.5 | 200.11 | 3883 | 4.79 | 0.7901 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H,I, Inverter No-4 total module cleaning -1386 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 2021-06-15 | 685 | 1003 | 973 | 1185 | 62.79 | 3908.79 | 3708.75 | 200.04 | 3909 | 4.885 | 0.77993 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 2021-06-16 | 650 | 947 | 917 | 1108 | 52.48 | 3674.48 | 3474.75 | 199.73 | 3675 | 4.595 | 0.77951 | Module cleaning has been done in Row-J,K,L, Inverter No-4 tracker 1,2,3 & Row-N,O,P,Q,R,S,T inverter No-3 total module cleaning -1368 |  | 1386 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 2021-06-17 | 413 | 595 | 575 | 696 | 28.34 | 2307.34 | 2142.75 | 164.59 | 2308 | 3.432 | 0.65545 | Grid failure from-07:30 to 07:59 & 01:14 to 02:28 & 02:52 to 02:55 & 03:06 to 03:10 & 04:06 to 04:10 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 2021-06-18 | 509 | 701 | 680 | 791 | 27.31 | 2708.31 | 2553 | 155.31 | 2709 | 3.09 | 0.85448 | Grid failure from-03:34 to 03:36 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 2021-06-19 | 298 | 393 | 378 | 434 | 13.2 | 1516.2 | 1366.5 | 149.7 | 1517 | 1.856 | 0.79664 | Grid failure from-11:02 to 11:17 & 12:57 to 01:36 & 02:17 to 02:19 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 2021-06-20 | 398 | 529 | 514 | 585 | 18.2 | 2044.2 | 1947.75 | 96.45 | 2045 | 2.213 | 0.90067 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 2021-06-21 | 378 | 585 | 560 | 660 | 28.8 | 2211.8 | 2082.75 | 129.05 | 2212 | 2.891 | 0.74574 | Grid failure from-12:16 to 02:05 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 2021-06-22 | 514 | 730 | 710 | 836 | 33.34 | 2823.34 | 2648.25 | 175.09 | 2824 | 3.443 | 0.79943 | Grid failure from-08:12 to 08:19 & 12:47 to 12:55 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 2021-06-23 | 701 | 993 | 963 | 1139 | 52.02 | 3848.02 | 3606 | 242.02 | 3849 | 4.658 | 0.80538 | Grid failure from-04:44 to 04:46 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 2021-06-24 | 539 | 711 | 685 | 807 | 33.97 | 2775.97 | 2616 | 159.97 | 2776 | 3.251 | 0.83225 | Grid failure from-01:18 to 01:21 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 2021-06-25 | 681 | 1003 | 963 | 1139 | 57.02 | 3843.02 | 3651 | 192.02 | 3844 | 4.722 | 0.79343 | Module Cleaning has been done in Row-I,J,K, Inverter No-2 & Row-G,H, Inverter No-1 total module cleaning -1281 |  | 1281 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 2021-06-26 | 645 | 938 | 897 | 1069 | 55.52 | 3604.52 | 3412.5 | 192.02 | 3605 | 4.423 | 0.7944 | Module Cleaning has been done in Row-A,B,C,D,E,F Inverter No-1 & Row-A,B,C,D,E Inverter No-4 total module cleaning -1266 |  | 1266 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 2021-06-27 | 710 | 1063 | 1023 | 1214 | 59.21 | 4069.21 | 3888.75 | 180.46 | 4070 | 5.144 | 0.77116 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 2021-06-28 | 379 | 489 | 469 | 539 | 16.32 | 1892.32 | 1785.75 | 106.57 | 1893 | 2.141 | 0.86176 | Module cleaning has been done in Row-F,G,H,I,J,K,L Inverter No-4 tracker 1,2,3 total module cleaning -1320 |  | 1320 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 2021-06-29 | 579 | 821 | 797 | 948 | 40.19 | 3185.19 | 2962.5 | 222.69 | 3186 | 3.755 | 0.82697 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 2021-06-30 | 630 | 918 | 892 | 1053 | 53.73 | 3546.73 | 3392.25 | 154.48 | 3547 | 4.29 | 0.80585 | Module cleaning has been done in Row-M,N,O,P,Q,R,S,T inverter No-3 total module cleaning -1092 |  | 1092 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 2021-07-01 | 595 | 887 | 857 | 1024 | 39.361 | 3402.361 | 3198 | 204.361 | 3403 | 4.635 | 0.71559 | Module cleaning has been done in Row-I,J,K,L inverter No-2 total module cleaning -1092 & Grid failure from-03:04 to 04:02 & 05:20 to 05:25 |  | 1092 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 2021-07-02 | 635 | 938 | 902 | 1073 | 50.24 | 3598.24 | 3410.25 | 187.99 | 3599 | 4.415 | 0.79452 | Module cleaning has been done in Row-A,B,C,D,E,F,G,H,inverter No-1 total module cleaning -1113 & Grid failure from-05:21 to 05:31 |  | 1113 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 2021-07-03 | 640 | 967 | 937 | 1119 | 54.18 | 3717.18 | 3506.25 | 210.93 | 3718 | 4.62 | 0.78437 | Module Cleaning has been done in Row-A,B,C,D,E,F,G,H, Inverter No-4 total module cleaning -1188 |  | 1188 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 2021-07-04 | 645 | 998 | 968 | 1149 | 61.41 | 3821.41 | 3652.5 | 168.91 | 3822 | 4.783 | 0.77883 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 2021-07-05 | 610 | 948 | 912 | 1104 | 57.24 | 3631.24 | 3419.25 | 211.99 | 3632 | 4.904 | 0.72185 | Module cleaning has been done in Row-I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-P,Q,R,S,T, total module cleaning -1167 & Grid failure from-01:11 to 01:12 & 03:32 to 04:09 |  | 1167 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 2021-07-06 | 645 | 1028 | 1008 | 1200 | 62.57 | 3943.57 | 3761.25 | 182.32 | 3944 | 5.098 | 0.75403 | Module Cleaning has been done in Row-M,N,OInverter No-3 & Row-K,L inverter no-2 total module cleaning -1176 |  | 1176 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 2021-07-07 | 671 | 1073 | 1039 | 1230 | 64.96 | 4077.96 | 3858 | 219.96 | 4078 | 5.084 | 0.7818 | Module Cleaning has been done in Row-I,J Inverter No-2 & Row-E,F,G,H inverter no-1 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 2021-07-08 | 685 | 1033 | 992 | 1189 | 58.36 | 3957.36 | 3731.25 | 226.11 | 3958 | 4.934 | 0.78186 | Module Cleaning has been done in Row-A,B,C,D,E Inverter No-1 & Row-A,B,C,D,E,F,G, inverter no-4 total module cleaning -1326 |  | 1326 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 2021-07-09 | 655 | 994 | 963 | 1159 | 55.54 | 3826.54 | 3661.5 | 165.04 | 3827 | 4.806 | 0.77612 | Module cleaning has been done in Row-H,I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-Q,R,S,T, inverter No-3 total module cleaning -1218 |  | 1218 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 2021-07-10 | 605 | 917 | 902 | 1074 | 43.43 | 3541.43 | 3371.25 | 170.18 | 3542 | 4.464 | 0.77335 | Module Cleaning has been done in Row-M,N,O,P, Inverter No-3 & Row-K,L, inverter no-2 total module cleaning -1323 |  | 1323 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 2021-07-11 | 529 | 751 | 726 | 852 | 32.45 | 2890.45 | 2736 | 154.45 | 2891 | 3.426 | 0.82246 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 2021-07-12 | 474 | 695 | 676 | 791 | 31.4 | 2667.4 | 2493.75 | 173.65 | 2668 | 3.196 | 0.81364 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 2021-07-13 | 640 | 983 | 947 | 1149 | 56.22 | 3775.22 | 3565.5 | 209.72 | 3776 | 4.738 | 0.77676 | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-E,F,G,H, inverter no-1 total module cleaning -1344 |  | 1344 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 2021-07-14 | 646 | 998 | 968 | 1149 | 53.38 | 3814.38 | 3607.5 | 206.88 | 3815 | 4.715 | 0.78862 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 2021-07-15 | 634 | 1003 | 968 | 1165 | 53.11 | 3823.11 | 3681 | 142.11 | 3824 | 4.803 | 0.77599 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 2021-07-16 | 545 | 852 | 831 | 993 | 42.64 | 3263.64 | 3075 | 188.64 | 3264 | 4.131 | 0.7701 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 2021-07-17 | 554 | 817 | 791 | 937 | 43.87 | 3142.87 | 2953.5 | 189.37 | 3143 | 2.871 | 1.067 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 2021-07-18 | 373 | 509 | 494 | 575 | 21.28 | 1972.28 | 1845 | 127.28 | 1973 | 1.933 | 0.99483 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 2021-07-19 | 464 | 654 | 635 | 746 | 24.46 | 2523.46 | 2355 | 168.46 | 2524 | 2.824 | 0.87112 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-1 & Row-A,B,C,D,E,F, inverter no-4 total module cleaning -1266 |  | 1266 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 2021-07-20 | 287 | 374 | 363 | 408 | 11.07 | 1443.07 | 1329.75 | 113.32 | 1444 | 1.585 | 0.88795 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 2021-07-21 | 418 | 569 | 550 | 630 | 20.84 | 2187.84 | 2020.5 | 167.34 | 2188 | 2.526 | 0.84424 | Grid failure from-09:37 to 09:49 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 2021-07-22 | 600 | 857 | 831 | 978 | 39.71 | 3305.71 | 3129.75 | 175.96 | 3306 | 3.944 | 0.81699 | Module Cleaning has been done in Row-A,B,C,D,E,F, Inverter No-4 total module cleaning - 790 |  | 790 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 2021-07-23 | 338 | 443 | 424 | 479 | 14.07 | 1698.07 | 1578 | 120.07 | 1699 | 1.855 | 0.89269 | Module cleaning has been done in Row-G,H,I,J,K,L Inverter No-4 & tracker 1,2,3, & Row-R,S,T, inverter No-3 total module cleaning -1230 & Grid failure from-02:31 to 02:34 |  | 1230 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 2021-07-24 | 514 | 737 | 715 | 836 | 31.01 | 2833.01 | 2656.5 | 176.51 | 2834 | 3.393 | 0.81408 | Module cleaning has been done in Row-M,N,O,P,Q, Inverter No-3 & Row-K,L, inverter No-2 total module cleaning -1449 & Grid failure from-01:24 to 01:37 |  | 1449 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 2021-07-25 | 141 | 171 | 161 | 187 | 4.82 | 664.82 | 559.5 | 105.32 | 665 | 0.741 | 0.87469 | Today U.P.S maintenanc from -09:28 to 10:12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 2021-07-26 | 151 | 197 | 191 | 211 | 5.58 | 755.58 | 619.5 | 136.08 | 756 | 0.902 | 0.8169 | Grid failure from -02:00 to 02:31 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 2021-07-27 | 343 | 463 | 454 | 525 | 15.71 | 1800.71 | 1656.75 | 143.96 | 1801 | 1.967 | 0.8924 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 2021-07-28 | 277 | 373 | 358 | 403 | 11.11 | 1422.11 | 1284.75 | 137.36 | 1423 | 1.556 | 0.89135 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 2021-07-29 | 172 | 222 | 217 | 237 | 6.23 | 854.23 | 714 | 140.23 | 855 | 0.945 | 0.88183 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 2021-07-30 | 302 | 403 | 388 | 438 | 12.84 | 1543.84 | 1408.5 | 135.34 | 1544 | 1.874 | 0.80303 | Grid failure from -03:49 to 04:52 & 05:38 to 05:41 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 2021-07-31 | 393 | 524 | 524 | 610 | 19.44 | 2070.44 | 1910.25 | 160.19 | 2071 | 2.376 | 0.84954 | Grid failure from -06:28 to 07:28 & 10:22 to 10:31 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 2021-08-01 | 414 | 560 | 559 | 660 | 20.94 | 2213.94 | 2067 | 146.94 | 2214 | 2.637 | 0.81831 | Grid failure from -09:22 to 09:35 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 2021-08-02 | 232 | 277 | 283 | 333 | 10.16 | 1135.16 | 1018.5 | 116.66 | 1136 | 0.787 | 1.4069 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 2021-08-03 | 317 | 419 | 418 | 504 | 15.27 | 1673.27 | 1523.25 | 150.02 | 1674 | 1.953 | 0.83542 | Today replace 3phase motor coil chang. |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 2021-08-04 | 388 | 509 | 514 | 620 | 21.94 | 2052.94 | 1903.5 | 149.44 | 2053 | 2.485 | 0.80522 | Grid failure from -09:21 to 09:26 |  |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2021-08-05 | 479 | 659 | 645 | 791 | 31.47 | 2605.47 | 2467.5 | 137.97 | 2606 | 3.225 | 0.78758 | Module Cleaning has been done in Row-I,J, Inverter No-2 & Row-F,G,H, inverter no-1 total module cleaning -1197 & Today we are found 1 MC4 connecter born Inverter No-2 AJB-112 string no-7 +tive & -tive site we replaced 2-MC4 connecter and started the string |  | 1197 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 2021-08-06 | 479 | 641 | 615 | 751 | 29.78 | 2515.78 | 2346 | 169.78 | 2516 | 3.065 | 0.80008 | Module Cleaning has been done in Row-A,B,C,D,E, Inverter No-1 & Row-Q,R,S,T, inverter no-3 total module cleaning -777 & Today we are clening all inverter door filters. |  | 777 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 2021-08-07 | 483 | 655 | 640 | 771 | 29.53 | 2578.53 | 2419.5 | 159.03 | 2579 | 3.243 | 0.7751 | Module Cleaning has been done in Row-M,N,O,P, inverter no-3 total module cleaning -798 |  | 798 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 2021-08-08 | 530 | 756 | 736 | 867 | 34.18 | 2923.18 | 2744.25 | 178.93 | 2859 | 3.709 | 0.75129 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0